## BOQ 1
Lot 1 , BOQ - SUPPLY AND INSTALL OF SOLAR SYSTEM FOR STAGE #02 ALSANAFEAH WELL IN MATNAH - SANAA CITY
Item # | Description | Unit | Qty | Unit Price (USD) |  | Total Price (USD)
|  |  |  | Figures | Words
A | Electrical Works
PV System
1 | Solar PV Module Supply, install, test, and commission a solar PV module with the following specifications: Type: Mono-crystalline Wattage: 650Wp Efficiency: 21% Operating temperature range: -40 to +85 degrees Celsius Warranty: 10 years product, 25 years performance | No. | 112
2 | MOBILE, UNHEATED HIGH-PRESSURE CLEAN Supply, delivery, test and commission of a mobile, cold water high-pressure cleaner such as Kärcher HD 10/23-4 S with the following specifications: • Working pressure = min 200 Bar • Motor = 4-pole, three-phase motor with air and water cooling Price shall include providing all required solar panel cleaning equipment, include brushes such as Kärcher iSolar 800 water-driven brush head or equivalent, sprayers, chemical cleaners such as RM 99 Solar Cleaner or equivalent and extender poles as well. A-shaped Ladder Supply A-shaped Ladder Telescopic lifting household folding double-side, 2.5 meter high, metal. | No. | 1
3 | Solar PV Pump Inverters Supply, install, test, and commission three-phase Solar Pump Inverters (Controllers) with the following specifications: • Voltage: 380-420 V • Frequency: 50 Hz • Built-in MPPT • Soft start • V/F speed control with solar radiation auto and manual start and stop • Monitoring system • All required accessories such as controls, wires, etc. • Capacity: Not less than 75 kW | No. | 1
4 | PV Combiner Boxes Supply, install, test, and commission PV Combiner Boxes with the following specifications: * 7 string imputs + 2 spare inputs • Enclosure materials: Coated metal with lockable door • Enclosure protection: IP65 • DC fuse rating for each string: 1500V, 30 A • DC output circuit breaker: In accordance with the maximum current × 1.25, 1500 VDC • Built-in surge protection device (SPD) 40KV, 1500V • Anti-backflow diodes • The work and installation should be achieved as per technical specifications and drawings | No. | 1
6 | DC Solar Cable | Notes
6.1 | Solar PV Cable Supply, install, test, and commission of Solar PV Cable from array to combiner boxes as per technical specifications and drawings. • Cable type: Solar PV cable • Size: 1×10 mm² • Insulation: Polyethylene • Jacket: PVC • UV resistant • Flame retardant • The cable must be installed in accordance with the technical specifications and drawings. • The cable must be tested for continuity and insulation resistance. • The cable must be commissioned by a qualified electrician. | m | 208
6.2 | Couple of Solar Connectors Supply, install, test, and commission of a couple of solar connectors of the same type and manufacturer of the PV panel as per technical specifications and drawings. • Connector type: MC4 connector • Size: 10 mm² • Quantity: 2 (Pair male and female) • The connectors must be of the same type and manufacturer as the PV panel. • The connectors must be installed in accordance with the technical specifications and drawings. • The connectors must be tested for continuity and insulation resistance. • The connectors must be commissioned by a qualified electrician. | No. | 7
6.3 | Solar PV Cable Supply, install, test, and commission of Solar PV Cable from PV combiner boxes to Inverter as per technical specifications and drawings. • Cable type: Solar PV cable • Size: 1×120 mm² • Length: As per drawings • Insulation: Polyethylene • Jacket: PVC • UV resistant • Flame retardant • The cable must be installed in accordance with the technical specifications and drawings. • The cable must be tested for continuity and insulation resistance. • The cable must be commissioned by a qualified electrician. | m | 30
7 | AC Power Cable: | Notes
7.1 | AC Power Cable Supply, install, test, and commission of AC submersible power cable CU/XLPE/PVC with the following specifications: • Cable type: CU/XLPE/PVC • Size: 4x (1 Core × 95 mm²) • Number of cores: 3 • Conductor per phase: 1 • Insulation: Cross-linked polyethylene (XLPE) • Jacket: PVC • UV resistant • Flame retardant • Voltage rating: 450/750 VAC • Type of conductor: Copper, flexible, finely multi stranded • Insulation: Black polychloroprene, HO7RN-F or equivalent material | m | 306
7.2 | Level Sensor Cable Supply, install, test, and commission of Level Sensor Cable with probes with the following specifications: • Cable type: Level Sensor Cable • Size: 3 x 1.5 mm² • Number of probes: 3 • Probe material: Stainless steel • Probe insulation: Polyurethane • Cable jacket: PVC • UV resistant • Flame retardant | m | 306
8 | Cable Tray | Notes
8.1 | Cable Tray Supply, install, test, and commission of covered cable tray for AC with all required accessories with the following specifications: • Material: Hot dipped galvanized steel (120 micron) • Thickness: 1.2 mm • Width: 20 cm • Depth: 10 cm • Length: As per Quantities • Tray coating: Powder coated • Tray finish: Black • Tray accessories: Cable tray brackets, cable tray supports, cable tray covers, cable tray labels • The cable tray must be installed in accordance with the technical specifications and drawings. • The cable tray must be tested for strength and durability. • The cable tray must be commissioned by a qualified electrician. | m | 30
9 | Earthing System Supply, install, test, and commission of Earthing System with the following specifications: • 2 x Copper rods, tap-clamps, earthing pits (Y/G earthing cable, earthing pits and all system accessories). • 3 x Earth bus bars. • Main earth cables (Bare cables between earth rods, earthing bars and its interconnections) should not be less than 70mm2 bare copper. • The sizing of earthing conductor and earthing installation shall be according to IEE Wiring regulations & BS 7671. • Earth resistance should be tested in presence of the UNOPS representative by calibrated earth tester, the earth resistance should not be more than 5 Ohm. • All conductive materials shall be copper. | System | 4
10 | Lightning System Supply, install, test, and commission of Lightning System with the following specifications: • Lightning arrester: Copper • Lightning arrester height: As per drawings • Lightning arrester compliance: IEC/BS EN 62305-3 • System resistance: Not more than 1 ohm • Earthing installation: In accordance with the IEE Wiring regulations, BS 7671 • All conductive materials: Copper • Conductor size: According to table 54.7 of IEE – BS 7671 – IEC 60365-5-54 | System | 2
11 | Cable Trench Supply, install, test, and commission of Cable Trench with the following specifications: • Depth: 60 cm • Width: 60 cm • Filling material: Sand or gravel • Conduits: PVC or steel • Marker tape: Yellow or orange • Civil work: Excavation, backfilling, compaction • Pipe fittings: Elbows, tees, couplings • Connection to manholes: Flexible conduit or sleeve • 12 mm nylon rope: For pulling cables • Required sleeves: For protecting cables from sharp objects All necessary accessories: As per drawings, specifications, and related codes and standards | m | 50
12 | Manhole Supply, construct, and install a Manhole with the following specifications: • Size: 70 x 70 cm • Material: Solid concrete blocks 15 x 20 x 40 cm • Watertight and airtight • Base: At least 15 cm thick of cast in situ concrete • Plastering: Yes • Painting: Two coats of hot bituminous paint • PVC cover: Yes, can withstand 200 kg/m² • All work to be completed in accordance with the technical specifications and drawings • To the complete satisfaction of the supervisor engineer | No. | 6
13 | Fire alarm System Supply, install, test and commission of a fire alarm system including all necessary accessories such as fire-resistant cable, trunkeys, metal conduit pipes, and proper labeling with complete drawings and documentation. | Notes
13.1 | Smoke and Heat Detectors Supply, install, test, and commission of standalone smoke and heat detectors. Smoke detectors: • Must be photoelectric or ionization type • Must have a sensitivity level of at least 5% obscuration • Must have a battery backup • Must be labeled in a clear and concise manner Heat detectors: • Must have a heat detection range of at least 50°F to 150°F • Must have a battery backup • Must be labeled in a clear and concise manner | No. | 2
13.2 | Flame Detectors Supply, install, test, and commission of standalone Flame Detector Technical Specifications: - Operating voltage: 24 VDC nominal (18-32 VDC) - regulated - Detects hydrocarbon and non-hydrocarbon fuel fires in all environmental conditions - Alarm Current ≤ 32 mA | No. | 2
13.3 | Fire CO2 Extinguishers Supply, install, test, and commission of fire CO2 extinguishers, according to specifications including: • Must be 5KG CO2 type • Must be approved to BS EN 3 Parts 7 to 9 and SS EN3 &UL standards • Must have a discharge time of at least 10 seconds • Must be labeled in a clear and concise manner Accessories: • Must include a carrying case • Must include a hose • Must include a nozzle | Pcs | 1
13.4 | Powder Extinguishers Supply, install, test, and commission of powder extinguishers, according to specifications including: • Must be 6 kg powder type • Must be approved to BS EN 3 Parts 7 to 9 and SS EN3 &UL standards • Must have a discharge time of at least 10 seconds • Must be labeled in a clear and concise manner Accessories: • Must include a carrying case • Must include a hose • Must include a nozzle | Pcs | 2
14 | LED Lighting Supply, install, test, and commission of LED lighting with all required accessories as per technical specifications including: • Must be LED type • Must be dimmable • Must have a lifespan of at least 50,000 hours • Must be labeled in a clear and concise manner Accessories: • Must include a power supply • Must include a mounting bracket • Must include a controller | Notes
14.1 | Solar LED Street Light Supply, install, and commissioning of a solar LED street light as per technical specifications including: LED: • Maximum output: 40W • Efficacy: At least 120lm PV module: • At least 60Wp Battery: • Type: LiFePO4 • Voltage: 12.8V • Capacity: At least 27 AH Mounting system: • For fence poles | Set | 7
15 | Supply, installing, Testing, and commissioning of Diesel Generator.Work sets according to technical specification and drawings of the following equipment with all continuous electric power generating equipment: | Note
15.1 | DIESEL GENERATOR SUPPLY, DELIVERY, INSTALING, AND COMMISSIONING OF 150-180 KVA Sound-Proof Prime Power Diesel Generator as per SOW • (150-180) KVA capacity, 3 phase,4Wire, 380-415 V, 50 Hz, 1500 RPM, • Diesel engine complete with its accessories. • Alternator, self-excited. • Steel base-plate complete with anti vibrators, bolts and nuts. • Automatic Voltage Regulator ( AVR ). • Control, instrument, meters and indicators panel board • Speed governor. • Water cooling system. • Inlet air system. • Exhaust system. This Item includes | No. | 1
15.2 | Fuel Tank: Supply, and delivery of a complete elevated outdoor daily Steel Fuel tank with a capacity of 5000 L and a thickness not less than 5 mm, including a Sight Glass Level Measurement (Gauge) and all necessary fuel pipes, fittings, valves, filters, flow meter up to 4 ℓ/sec, suitable for diesel service, instruments and all accessories for connection to the genset base fuel tank. The tank must be applied with two layers of epoxy outside and three layers inside. | set | 1
15.3 | Generator AC Output Cable Size: 4 X 95 mm² Cable shall include joints and all accessories As per Drawings, "Annex 1. Electrical and Mechanical Technical specification" and "RFQ_Section_Il_Schedule of Requirement. | LM | 10
15.4 | Circuit Breaker Supply, install, test and commissioning NEMA 3R enclosure, powder-coated steel construction include 200A, 400V, 3P & 25KA Molded Case Circuit Breaker (MCCB) , as per Electrical and Mechanical Technical specification" and "RFQ_Section_Il_Schedule of Requirement and drawing. | Pcs | 1
15.5 | Set of fuel filter elements. | set | 4
15.6 | Set of oil filter elements. | set | 6
15.7 | Set of air filter elements. | set | 2
16 | Project sign boards Supply, install, and maintenance of a project sign board with the following specifications: • Size: 1.6m x 1.4m • Height from ground: 1.2m • Material: Similar to specified large sign support • Information: Written in Arabic and English Languages as shown in attached drawings, and any other information instructed by the Employer/Engineer | pcs | 1
17 | System Maintenance: System maintenance for a period of 1 year, including preventive maintenance visits as per scope of work. Preventive maintenance visits: • The contractor will visit the system on a 3-month basis to perform preventive maintenance tasks. The preventive maintenance tasks will include: • Cleaning and inspecting the system components. • Lubricating the system components. • Replacing any worn or damaged components. Corrective maintenance: • The contractor will repair any system components that fail during the warranty period. • The contractor will also repair any system components that are damaged due to negligence or misuse. | LS | 1
18 | System Training: Comprehensive training on how to operate and maintain the system. The training will cover the following topics: • System overview • System operation • System maintenance • System troubleshooting • The training will be conducted by a qualified instructor. • The training will be tailored to the specific needs of the owner's staff. Training materials: The contractor will provide the following training materials: • Training manual • Training exercises • Training videos | LS | 1
Total Carried to Summary Page 1
Sub Total (1)
B | Mechanical Works
1 | Well Cap / Cover: Supply, install, and commissioning of a well cap / cover suitable for an 10-inch well, as per drawings and technical specifications including: • Material: Cast iron or aluminum • Size: 10 inches in diameter Features: • Watertight seal • Secured with bolts or a padlock • Has a vent to prevent pressure buildup • Has a label with the well depth, casing size, and gallons per minute | No. | 1
2 | Well Head Piping Fittings: Supply, install, and commissioning of well head piping fittings with all required fittings, as per drawings and technical specifications including: Pipe: 3 inch, PN40, carbon steel | LS | 1
2.1 | Mechanical flow meter: 3 inch, with a flow rate of up to 1000 liters per minute | No. | 1
2.2 | Gate valve: 3 inch, PN40, with a pressure rating of 40 bar | No. | 1
2.3 | Non-return valve: 3 inch, PN40, with a pressure rating of 40 bar | No. | 1
2.4 | Air vent valve (Air releaser), 2 inch, PN40 | No. | 1
2.5 | Valves Chamber | No. | 1
3 | Analog Pressure Gauge: Supply, install, and commissioning of an analog pressure gauge, as per drawings and technical specifications including: • Range: 0-30 bar • Accuracy: ±1% of reading • Resolution: 0.1 bar • Connection: G1/4 NPT • Housing: Stainless steel • Dial: Black • Needle: Red • Mounting: Back mount | No. | 1
4 | Pressure Switches: Supply, install, and commissioning of pressure switches, as per drawings and technical specifications including: • Setting pressure: 10-11 bar • Accuracy: ±1% of reading • Response time: <1 second • Connection: G1/4 NPT • Housing: Stainless steel • Terminals: Screw terminal block | No. | 1
5 | Raiser Pipes: Supply, install, and commissioning of raiser pipes with joints, 4" GI CS 6 m long, as per drawings and technical specifications including: • Size: 3 inches • Material: Galvanized iron (GI) • Type: Carbon steel • Length: 6 meters • Joints: Flange joints | No. | 81
6 | Vertical raiser Non-return Valves: Supply, install, and commissioning of vertical raiser non-return valves, 3 inches, as per drawings and technical specifications including: • Size: 3 inches • Material: Cast iron or bronze • Type: Vertical raiser non-return valve • Pressure rating: 30 bar • Temperature rating: -20 degrees Celsius to +85 degrees Celsius • Features: Prevents backflow, Easy to install, Durable | No. | 1
7 | Electrical Submersible Pump Supply, install and commissioning Submersible Pump as shown in the drawings and technical specifications: -Rated capacity: 36 m3/hr @ Head of 298m - Mixed flow multi -stage separate type, AC 3PH motor type; - Pump diameter: 6 inches - Power supply: Three-phase, 380 volts, 50 Hz - Motor: Centrifugal, wet-rotor, induction motor - Impellers: Stainless steel, multi-stage - Shaft: Stainless steel | No. | 1
Total Carried to Summary Page 2
Sub Total (2)
Total Sum

## BOQ-Civil
BOQ - SUPPLY AND INSTALL OF SOLAR SYSTEM FOR STAGE #02 ALSANAFEAH WELL IN MATNAH - SANAA CITY
Item # | Description | Unit | Qty | Unit Price (USD) |  | Total Price (USD)
|  |  |  | Figures | Words
C | PV System Civil Works
1 | Steel Mounting Structure: Supplying, delivering, fabricating, installing, hoisting, and fixing in place, and making all structural steel work in accordance with shop drawings for columns, beams, purlins, bracing, brackets, etc., with minimum yield strength as specified in the technical specifications. The contractor will be responsible for the following: * Supplying all materials required for the steel mounting structure. * Fabricating the steel mounting structure in accordance with the shop drawings. * Delivering the steel mounting structure to the project site. * Installing the steel mounting structure in accordance with the technical specifications. * Hoisting and fixing the steel mounting structure in place. * Providing all temporary staging and supporting work required for the installation of the steel mounting structure. * Making all connections using plates, channels, angles, gusset plate, anchor bolt, cleats, fasteners, etc. * Hot galvanizing the steel mounting structure (min galvanized 120mic)). * Providing all necessary bolts and washers for fastening, including bolt grouting. * Completing the work to the complete satisfaction of the supervisor engineer. * Works shall be in accordance with EC3 std., and all bolts shall be Anti-thief high strength bolts (Grade 8.8), as per the technical specifications and drawings. | Note
1.1 | SITE GRADING AND LEVELING Clearing, grubbing, removing and disposing of all trees, brush, stumps, fences, debris, and miscellaneous structures not covered under other contract items within the construction area and such other areas as specified in drawings. The Contractor shall clear such additional areas within the limits of the right-of-way as specified or directed by the Engineer. Materials generated by the work, including construction and demolition debris, shall be disposed to an approved dumping site. The Contractor shall grade the new site by cut and backfill in any type of soil, construct necessary driveways and sidewalks, topsoil and/or seed the area and perform other incidentally required items of work to prepare the site in accordance with the contract documents. | LS | 1
1.2 | GROUND LEVEL MOUNTING STRUCTURES - TYPE 1 The item shall include the following: • Surveying and conducting all site levelling. • Supplying, fabricating, delivering at site, hoisting and fixing in position, including all temporary staging and supporting work and making all structural steel work as per in the shop drawings and technical specifications of mounting structures. • Supply and implementation of reinforced concrete C25 (Cylinder 25 MPa) for all mountings foundations, including anchor bolts, the excavation works and all necessary related works according to the shop drawings, technical specifications and the instructions of the supervising Engineer. • Fabrication and erection in position structural steel sections for base plates, columns, rafters, eaves, bracing, galvanized purlins and others made out of plates, IPE Sections, L and UPE sections and other structural steel sections complete as per drawing and as per the direction of supervising engineer in Charge including grouting, cutting, welding, grinding, drilling, hoisting, fixing in position at all heights and levels. The rate includes all connections nuts, bolts, washer plates, welds required for fabrication and erection and all necessary related work according to the shop drawings and the technical specifications. • Providing and applying a coat of approved zinc chromite primer and two coats of synthetic enamel paint over all as specified and directed. | m² | 315
| SECURITY FENCE (METALCHAIN LINK FABRIC). Supply and install Chain Link Metal Fence with Barbed wires as per in the drawings and the technical specifications, the work includes the following: • Survey and conduct all site settlement and levelling such as cut and backfill in any type of soil, and clear all planned areas for the work from materials, debris, chairs and disposal of debris to authorized area prior to the commencing of work. • Provide materials and construction of 2.50-meter-high chain Link Fence made from hot dip galvanized coated with pvc coated Post that shall be embedded in concrete footings and pressed at end. The panels width is 3 meter. The chain link comprise 50mmx50mm openings. the work includes installing of three lines of Barbed Wires above. • Provide materials and construction of 3m wide double leaf gate as shown on the drawings and according to the technical specifications and instructions of the supervising Engineer. | L.M | 188
D | CONSTRUCTIONS WORKS
| General Notes: • The bidders are requested to refer General Notes, Pricing Preambles, Drawings, Specifications, Conditions of Contract, Special Conditions of Contract and all other relevant documents prior to pricing of the following items. • All Concrete Works shall comply to the specifications, • Contractor shall ensure that all contacting surfaces including reinforcement dowels left out for bonding purposes is free from any organic or artificial material which can be a hindrance to achieve specified properties in the Drawings and Specifications. • Rates for lean concrete shall include for preparation of bottom of excavation prior to pouring of lean concrete. • Rates for formwork shall include for control joints, isolation joints wherever specified and required according to the drawings and specifications. • Rate for concrete shall include for construction joint, isolation joint, expansion joint, with dowel bars, end cap and compressible filler with sealant on top as per drawing. • Rates for concrete shall include all necessary tests by an Authority acceptable to the Engineer. • Formwork for buried concrete may be of timber, for all other concrete, shall be 15 mm thick plywood. • Rates for concrete shall include all necessary equipment which are required for concreting. Rate shall include for continuous curing for 7 days. • The size of reinforcement bars comply BS 4449 described in the drawing or elsewhere shall be the minimum size and the rolling margin and any other tolerance shall be wholly above this size. Hooks and laps have been measured and included with the quantities for reinforcements. • All reinforcement shall be free from mill scale, dirt, oil, paint, grease or loose rust before fixing in position and shall be brushed with a stiff wire brush if so directed by the Engineer. • Reinforcement shall be bent cold by applying a slow even pressure on an approved type of bending apparatus. • Re-bending of incorrectly bends bars shall not be attempted. • Rates shall include for cutting, bending, fabricating, placing in position, holding and supporting including temporary fixing supports, hangers, binding wire spacers, laps and waste. •The price includes supply and laying insulation layer (Nailon sheet minimum 2mm thick) and Painting 2 layers with bitumen (Minimum 2mm thick/layer for all underground foundations. | NOTE
1 | GENERATOR ROOM
1.1 | SITE CLEARANCE
A | Site clearance and preparation including the removal of trees and plants as much as possible. (Site visit necessary) to prepare the site to start construction the project. All debris shall be transported out of site | L.S | 3
1.2 | EARTH WORK
A | Excavation in soil. The job includes shoring and shuttering. The items includes disposal of surplus earth to outside to any unobjectionable place to be identified by contractor at his own cost and approved by engineer | m³ | 43.2
B | Supply and lay approved crushed stone base coarse 20 cm thick with CBR > 80% y to the levels shown in the drawings. Price includes watering & compaction to reach 100 % of maximum dry density , the work includes all tests as per specifications & Engineer Instructions | m³ | 10.23
C | Supply and lay filling material from imported material around foundations & any other element up to ground slab level in layers not more than 20cm thick for each layer with compaction to 98% of MDD. The works including compacting the design soil surfaces to get (98% MDD), the work includes all tests as per specifications & Engineer Instructions | m³ | 32.4
1.3 | CONCRETING WORKS
A | Supply and cast ready mix plain concrete Fcu = 20 MPa for all Blinding bed works, including polythene sheets and any others required | m³ | 1.88
B | Supply and cast ready mix reinforced concrete Fcu = 30 MPa for the isolated foundations with steel reinforcement. | m³ | 2.02
C | Supply and cast ready mix reinforced concrete Fcu = 30 MPa for the GENSET foundation with steel reinforcement. | m³ | 5.76
D | Supply and cast 10cm thick ready mix reinforced concrete Fcu = 30 MPa for the Solid Slab with steel reinforcement around the GENSET foundation. | m³ | 3.44
1.4 | STRUCTURAL STEEL WORKS
A | Supply and construct a complete structural steel shed made (structural steel columns, main and secondary beams, purlins and 50 mm fiberglass insulation 25~30kg/m3 +0.50mm gauge corrugated steel sheet ceiling. , painting) . The unit rate shall include all required materials types, fabrication, welding, painting (zinc rich epoxy for prime coat, intermedite and final coats), erection, workmanship, And any others required to complete the work as per drawing and engineer instruction. | m² | 18
B | Supply and construct a complete structural steel wall made from mesh steel 1.8mm th with h.s40x40x2.8mm @1220mm vertical and horizontal. high density (150kg/m3) . The unit rate shall include all required materials types, fabrication, welding, painting (zinc rich epoxy for prime coat, intermedite and final coats), erection, workmanship, And any others required to complete the work as per drawing and engineer instruction. | m² | 104.4
1.5 | METAL, ALUMINUM & WOODEN WORKS
A | Supply and install swing metal door double leave made from mesh steel with H.S steel tubes, painted finish including all required accessories to complete the work as per drawings | m² | 10
1.6 | INSULATION/WATERPROOF WORKS / TERMIT PROTECTION WORKS
A | Supply and install granular top surface 4mm thick bituminous sheet (One Layer) under foundations for water proofing. The price shall include supplying, installing, workmanship, prime coat, overlapping and any others required to complete the works. | m² | 54.12
B | Supply and install 2 coats of water proofing bituminous paint for Isolated foundations. The price shall include supplying, installing, workmanship and any others required to complete the works. | m² | 8.56
C | Supply and install TERMIT PROTECTION layer on backfill materials to protect from termit grouth. | m² | 54.12
1.7 | SAFETY AND LIFE SAVING SYSTEM
A | Fire extinguisher ABC powder 6kg | No. | 2
B | Fire extinguisher (CO2 6kg ) | No. | 2
2 | FUEL TANK
2.1 | P.C WORKS
A | Supply and cast plain concrete (10 cm thick) B200 kg/cm² below G.L foundations of diesel tank, as well as everything else required to complete the work according to drawings, specifications, technical assert and workmanship, general and specific conditions, and supervisor engineer's instructions. | m² | 24.5
2.2 | RCC FOUNDATION
A | Supply, cast outside in open area - RCC foundation B300kg/cm2 for genset. Reinforcement shall be 60 degree threaded with a yield strength of 420 MPa and a rebar diameter of 12mm @ 20cm as specified in the drawings. The height of this foundation should be 300mm above ground level, or as recommended by the generator set manufacturer, whichever is greater. The foundation's length and breadth must be at least 250mm greater on all sides than the enclosure's dimensions. For vibration within the box, the generator must be positioned on counter mounts. The price includes all necessary filling and compaction works to prevent settlement and to achieve the required soil bearing capacity. | m³ | 3.5
B | Supply, cast outside in open area - a RCC B300 foundation and chamber for fuel tank. Reinforcement shall be 60 degree threaded with a yield strength of 420 MPa and a rebar diameter of 12mm @ 20cm as specified in the drawings. The works include the adjustment of the tank chamber slope in the direction of the drain valve, and painting the fuel tank chamber with minimum 3 coats of approved epoxy paint, all according to the instructions of the Engineer. | m³ | 5
2.3 | Fuel Tank: Supply and delivery of a complete elevated outdoor daily Steel Fuel tank with a capacity of 5000 L and a thickness not less than 5 mm, including a Sight Glass Level Measurement (Gauge) and all necessary fuel pipes, fittings, valves, filters, flow meter up to 4 ℓ/sec, suitable for diesel service, instruments and all accessories for connection to the genset base fuel tank. The tank must be applied with two layers of epoxy outside and three layers inside. | L.S | 1
2.4 | SAFETY AND LIFE SAVING SYSTEM
A | Fire extinguisher (CO2 6kg ) | No. | 1
3 | CONTROL ROOM
3.1 | EARTH WORK
A | Earthwork excavation for isolated foundations and strip walls in any kind of soil to the dimensions and levels shown in drawings(at least 1m depth for isolated footing) . Price to include backfilling with excavated soil if suitable or substituting same with selected approved imported soil, and removal of extra and unsuitable soil. Back filling shall be on layers of 200 mm thick with watering and compacting to (95%) of MDD. The item includes Disposing surplus excavated soils outside the site. | m³ | 14.9
B | Supply and Laying, spreading and compacting well graded stone in layers not exceeding 25cm, including spreading in uniform thickness, hand picking, watering and compacting to the required density, leveling, and finish the surface. Payment shall be made for the measurement of the volume of the compacted fill. | m³ | 4.9
C | Supply and Build base black "BASILTE" stone to cover the ground beams with cement mortar 1:3in first class. Texturing shall be in accordance with Engineer’s instructions and approval. Cutting, shaping and building of stone shall be in straight angles, no twisting, distortion or uneven sizes shall be allowed. The price included any work to finish work as per workmanship recommendations. | m² | 10.6
3.2 | CEMENT BLOCK WORKS
A | Supply and build concrete hollow blocks (40x20x20) cm (Automatic) for external walls with all required works. Prices of block works shall include supply of automatic solid concrete blocks from v. good and approved factory in perfect dimension and build it in good manner, cement sand mortar (1:3). Works shall include all materials, testing, scaffolds, placing of approval blocks, curing, racking out the joints, workmanship, all ducts, sleeves, opening areas, fiber board, protection concrete(B-200) around sleeve sand pipes for electrical tools and anywhere else, needed, all according to drawings, conditions and directed instructions by the Engineer. The price includes installing concrete R.C LINTEL with reinforcement above door and windows. Fcu = 25 Mpa, the length shall extend 15cm on both sides. | m² | 82
3.3 | CONCRETE WORKS
| Supply and cast reinforced concrete class(C25) including formwork, placing, vibrating, shuttering, curing, complete as directed. The price includes Supplying reinforcement of (Grade 40), size and length as detailed in the drawings, storing on site including cutting, bending and fixing in position and providing all tying wires, spacers. Item include Preliminary installations for electrical pips and floor drainage in concrete beams, and any concrete elements wherever required. The price include surface leveling, making good the harmed surfaces and edges and all surface finishing as per workmanship recommendations. For the following elements | Note
A | Isolate foundation and pedestal. item include 10cm plain concrete under RC footing. The work inclueds painting two coats of water proofing bituminous for foundation surfaces. | m³ | 4
B | Ground beams. | m³ | 2.6
C | Internal room floor slab (must be levelled and smoothed by Troweling Machine). The item inclueds ployethylene sheet under RC floor. | m³ | 5.7
D | Columns. | m³ | 1.73
E | Roof solid slab. | m³ | 9
3.4 | INSULATION WORKS
A | Supply and install roof water proofing membrane of bitumen rolls 4mm thick covered with quartz granules for main roof, parapet walls and primer coat GS at rate 25 kg/m2 installation of 15x15cm angle fillet 474 groove, groove sealant, groove cover, joints over lapping, backing sheets or pieces all around external corners roof drains, and all necessary material to complete the works as shown in the drawings and as per manufacture instructions and codes of practice. | m² | 37.8
3.5 | SCREED CONCRETE WORKS
A | Supply and cast concrete screed slab class(C25) 12 cm average thick including formwork, placing, vibrating, shuttering, curing, complete as directed. The price include surface leveling, making good the harmed surfaces and edges and all surface finishing according to workmanship recommendations. | m³ | 4.5
3.6 | PLASTERING WORKS
A | Supply and make external plastering 20 mm thick for walls with four faces: the first is the rough nail rendering (mix 1:1) cement: sand, the second is 5mm thick mortar (mix1: 2) cement: sand, the third is the undercoat 13mm (mix 1: 3) cement: sand, the forth is make Finishing Coat, smooth surface with (1:1) cement: sand mortar. and all this is according to drawings and supervisor engineer's instructions | m² | 110
B | Supply and make internal plastering 12 mm thick for internal walls and ceiling with two faces: the first is the rough nail rendering (mix 1:1) cement: sand second layer 13mm: Base‐Coat "Rendering" with (1:3) cement: sand mortar. Works include all materials needed to finish the works according to drawings and supervisor engineer's instructions. | m² | 115.5
3.7 | PAINTING WORKS
A | Supply materials and make emulsion paint (Supercryl) for external walls, sanding, priming, putty, under coat, and finishing coats, all according to Drawings, Specifications and instructions of the Engineer. The price should include preparing surface, clean, remove dust. | m² | 110
B | Supply and apply two coats of oil paints on internal walls. Price shall include surface preparation, priming, and putty. All according to Drawings and instructions of the Engineer. | m² | 80
C | Supply and apply two coats of water paints on celling. Price shall include surface preparation, and putty. | m² | 37.8
3.8 | PERIMETER SIDE WALK WORKS
A | The Perimeter side walk shall have a minimum width of 70 cm and construct from concrete Curbs 50 cm height with buried 20 cm. filled in layers with good compacting. The top surface of side walk shall cover with plain concrete 10cm thick the surface of concrete must be levelled and smoothed. The price inclueds a layer of crushed stones under the plain concrete. All according to the instructions of the Engineer. | LM | 29.2
3.9 | DOOR WORKS
A | Supply, fix and install single external steel door size (1x1.2m) made out steel tubes adjoining vertically without space (tube 50x50x1.25 mm), complete with frame (L section 50x50x0.4), item includes all accessories, handles, locks, hinges and all required accessories according to the instructions of supervisor Engineer. | NO. | 1
3.1 | ROOM ELECTRICAL WORKS
A | Carry out single phase electricity network black and red of 1x 4 mm2 + 2.5 mm2 ground wire with two ceiling led lamps (10 watt) with switches and two electricity sockets of 13A and one 16 A for ventilation with each switches. In addition to that supply and install outdoor lamp located above the door with switch located inside the door. The electricity network should include MDB with 6 circuits with circuit breakers installed inside the room next to the door. | L.S | 1
Total Carried to Summary Page 4
Sub Total (4)
Total Sum