PROJECT.

- SUPPLY, INSTALLATION, TESTING, COMMISSIONING OF One SOUND-PROOF EMERGENCY ELECTTIC POWER DIESEL-ENGINE GENERATOR FOR CHILDREN AUTISM CENTER-ADEN CITY.

TECHNICAL SPECIFICATIONS

Technical Specification

- SECTION (1) TECHNICAL SPECIFICATIONS FOR GENERATOR

  - General Site Conditions:

The de-rating for electric power generator sets shall be provide at following conditions:

- Ambient temperature Max. 50°C. Min 25°C.

- Relative Humidity Max. 98°C Min 65°C.

- Pollution type: Desert Dust and Sand Storm.

- Altitude: 100 meter ASL.

  - Scope of Work:

Supply, Install, Test, and Commission new soundproof (Canopy) (Prime) Power Diesel Generators for Children Autism Center. in ADEN city. including construction of generator room, Electrical reticulation/ cabling and Automatic / manual transfer switch panel between the new diesel generator and existing public network include all devices and equipment specified herein or required for the service:

- Main fuel storage tanks complete with all accessories as BOQs

- Electric fuel transfer pumps complete with all accessories as BOQs.

- Complete Automatic Transfer switchboards/ manual transfer, according to technical specification and BOQ.

For ADEN  facilities at the following locations:

| NO | Location | Capacity KVA | Location Coordinates |  | Qyt |
| --- | --- | --- | --- | --- | --- |
| 1 | CHILDREN AUTISM CENTER | 50-60 | 12˚48´10.98"N | 12˚48´10.98"N | 1 |

The scope of the work shall include any other works required to ensure a well-functioning Diesel Generators but not explicitly mentioned shall be the responsibility of the bidder:

- Supply of adequately rated cables, lugs, connectors, screws, nut bolts etc. required for retrofitting and other accessories, which are necessary for satisfactory operation of the DGs though not individually or specifically mentioned herein.

- All Civil and electromechanical works required for correct mounting and installation of DG, taking in consideration the existing generator is place on paved ground and concrete blocks.

- The unit shall be automatically and manually start and stop. The power supply system shall be complete in all respect for supply, installation and should be deliver ready for operation, complete with necessary fuel, coolant and lubricant to run the unit for 72 hours.

  - Inspection And Testing

    - Inspection

The generating set shall be subject to inspection by the owner, or owner's appointed representative .

Approval by any of the above inspectors shall not relieve the manufacturer of his commitments under the terms of the purchase order and this specification.

Purchaser shall be give fifteen (15) days’ notice before shipment to arrange for formal inspection

    - Testing

The generating set shall be subject to witness tests in accordance with the current Standards referenced herein and manufacturer's standards carried out at the manufacturer's works.

The owner or its appointed representative at the Vendor’s works shall witness these tests, either during site installation or during erection. The Vendor shall give the owner a’ notice before the start of any test. The tests shall include the following:

- Full functional testing to ensure proper operation of all components.

- Full load heat run for a period of 1-hour test to determine temperature rise, and to demonstrate engine and generator performance. Heating effects based on maximum design ambient shall be simulate to confirm the adequacy of the cooling system. Engine generator controls shall be use during testing. The heat run test shall be carried out in accordance with the following:

    - Test Program

- Generator control tests to demonstrate all generator trips, alarms, and changeovers from duty to standby equipment.

- Rejection of full load current at the design power factor. Voltage, frequency and load current should be record on chart recorders.

- Trip of main auxiliaries from generator fully loaded condition to demonstrate ability of emergency run down equipment.

- One hour running at 110% load Cool down

- oil temperature test and emergency test

- After acceptance, the engine water-cooling system shall be drain prior to packing for shipment.

- The test certificates shall be approve by the owner before the machines are dispatch from the manufacturer's works.

  - Materials and Equipment

- Materials and equipment to be supply shall be as per standards, and the manufacturer also well-known and equipment is commonly used.

  - Safety Protection for Personnel

- Belts, pulleys, chains, flywheels, couplings, projecting set screws, shaft keys, and other rotating parts, so located that any person can come in close proximity thereto, shall be fully enclosed or otherwise properly guarded. Engine local control panels shall be "dead format" and shall have suitable barriers or screens, wherever necessary, to protect personnel from contacting live electrical.

- Parts during normal routine use. Removable panels that, when removed will expose live electrical parts, shall have warning declare thereto.

  - General Requirements

- The diesel engine shall be directly couple to the alternator. The diesel engine, alternator, lubrication Oil filters, fuel oil filters, lubrication Oil strainers, fuel oil strainers, and lubrication Oil coolers and other accessories deemed necessary by the manufacturer shall be mounted on a common steel fabricated base plate of sufficient strength to adequately support all equipment mounted on it, without distortion, either during operation or shipment.

- The steel base plate shall be support on steel springs, working as vibration isolators specifically designed for the weights involved. The isolators shall be furnished as a part of the equipment. All pipes connections between the engine and accessories such as air intake and exhaust: shall be flexible connections. These flexible shall be furnished as a part of the equipment. Owing to elastic suspension, the set should always have the possibility to move freely surrounding structures.

- The diesel engine exhaust pipe shall be complete with silencer to eliminate noise and flexible joints to eliminate transport of vibration.

  - Submittals

Submittals for approval shall be include but not be limited following:

- Component List - A breakdown of all components and options.

- Technical Data - Manufacturer produced generator set specification or data sheet identifying make and model of engine and generator, and including relevant component design and performance data.

- Auxiliary Equipment - Specification or data sheets, including, transfer switch, battery charger, jacket water heater, main circuit breaker etc.

- Drawings - General dimensions drawings showing overall generator set measurements, mounting location, and interconnect points for load leads, fuel, exhaust, cooling and drain lines.

- Warranty Statements - Warranty verification published by the manufacturer.

- Service - Location and description of supplier's parts and service facility including parts inventory and number of qualified generator set service personnel.

  - Warranty

The manufacturer shall have a local authorized dealer who can provide factory-trained service members, the required stock of replacement parts, technical assistance, and warranty administration. (One YEAR FACTORY WARRANTY SHALL BE PROVIDED).

  - Technical support

    - Training

- The supplier shall detail their capacity for delivering training courses in installation, commissioning, operation and maintenance of al equipment across their local service centers and/or requested locations. (the provision of these training courses is not to be included in this offer).

- The supplier shall also outline the content, and various levels, of their training courses.

    - Guarantee

The Supplier shall state and guarantee of following:

- Fuel usage rates at 110%, 100%. 75% and 50% prime  rated output (g/kWe) and corrected values as noted.

- Maximum net output (kWe) of each diesel generator

- prime net output (kWe) of each diesel generator.

    - Manuals, Catalogues and Electrical Drawings

Manuals, catalogues and drawings and any other documentation supplied shall be available in English, the following manuals and catalogues shall be supplied with each generating set:

- Engine and alternator Manuals.

- Generating set operation Manual.

- Control installation and operation manual

- Maintenance Manual.

- Troubleshooting Manual.

- Workshop and Spare Parts Manuals and catalogues. g) Electric diagram.

In particular, the appended manuals should contain the following information:

      - Operating Instructions:

The Instruction Manual shall include detailed Operating Instructions and, as a minimum, should cover starting, stopping, protection of circuits, automatic controls, battery charging, safety considerations, method of adjustment of speed, output voltage, control timers, etc.

Performance parameters of the generator set shall be detailed for the operator's guidance and as a minimum should cover output voltage, frequency, load, engine temperature and oil pressure nominal values and acceptable limits. Circuit drawings with component identifications shall be included for reference purposes.

      - Maintenance Recommendations:

The supplier shall provide complete maintenance procedures for all the equipment supplied. Schedules for maintenance to be effected on a daily, weekly, monthly, etc. or on hourly run basis should be included.

Guidelines for the selection of fuel oil, lubricating oil, use of water treatment additives and anti-freeze if applicable.

      - Troubleshooting:

Troubleshooting procedures shall be available to enable the timely diagnosis of a defect considered likely to occur in service. Reference outputs and conditions shall be quoted to facilitate diagnosis.

Note: It is mandatory that one set of above manuals, catalogues, and electrical drawing/diagram for each category of the offered generating sets is supplied with the bid (electronic versions). Bids shall not be acceptable unless the offer includes these items.

  - Generator Unit (Set):

    - Diesel Engine:

      - General

- The diesel engine shall be of the turbocharger, after cooled type with the following characteristics:

- The engine shall be of the vertical, four strokes, cold starting.

- The engine shall be capable of running satisfactorily with fuel oil and lubricating oil of grades and standards used in ADEN – Yemen.

- The engine speed regulation shall not exceed ± 10% for the momentary and ± 6% for the permanent change when the full load on the engine is suddenly thrown off or put on, respectively.

- Provision shall be made for varying the engine speed within 6% above or below the normal speed at all loads.

- The engine shall be provided with a control panel as mentioned hereafter.

      - Engine Rating

- The engine when running at 90% of its continuous rated output at site shall be capable of driving the alternator when delivering its full load output, i.e. the power of the engine shall be nearly 10% in excess of the power of the alternator.

      - Supercharging

- The supercharging of the diesel engine shall be achieved by means of charging blowers utilizing the energy of exhaust gases. An after cooler must be fitted in the air manifold for cooling air before entering the engine cylinders.

      - Cylinders, Liners and Cylinder Cover

- The engine shall be multi-cylinder type provided with removable cylinder covers and renewable liners, furnished with water jacket of ample size, avoiding any pockets, which may cause accumulation of deposits from the cooling water.

      - Duplex Fuel Oil Strainer and Filter

- Fuel-flow strainers shall be provided ahead of the engine fuel pump. The fuel-flow filters shall be provided after the engine fuel pump. Strainers shall be of the metal edge or screen type as recommended by the engine manufacturer. The filter case shall have inlet and outlet connections plainly marked. The case shall be mounted in an accessible location, which will permit changing strainers and filter elements without disconnecting the piping or other engine-mounted equipment.

      - Engine Fuel Pumps

- Engine fuel pumps shall be of the positive-displacement, engine-driven type and capable of sullying the necessary quantity of fuel under all conditions of operation. Relief valves shall be provided to prevent equipment damage due to buildup of excessive pressures, which might result from restrictions in the discharge lines. In addition, a hand-operated fuel oil priming pump shall be provided.

      - Fuel Oil Drip

- Nozzle drip lines, overflow, … etc., shall not drain on the floor. Means shall be provided for collecting these lines, and return of excess fuel to the day tank automatically.

      - Fuel Oil Lines

- Fuel oil lines shall be provided with solid connections between fuel piping and engine.

      - Lubricating System

- The engine lubricating system shall operate and be maintained at a predetermined constant pressure by means of an engine-driven positive-displacement lubricating oil pump. Relief valves, a pressure gauge, and automatic safety feature, to sound an alarm and shut down the engine at a predetermined lubrication oil pressure by closing contact, shall be supplied. To maintain proper oil temperature, if deemed necessary, lubrication system shall be provided with water cooler.

      - Oil Cooler

- One shell type or plate type cooler arranged to utilize engine-cooling water as the oil-cooling medium, shall be furnished with the engine. The capacity and construction of the unit shall be as recommended by the engine manufacturer. Suitable connections shall be furnished for connections between the engine, radiator, and oil cooler as required.

      - Lubrication Oil Strainers and Filters

- Duplex full-flow filters shall be provide in the lubrication. Oil line. The filters shall be of the cartridge type.

      - Lubrication Oil Priming Pump

- An electrically operated priming pump shall be provide for priming the engine lubricating system prior to starting. The pump shall be of suitable capacity. The pump shall be mounted on the engine and shall be factory completed. A manual pump shall also be provide as stand-by. Starting of engine without priming can be accept if the engines' manufacturer recommends it.

      - Exhaust System

- The exhaust system shall include a flexible section, condensate drain, muffler-silencer, weather cap and all necessary accessories.

- Exhaust piping shall be of the diameter recommended by the diesel manufacturer. The flexible exhaust connection shall be stainless steel. The exhaust silencer shall be of heavy duty, side inlet and end outlet, designed for vertical installation. It shall be of size and design that will ensure durability, prevent backpressure and provide medium degree silencing. Flanged connections shall be provided at each end of the silencer. All companion flanges shall be furnished, installed and securely attached to the housing. Exhaust system components shall be painted with high temperature aluminized paint. Each flanged joint shall be provided with 1/16" asbestos, full-face gaskets.

      - Air Intake System

- The engine shall be equipped with heavy-duty oil bath or dry type air cleaner (S) of sufficient capacity to protect working parts of the engine from dirt or grit. The air-cleaner shall be equipped with a pre-cleaner and a restriction indication. A crankcase breather shall be included. In-line air inlet silencer shall be provided between the turbocharger and air inlet.

      - Speed Control Governor

- The engine shall be equipped with a full hydraulic isochroous governor, which shall be mechanically driven by the engine, and which shall hold engine speed to within ± 5% of any selected speed at any constant load form no-load to full-load.

- The governor shall control speed smoothly but positively and shall be fitted with stabilizing or compensating device to preclude hunting or over travel. The governor shall prevent variation in speed of the sustained periodic type (Hunting) and shall limit variation in speed of

      - Flywheel

- The flywheel shall be adequately protect by means of removable guards. An appropriate means shall be provided for barring.

      - Emissions standers

- The engine shall be meet Tire 4 final emission standers .

  - Alternator

    - Design Data

- The alternator shall be directly connect to the engine flywheel through a coupling designed and supplied in accordance with alternator manufacturer requirements.

- The alternator shall be of three phase, synchronous, drip proof, self-excited with built in exciter machine and voltage setting rheostat, provided with special windings for reduced harmonics and arranged for parallel operation with similar unit.

- Insulation shall be of tropical and moisture proof type, class (F).

- The alternator shall be of the following technical data:

Power 	As mentioned in B.O.Q

Power factor	0.8 – 0.85

Efficiency	Minimum 92%

Voltage	400 V

Frequency	50 Hz

Speed not exceed	1500 r.p.m

Voltage dip at starting not exceed	15%

Overload rating	10% for two hours

Short circuit rating	300% of alternator capacity symmetrical for 10 seconds.

Temperature rise over ambient temperature.	65°C

Maximum harmonic content	1.10

Ambient temperature	50°C

    - Exciter

- The exciter shall be brush less and its armature shall be directly connected to the alternator shaft. It shall be of the alternator type and have a solid-state, hermetically sealed rectifiers mounted directly on its armature. The rectified exciter output shall be directly connected to the revolving alternator field windings without brushes, slip ring or communicators. The excitation system shall be equipped with a series of boots transformers or permanent magnet generator for field forcing capabilities.

    - Automatic Voltage Regulator

- The AVR shall be of a solid state electronic . The AVR shall be manufactured such that it will maintain electrical properties, even under severe overload, under/over voltage and under/over frequency conditions. Input correction range shall be -30% to +20% of nominal input voltage. The system design shall be capable of operating at an input frequency range of -15% to +10% of nominal, without clearing protective devices or causing component failure within the AVR. When generator or utility power is restored, the AVR shall automatically restart. Upon turn on or restart, the output of the AVR shall not exceed the specified output regulation limits.

  - Main Line Circuit Breaker, Control and Instrument Panel:

- The main line circuit breaker shall be mounted and connected in a guarded drip-proof enclosure meeting IP 22 and IEC 144.

- For generating unit, a main line circuit breaker with shunt trip to protect generator set from accidental faults and to disconnect it from its load shall be supplied. (It shall be with min. rating Amps as specified at BOQs).

- The control and instrument panel shall be provided. This panel shall be mounted on to the alternator and shall be provided with vibration isolators of adequate size to protect the instruments and control from vibrations. The following minimum instruments and control shall be provided.

- Lubrication Oil from engine.

- Engine water temperature, high-shut down of the engine.

- Engine, over speed and visual alarm.

  - Starting of the Generating Units

    - Electric Starting System

- The engine shall be equipped with a 12/24 VDC solenoid shift electric starter capable of withstanding four, 30 second consecutive cranking periods.

- The starting battery shall be Lead Acid, especially designed for diesel engine cranking service and of a capacity as recommended by the battery manufacturer for cranking the engine being furnished, for the necessary break-away current as required and spinning current for four consecutive starts of thirty seconds of cranking on each start, or for 60 seconds of continuous cranking without being recharged and with the ambient temperature of both the engine and battery of 45°C. Steel battery rack shall be secured to the mounting skid and the battery shall be secured to this rack.

- A complete automatic battery charger shall be furnished for charging the lead acid battery being supplied. The charger shall be the static type, magnetic amplifier control with direct current voltmeter, direct current ammeter and potentiometer for voltage adjustment and shall have float and high charge rate, with a 0 to 24 hour high rate charge timer. Charge rate shall be automatically determined by the state of the battery and reducing to milliamp. Current to fully charged battery. Charger shall be for 220 volt, single phase, and 50 Hz alternating current input, with an output of not less than 6 percent of the nominal ampere-hour rating of the battery. A time delay under voltage relay shall be provided within the charger for remote alarms. The charger shall be for the correct voltage for the battery. The charger shall be mounted inside the pump housing.

- Required battery cables shall be installed for connecting the battery to electric starter.

  - Cooling System

- The engine shall be water-cooled of a closed type system, with liquid to air radiator supplied with blower fan(s) to maintain desired operation conditions. The radiator unit shall be of the indoor or outdoor type designed for operating 10% continuous overload at 50°C ambient temperature.

- All connections to the engine and its mounted accessories shall be solid. The radiator shall have an engine driven fan of adequate size.

- The system shall not be susceptible to the formation of deposit of rust and scale within the engine, and shall circulate the coolant through the engine at a regulated temperature and flow rate as recommended by the manufacturer.

- A jacket water temperature control valve shall be provided. It shall be of thermostatic type with 3-way body and flanged connections. The thermostatic element shall be designed to maintain the jacket water temperature within the requirements at stated by the engine manufacturer.

- The system shall also include a separate path of lubrication Oil cooling.

- Similar approved type can be taken into consideration.

- Gen sets shall be equipped with a cooling system having sufficient capacity to effectively cool the engine when delivering full rated horsepower at the conditions stated above. A radiator and engine-driven fan of a type and capacity recommended by the engine manufacturer shall be included.

- The radiator shall be sized in accordance with the engine manufacturer’s recommendation for use with 50 percent aqueous ethylene glycol. Air flow shall be controlled by a power inlet damper and a gravity discharge damper, Design ambient air temperature shall be 50 degrees C at sea level.

- Gen sets shall have an engine-driven, gear driven centrifugal type water circulating pump for circulating water through the cooling system.

  - Manual Transfer Switch (M.T.S)

- The Manual transfer switch shall have an electrical rating on the normal power source side of 400 volts, not less than the specified value at BOQs, 50 Hz frequency, 4 poles, and on the alternator power source side of 400 volts, not less than the specified value at BOQs, 50 Hz frequency, 4 poles,

- CONTROLS

- Automatic transfer switch.

- Auto start / stop and Emergency stop.

- Lamp test.

- Cycle crank.

- Voltage control.

- Cool down timer.

- Phase selector switch.

- Load demand relay.

- INDICATING LIGHTS

- Low oil pressure.

- High coolant temperature.

- Over speed.

- Emergency stop.

- Fault shutdown and Fault alarms.

- 3 spare lights / 4 spare inputs, customer programmable (shutdown or alarm) to spare alarm or fault Leeds and Over crank.

- PROTECTIVE RELAYING

- Programmable relays.

- Over / under voltage.

- Reverse power relay.

- Over / under frequency and over current.

- LOW VOLTAGE CIRCUIT BREAKERS

- Low voltage circuit breakers shall be metal clad and shall be of the air break, horizontal draw out pattern 400 volts and rupturing capacity as mentioned in the drawing. Circuit breakers shall comply with VDE or BS 4752 & IEC 60439 and shall be complete with the auxiliary equipment described for high voltage circuit breakers. The circuit breakers closing mechanism shall be of the trip-free type and shall incorporate a mechanical "ON/OFF" indicator and mechanical interlock in order to prevent withdrawal, plugging or access to the breaker in the closed position.

- Contactors shall be robust in design and shall be capable of carrying full load for an indefinite period, and shall be provide with an arc-quenching device. Contacts shall have readily renewable tips. The live fixed contacts shall be fully shroud.

- LOW VOLTAGE FUSED SWITCHES / ISOLATORS

- Fused switches shall be of the heavy duty type complying with VDE No.0670 part 1/1.64 and shall be equipped with detachable neutral links and class Q1HRC fuses to VDE No.0670 part 4/3.67.

- Fused switches shall be of the triple pole and neutral type or heavy duty composites unit of the air break switch type and have not more than one fuse in any one pole, the fuse being contained in or mounted on the moving member or the switch. The neutral shall be either switch or taken through a removable link. A separate brass earth terminal shall be provide.

- Isolators shall be identical to fuse switches but the fuse links shall be replace by high conductivity copper link.

  - Earthing System:

- The Contractor shall Supply, installing, testing, and commission-earthing installation in accordance design of the system and all items shall be according to BS 7430, with the IEE Wiring regulations BS 7671. The system of PVC conduits and trunking, metallic sheaths of cables, cases and enclosures of switchgear and electrical apparatus shall be connect to the earth point, according to the current rules and regulations. The Contractor is remind that the resistance of the earth conductor from the earth-electrode to any point in the earthing system shall not exceed one ohms as per ANSI IEEE Standard 80.

- Codes of practice and highest prevailing engineering standards for the following main system component:

- Extendible copper electrodes, (suggested length: 1.6~2.4 m),

- Main earthling cable: copper bared as per BOQ and the length as required. And earthling cables for Gen. sets, hanger frame, fuel tank and any other equipment: insulated copper as per BOQ, Cupper earthling bar, Earth pit with manhole cast iron cover plate complete as per standard, the cover of the manhole is preferred be clearly stamped with grounding sign.

- Ground Enhancement Material (Bentonite / (Salt & Coal) 50kg.

- Earthing busbar shall be protected fixed inside sealed box

  - Cables

- Cables shall be supplied by an approved manufacturer and where possible the same manufacturer shall be used for all cables and according to IEC 60228,   IEC 61537, ISO, IEC 60227/IS 694, IEC 60502/151554 standards. In addition, the Calculations of the current rating of the cables should be according to IEC 60287.

- Rating :

- The Contractor shall ensure that each cable is adequately rate for its duty under normal and possible fault conditions.

- The rated voltage of the cable shall not less than the operating voltage and when assessing the rating and cross section of each cable the following factors shall be taken into account:

- Maximum voltage drop permissible.

- Type and magnitude of load.

- Fault level and duration related to circuit protection relays and fuse gear.

- Over current setting of relays and circuit breakers.

- Route length and disposition of cables.

- Ambient temperature.

- Method of laying.

- Type :

- Cables complying with VDE or approve equivalent standards will be accepted provided all cables, which are supplied for a specified operating voltage, are to the same national standard. Standards specified in the following clauses indicated the type of cables used in the design: if the contractor wishes to use cables to alternative standard then details of current carrying capacity, de-rating factors ect, shall be submitted to the Engineer for approval.

a)	XLPE/SWA/PVC:

- Power cables specified as cross-linked polyethylene insulated steel wire armored and PVC sheathed are hereafter refer to as XLPE/SWA/PVC.

- All such cables shall be terminate with mechanical glands, which shall be of a type as to provide adequate mechanical support by positively locking on the armor and shall at the same time give a high level of earth continuity.

b)	PVC/SWA/PVC:

- Power and control cables specified as PVC insulated and sheathed, galvanized single wire armored cable with an overall PVC sheath are hereinafter referred to as PVC/SWA/PVC.

c)	MICC/PVC:

- Certain control and miscellaneous circuits shall be carry out in mineral insulated copper clad cable with an overall extruded PVC sheath, hereinafter referred to as MICC/PVC cable.

- For the purposes of core phase identification colored PVC core sleeves or colored PVC extension sleeves shall be use. Core sleeves and extension sleeves to be use on the core sizes for which they are intend.

  - System Accessories

Cable Tray

- Perforated type Galvanized steel cable trays, cable tray covers, clamping bolts and other cable tray accessories such as coupler plates, bends, tees, reducers, vertical elbows in manufactured accordance with ASTM A653 SS, Grade 33, coating designation G90.

- Hot-dip Galvanized Steel: Straight section and fitting side rails and rungs shall be made from steel meeting the minimum mechanical properties of ASTM A1011 SS, Grade 33 for 14 gauge and heavier, ASTM A1008, Grade 33, Type 2 for 16 gauge and lighter, and shall be hot-dip galvanized after fabrication in accordance with ASTM A123.

- Perforated cable trays must conform to IEC 61537 and EN ISO 1461 standard.

  - DG Room

- The unit rate shall include all required materials types, fabrication, welding, painting, erection, workmanship, sand bags, lighting with its wiring and switches , and any others required to complete the work as per drawing, specification and engineers’ instructions.

  - DG built in fuel tank

- The DG built in fuel tank capacity should not  be less than below

| DG built in fuel tank |  |  |
| --- | --- | --- |
| N.O | DG Capacity in KVA | build-in Fuel Tank Capacity in liter |
| 1 | 50-60 | 70-100 |

  - Concrete work

- The bidders are requested to refer General Notes, Pricing Preambles, Drawings, Specifications, Conditions of Contract, Special Conditions of Contract and all other relevant documents prior to pricing of the following items.

- • All Concrete Works shall comply to the specifications,

- • Contractor shall ensure that all contacting surfaces including reinforcement dowels left out for bonding purposes is free from any organic or artificial material which can be a hindrance to achieve specified properties in the Drawings and Specifications.

- Rates for lean concrete shall include for preparation of bottom of excavation prior to pouring of lean concrete.

- Rates for formwork shall include for control joints, isolation joints wherever specified and required according to the drawings and specifications.

- Rate for concrete shall include for construction joint, isolation joint, expansion joint, with dowel bars, end cap and compressible filler with sealant on top as per drawing.

- Rates for concrete shall include all necessary tests by an Authority acceptable to the Engineer.

- Formwork for buried concrete may be of timber, for all other concrete, shall be 15mmthick plywood.

- Rates for concrete shall include all necessary equipment which are required for concreting. Rate shall include for continuous curing for 7 days.

- The size of reinforcement bars comply BS 4449 described in the drawing or elsewhere shall be the minimum size and the rolling margin and any other tolerance shall be wholly above this size.  Hooks and laps have been measured and included with the quantities for reinforcements.

- All reinforcement shall be free from mill scale, dirt, oil, paint, grease or loose rust before fixing in position and shall be brushed with a stiff wire brush if so directed by the Engineer.

- Reinforcement shall be bent cold by applying a slow even pressure on an approved type of bending apparatus.

- Re-bending of incorrectly bends bars shall not be attempted.

- Rates shall include for cutting, bending, fabricating, placing in position, holding and supporting including temporary fixing supports, hangers, binding wire spacers, laps and waste.

- Rates shall include for working in difficult conditions.

  - Recommended Spare Parts for the Warranty

- Recommended Spare Parts for the Warranty period and continuous operating for one year by separate list.

  - Recommended Maintenance Spare Parts for the Whole Maintenance

- Recommended maintenance spare parts complete set one time during the whole maintenance period by separate list (include piston rings, main bearing, rod bearing, valve rotators and crankshaft seals turbocharger oil pump water pump and all other important parts).

  - Tools

- Recommended tools set of system tools by separate list.

  - Applicable standards

IEC 60364-1, IEC 60364-4-41, IEC 502, IEC 811, IEC60034-1, ISO3046, ISO8528, NEMA MG1-22, NEMA MG1-33, NFPA37, NFPA70.

- SECTION (2) TECHNICAL SPECIFICATIONS FOR PV

2.1. Background

The conflict in Yemen has significantly worsened the already low electricity access level with severe impacts on urban public services as well as commercial and industrial activities, which all rely heavily on a functioning power supply. Fuel is scarce and many electricity generation facilities have been damaged.

The national grid has disintegrated into several subnational systems because transmission links were damaged or ceased operations due to the conflict. Consequently, public electricity supply has been completely shut down in large areas of the country, including major cities such as Sana’a, Al Hodeida and Taiz. Only an estimated ten percent of the population has access to reliable electricity. Light emissions visible from satellite imagery indicate that electricity consumption has decreased by about 75 percent. The impact on facilities dependent on reliable electricity has been devastating. Hospitals, water pumping stations, water treatment stations, industry and commercial facilities have all had to cut back operations or find alternative power sources.

The aims of this sub-project is to provide critical public services facilities, including health services and schools with sufficient electricity to run their daily life in urban areas.

2.2 Objective

The purpose of this sub project is to provide sufficient electricity access for Autism center located in Aden with a total capacity of not less than 10.2 kWp.

2.3 Scope of Work

| No. | Facility Name | Location Coordinates |  | Cat. No. | Type | PV Capacity kWp | Inverter kVA | Battery Ah @ 2VDC |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | Children's Center For Autism | 12˚48´10.98"N | 45˚02´18.75" E | 1 | Rehabilitation center | 10.2 | 3 X5 | 48X 800 |
|  | Total |  |  |  |  | 10.2 |  |  |

The scope of work includes supply, delivery, installing, testing, commissioning, operating, handing over and maintaining a solar PV off grid systems for Children Autism Center-Aden as presented

in the table 1

Table 1: Facility information

- Bidders shall submit data sheets/ catalogues for all of the proposed material including but not limited to PV modules, battery inverter, charge controller, DC cables, AC cables, DC junction box, AC coupling panel, Main Distribution Board (MDB), LED lights and air conditions;

- The contractor will be responsible for providing training course focusing on system operation, maintenance and management, the scope of training and schedule shall be proposed by the contractor and approved by UNOPS engineer;

- The contractor is responsible for set up a protection system against lightning, any equipment fails due to lightening will be replaced by the contractor and on his own cost;

- Installation of PV systems components shall be done in accordance with manufacturer operation manual;

- The awarded bidder will be responsible for setting up a battery management plan in line with Environmental Point of Practice;

- The contractor should take into account the site condition in terms of obstacles and shadings;

- Outdoor cables shall be housed inside galvanized steel cable trays;

- The contractor shall supply all the required components required for data logging and monitoring;

- All electrical works shall comply with the manufacture instructions and regulations;

- The contractor will be responsible for balancing the existing loads to the three phase panels;

- The contractor will be responsible for dismantling the old MDB and replace it with new MDB where applicable in accordance with specifications and drawings.

- The contractor will be responsible for connecting new EMDB and integration with existing MDB, in accordance with the specifications and drawings;

- The contractor will be responsible for installing, wiring and connecting new SDB as presented in the drawings including wiring of essential loads from old SDB to new SDB.

- The contractor will be responsible for dismantling old FLO light and replace it with new LED;

- System configuration, testing and commissioning should be carried out by an experienced electrical engineer.

- The contractor shall provide permanent equipment marking, labelling and signage for the project;

- It is the contractor responsibility to clean the modules once the construction work is completed;

- Control room shall include two air conditioning split units with alternate operation and temperature control unit, also include the control for alternate operation within AC main grid panel or in separate.

3.1 System Commissioning

- The contractor shall provide a time plan and test procedure for the process of commissioning;

- The contractor shall prepare a commissioning report and carry out all needed test procedures of commissioning. The commissioning process should be witnessed and approved by UNOPS;

- Such testing should include the following tests as minimum:

- Cable insulation and continuity test:  such tests should be carried before commending installation;

- System earthing test;

- Battery testing which includes the following:

- Ensure that batteries are fully charged by measuring the terminal voltage, if not batteries should be charged before carrying out testing and commissioning;

- Battery Inspection and Cleaning: A visual inspection should be done to assess the general condition of the system’s batteries. Check for any electrolyte leak, cracks in the batteries, or corrosion at the terminals or connectors;

- Terminals and connections: ensure that all terminal and connections are tight, and making sure that the same cross section is used for jumpers, measure the negative and positive pole cable length to ensure that its equal.

- Module testing which includes the following:

- Checking the cleanness of surface (glass) area of the module as it should be free of any dirt and dust;

- PV modules Visual Inspection: A visual inspection of the modules should be done to check for defects in the modules such as cracks, chips, de-lamination, fogged glazing, and discoloration, this should be done for the front glass and back sheet;

- PV modules connector and cable Inspection: Check the sealing gels of the junction box to ensure it have no crack or crevice;

- Ensure that all modules have been tested before shipping by double checking the flash reports;

- DC voltage measurement: This can be done either on the modules level or on combiner box level;

- Inverter and Charge Controller

      - Ensuring that all components are free of dust, if not, a dry cloth should be used to wipe away any accumulated dirt/dust;

      - A visual inspection should be done to ensure that all the indicators such as LED lights are working and a check on the tightening of the bolts both DC and AC;

      - Charging: The charge controller should indicate that the system is charging when the sun is up, the charging current should be measured for each string/ array;

      - If such measurement were taken at noon time, the charging current should be close to the maximum current;

      - Discharging: checking that the battery is discharging when connected to the load;

      - Inverter: Checking the voltage and current in the inverter, measuring the output voltage and frequency;

- Wiring, Connections and Electrical Panels: Wiring installations should be checked for any cracks, breaks or deterioration in the insulation/conduits, inspect connections for any corrosion and/or burning. Switches should not spark when turned on or off;

- Combiner Boxes and fuses Box: must check strings fuses using a multi meter (continuity test on each fuse) to insure no blown fuse exist, check the tightening of the bolts of the fuse holders should be checked as per manufacturer manual, visual check of the cables and fuse holders;

- AC Panels: After switching off loads and inverters, check the functionality of the RCDs and RCBOs by bushing test button and noticing the breaker open, check the tightening of all cables bolts as per manufacturer manual, visual check of all cables and breakers.

- Load balancing shall be performed if required over all three phases panels and connections

3.2 Training Program

- The contractor shall include in his tender cost of training of operators and maintenance staff and local focal point;

- The training should focus on three major topics which are listed below, and it shall be provided at the site level to ensure competence in the operation and maintenance of the system provided, it shall include hands on training;

- The training program shall include but not limited to the following elements and activities:

- System safety and Operation

- System description including system features, components and their functions, system software and interface;

- Running PV system safely;

- System operating procedures;

- System operating characteristics;

- System limitations;

- On-site system operation.

- System Maintenance

- System and components and simple troubleshooting;

- On-site inspection and operation and maintenance

- Schedule of maintenance, safety checks and procedures

- Types of alarms and notifications;

- Energy Efficiency

- Contractor should provide basic training to all staff on energy efficiency best practices and energy efficient alternatives;

- Customized basic energy management session for each site to all users on which appliances they can run using the solar system;

- Printed leaflet should be available in Arabic presenting system on/off operation, simple troubleshooting and basic maintenance;

3.3 System Warranty and After Sales

- Bidders shall include in their offers system maintenance for 2 years, bidders shall provide necessary equipment and components to run the system safely;

- Bidders shall also carry out periodic preventive maintenance visits at least one visit each three months, the scope and nature of such visits shall be consulted and agreed with UNOPS engineer, bidders are entitled to provide signed checklist by the end-user.

The preventive maintenance shall but it shall include the following as minimum:

- Battery System: A visual inspection should be done to assess the general condition of the system’s batteries. Check for any electrolyte leak, cracks in the batteries, or corrosion at the terminals or connectors. Ensure that all terminal and connections are tight;

- PV Modules: Checking the cleanness of surface (glass) area of the module. A visual inspection of the modules should be done to check for defects such as cracks, chips, de-lamination, fogged glazing, and discoloration. Check the sealing gels of the junction box to ensure it have no crack or crevice;

- DC voltage measurement: This can be done either on the modules level or on combiner box level.

- Charge Controller/ Inverter: Ensuring that all components are free of dust, if not, a dry cloth should be used to wipe away any accumulated dirt/dust; A visual inspection should be done to ensure that all the indicators such as LED lights are working and a check on the tightening of the bolts both DC and AC;

- Electrical Panels: Wiring installations should be checked for any cracks, breaks or deterioration in the insulation/conduits, inspect connections for any corrosion and/or burning. Switches should not spark when turned on or off;

- Combiner Boxes and fuses Box: must check strings fuses using a multimeter (continuity test on each fuse) to insure no blown fuse exist, check the tightening of the bolts of the fuse holders should be checked as per manufacturer manual, visual check of the cables and fuse holders;

- AC Panels: After switching off loads and inverters, check the functionality of the RCDs and RCBOs by bushing test button and noticing the breaker open, check the tightening of all cables bolts as per manufacturer manual, visual check of all cables and breakers.

- The bidder shall assign a service technical personnel (local focal point) to provide satisfactory and uninterrupted services during the maintenance period, bidder shall respond within 2 days from the date of the intimation of fault, carrying out system maintenance and troubleshooting, carrying out preventive maintenance protocols and procedures, update the system software and interface when needed, and keep records and activities log

- It’s the bidder sole responsibility to establish sufficient inventory of spare parts to run the system without interruption during maintenance period;

- The bidder shall provide necessary labels highlighting warranty details and phone numbers to call in case of problems;

3.4 Final Completion

- The Contractor shall complete any required document or list, clean up the construction site and remove any temporary structures, equipment or services, and construction debris;

- Copies of all final approvals and certifications shall be provided to UNOPS.

- The Contractor shall provide three (3) hard copy sets and one soft copy of the final Project as-built documentation