Section III: Returnable Bidding Forms

eSourcing reference: RFQ/2020/16759

Note to Bidders: The following returnable forms are part of this RFQ and must be completed and returned by bidders as part of their quotation. Instructions to complete each Form are highlighted in blue in each Form. Please complete the Returnable Biding Forms as instructed and return them as part of your quotation by uploading them against their specific Document Checklist in the UNOPS eSourcing system.

Form A: Quotation submission form

Bidders are requested to complete this form, sign it and return it as part of their bid submission. The bidder shall fill in this form in accordance with the instructions indicated. No alterations to its format shall be permitted and no substitutions shall be accepted.

Date: [Insert submission date]

Subject: Quotation for the supply of [Insert a brief description of goods/services] in [Name of country/city], RFQ Case No. [Insert RFQ ref number], dated [insert date]

We, the undersigned, declare that:

  - We offer to supply in conformity with the bidding documents, including the UNOPS General Conditions of Contract;

  - Our quotation shall be valid for the period of time of [insert number of days which shall not be less than the specified in the Tender Particulars section, Period of Validity of Quotations] from the date fixed for the submission deadline as set out in the RFQ, and it shall remain binding upon us and may be accepted at any time before the expiration of that period;

  - We have no conflict of interest in any activity that would put it, if selected for this assignment, in a conflict of interest with UNOPS [If you have any actual or potential conflict of interest as defined in Article 3 of Section I: Instructions to Bidders, please disclose it here];;

  - Our firm confirms that the offeror and sub-contractors have not been associated, or had been involved in any way, directly or indirectly, with the preparation of the design, terms of references and/or other documents used as a part of this solicitation;

  - Our firm, its affiliates or subsidiaries—including any subcontractors or suppliers for any part of the Contract—has not been declared ineligible by UNOPS, nor is included in the suspended/ineligibility list of the UN/PD, other UN Agencies, the UN Security Council, and the World Bank, in accordance with Instructions to Bidders Article 3, Eligibility;

  - We embrace the UN Supplier Code of Conduct and adhere to the principles of the UN Global Compact;

  - We have not declared bankruptcy, are not involved in bankruptcy or receivership proceedings, and there is no judgment or pending legal action against them that could impair their operations in the foreseeable future;

  - We have not offered and will not offer fees, gifts and/or favours of kind in exchange for this RFQ and will not engage in any such activity during the performance of any Contract awarded.

I, the undersigned, certify that I am duly authorized by [insert full name of bidder] to sign this quotation and bind [insert full name of bidder] should UNOPS accept this quotation:

Name: [complete]

Title: [complete]

Date: [complete]

Signature: _____________________________________________________________

Provide the name and contact information for the primary contact from your company for this quotation:

Name: [complete]

Title: [complete]

Email address: [complete]

Telephone: [complete]

# Form B: Price Schedule Form

Bidders shall fill in this Price Schedule Form in accordance with the instructions indicated.

RFQ reference no: [insert RFQ reference No.]

| Currency | USD |
| --- | --- |

| Item | Description | Qty (a) | Currency USD |  |
| --- | --- | --- | --- | --- |
|  |  |  | Unit price DAP | Total price DAP |
| 1. | Water Treatment Plant for Hemodialysis Equipment | 1 | insert | insert |
|  | Cost Break down: |  |  |  |
| 1.1 | Main Feed Pumps Supply and install main feed pumps set consists of two pumps, one duty and one standby, each of 4.8 m3/hr. flow rate, and 3 bar head, - 304St.St. pump body, impeller & shaft, complete with control panel, pressure control unit and motor protection, suction & discharge hygienic isolation valves, & check valve, pressure gauges, and steel bases with vibration absorbers, control and electrical wiring, and any other element to put the system in good operational conditions as per Specifications and UNOPS engineer instructions and approval. 1. Ref. FWP (SET consists of two pumps) | 1 | insert | insert |
| 1.2 | Sediment Cartige Filter 5 Micron Supply and install sediment cartige filter, polypropylene, #20 slim, 5 micron, 20 inch length, 125 psi, 3/4 inch, complete with hygienic isolating valves, and pressure gauges, as per specifications, and UNOPS engineer instructions and Approval. 1. Ref. 5 Micron Filter 2.4 m3/hr. | 2 | insert | insert |
| 1.3 | Automatic Activated Carbon Cartige Filter Supply and install automatic activated carbon sediment cartige filter, granular activated carbon 20 inch length, 125 psi, 3/4 inch, complete with hygienic isolating valves, pressure gauges, as per specifications, and UNOPS engineer instructions and approval. 1. Ref. Automatic activated carbon cartige Filter 4.8 m3/hr. | 1 |  |  |
| 1.4 | Duplex Softener set Supply and install automatic duplex softener, consists of two vessels, duty and standby, meter initiated, 125000 grain each vessel, 4.5 ft3 each vessel, (16”dia x 65”), brine tank not less than 100 L, HDPE cover and air check valve. complete with all accessories, fittings, control, pressure gauges, valves, and any other component required for good operational conditions, as per specifications and UNOPS engineer instructions and approval. 1. Ref. SOF (DUPLEX SOFTNER DUTY/STAND BY each 4.8 m3/hr.) | 1 |  |  |
| 1.5 | Automatic Activated Carbon Cartige Filter Supply and install automatic activated carbon sediment cartige filter, granular activated carbon 20 inch length, 125 psi, 3/4 inch, (16x65")complete with hygienic isolating valves, pressure gauges, as per specifications, and UNOPS engineer instructions and approval. 1. Ref. Automatic activated carbon cartige Filter 2.4 m3/hr. | 2 |  |  |
| 1.6 | Automatic Sand Filter Supply and install automatic sand filter,20 inch length, 125 psi, 3/4 inch, 16x65" multi layers with media complete with hygienic isolating valves, pressure gauges, as per specifications, and UNOPS engineer instructions and approval. 1. Ref. ASF (Automatic Sand Filter 4.8 m3/hr.) | 1 |  | - |
| 1.7 | Reverse Osmosis Unit Supply and install complete RO SET consists of two units, duty and stand by, complete with hygienic isolating valves, pressure gauges, control panel, powder coated steel frame, St. Steel waste and recycle control valve, 5 micron cartige filter TFC spiral wound membrane, PVC membrane housing, St. Steel multistage H.P pump (0.77 l/s @ 100 m head), liquid filled gauge (0-300 psi), product and waste flow meters, low pressure switch, level switch for product water tank, St. Steel needle valve, - Microprocessor controller, 220v, 50 Hz, 20 Amp, TDS & pH sensors with digital LCD monitor and alarm, - UPVC fittings, valves & pipes. As per specifications and UNOPS engineer instructions and approval 1. Ref. RO (each 2.4 m3/hr. product flow, each unit daily product 57 m3/day) | 1 |  |  |
| 1.8 | Purified water storage tank Supply and install HDPE tank, FDA approved construction, oval, no corner nor edges, electrical float valve, inlet and outlet drain and overflow openings, biological filter connected to the vent, transparent FDA approved, base, cover, and all required accessories, as per specifications and UNOPS engineer instructions and Approval. 1. Ref. PWT (2 m3) | 1 |  |  |
| 1.9 | Purified Water Pumps Supply and install purified water pumps (single stage centrifugal) set consists of two pumps, one duty and one standby, each of 3.6 m3/hr. flow rate, and 3 bar head, - 304St.St. pump body, impeller & shaft, complete with control panel, pressure control unit and motor protection, suction & discharge hygienic isolation valves, & check valve, pressure gauges, and steel bases with vibration absorbers, control and electrical wiring, and any other element to put the system in good operational conditions as per specifications and UNOPS engineer instructions and approval. 1. Ref. pwp (SET consists of two pumps) | 1 |  |  |
| 1.10 | Ultraviolet Sterilizer Supply and install ultraviolet sterilizer, 125 psi, 304 st.st, UV lamp and quarts sleeve, audible alarm, pressure gauges, hygienic isolation valves, as per specifications and UNOPS engineer instructions and approval. 1. Ref. UV (3.6 m3/hr.) | 1 |  |  |
| 1.11 | Sediment Cartige Filter 1 Micron Supply and install sediment cartige filter, polypropylene, 1 micron, 20 inch length, 125 psi, 3/4 inch, complete with hygienic isolating valves, and pressure gauges, as per specifications, and UNOPS engineer instructions and approval. 1. Ref. 1 Micron Filter 3.6 m3/hr. | 1 |  |  |
| 1.12 | Sediment Cartige Filter 0.2 Micron Supply and install sediment cartige filter, polypropylene, 0.2 micron, pharmaceutical grade, 20 inch length, 125 psi, 3/4 inch, complete with hygienic isolating valves, and pressure gauges, as per specifications, and UNOPS engineer instructions and approval. 1. Ref. 0.2 Micron Filter 3.6 m3/hr. | 1 |  |  |
| 1.13 | Main Control Panel Main control panel for all hemodialysis equipment complete with contactors, overloads, relays, TDS monitor, alarm for water level. 1. Ref. Main Control Panel | 1 |  |  |
| 1.14 | Dismantle the existing plant Carefully dismantle the existing water treatment plant with all accessories, and handle it to the building operator as per the approved schedule and method statement. | L.S |  |  |
| 1.15 | Connect to the existing piping network Connect the new installed treatment plant to the existing water distribution network, and allow for rearranging the piping inside the hemodialysis hall, by covering exposed pipes with decorative trunks. | L.S |  |  |
| 2. | Portable Water Treatment Plant for Hemodialysis Equipment |  |  |  |
| 2.1 | Main Feed Pumps Supply and install main feed pumps set consists of two pumps, one duty and one standby, each of 0.5 m3/hr. flow rate, and 4 bar head, - 304 St.'s. pump body, impeller & shaft, complete with control panel, pressure control unit and motor protection, suction & discharge hygienic isolation valves, & check valve, pressure gauges, and steel bases with vibration absorbers, control and electrical wiring, and any other element to put the system in good operational conditions as per specifications and UNOPS engineer instructions and approval. Ref. FWP (SET consists of two pumps) | 1 |  |  |
| 2.2 | Sediment Cartige Filter 5 Micron Supply and install sediment cartige filter, polypropylene, #10 slim, 5 micron, 10 inch length, 125 psi, 3/4 inch, complete with hygienic isolating valves, and pressure gauges, as per specifications, and UNOPS engineer instructions and approval. Ref. 5 Micron Filter 0.5 m3/hr. | 1 |  |  |
| 2.3 | Automatic Activated Carbon Cartige Filter Supply and install automatic activated carbon sediment cartige filter, granular activated carbon 10 inch length, 125 psi, 3/4 inch, complete with hygienic isolating valves, pressure gauges, as per specifications, and UNOPS engineer instructions and approval. Ref. Automatic activated carbon cartige Filter 0.5 m3/hr. | 1 |  |  |
| 2.4 | Single Softener Supply and install automatic single softener, consists of one vessel, duty meter initiated, 15000 grains, 0.75 ft3 vessel, (8”dia x 44”), brine tank not less than 50 L, HDPE cover and air check valve. complete with all accessories, fittings, control, pressure gauges, valves, and any other component required for good operational conditions, as per specifications and UNOPS engineer instructions and approval. Ref. SOF (SINGLE SOFTNER 0.5m3/hr.) | 1 |  |  |
| 2.5 | Reverse Osmosis Unit Supply and install complete RO SET consists of one unit, duty, complete with hygienic isolating valves, pressure gauges, control panel, powder coated steel frame, St. Steel waste and recycle control valve, 5 micron cartige filter TFC spiral wound membrane, PVC membrane housing, St. Steel multistage H.P liquid filled gauge (0-300 psi), product and waste flow meters, low pressure switch, level switch for product water tank, St. Steel needle valve, - Microprocessor controller, 220v, 50 Hz, 20 Amp, TDS & pH sensors with digital LCD monitor and alarm, - UPVC fittings, valves & pipes. As per specifications and UNOPS engineer instructions and approval. Ref. RO ( 1 m3/day product flow 50% recovery , 98%salt rejection) | 1 |  |  |
| 2.6 | Purified water storage tank Supply and install HDPE tank, FDA approved construction, oval, no corner nor edges, electrical float valve, inlet and outlet drain and overflow openings, biological filter connected to the vent, transparent FDA approved, base, cover, and all required accessories, as per specifications and UNOPS engineer instructions and Approval. Ref. PWT (200 L) | 1 |  |  |
| 2.7 | Purified Water Pumps Supply and install purified water pumps (single stage centrifugal) set consists of two pumps, one duty and one standby, each of 0.5 m3/hr. flow rate, and 3.5 bar head, - 304St.St. pump body, impeller & shaft, complete with control panel, pressure control unit and motor protection, suction & discharge hygienic isolation valves, & check valve, pressure gauges, and steel bases with vibration absorbers, control and electrical wiring, and any other element to put the system in good operational conditions as per specifications and UNOPS engineer instructions and approval. Ref. pwp (SET consists of two pumps) | 1 |  |  |
| 2.8 | Ultraviolet Sterilizer Supply and install ultraviolet sterilizer, 125 psi, 304 st.st, UV lamp and quarts sleeve, audible alarm, pressure gauges, hygienic isolation valves, as per specifications and UNOPS engineer instructions and approval. Ref. UV (0.5 m3/hr.) | 1 |  |  |
| 2.9 | Sediment Cartige Filter 1 Micron Supply and install sediment cartige filter, polypropylene, 1 micron, 10 inch length, 125 psi, 3/4 inch, complete with hygienic isolating valves, and pressure gauges, as per specifications, and UNOPS engineer instructions and approval. Ref. 1 Micron Filter 0.5 m3/hr. | 1 |  |  |
| 2.10 | Sediment Cartige Filter 0.2 Micron Supply and install sediment cartige filter, polypropylene, 0.2 micron, pharmaceutical grade, 10 inch length, 125 psi, 3/4 inch, complete with hygienic isolating valves, and pressure gauges, as per specifications, and UNOPS engineer instructions and approval. Ref. 0.2 Micron Filter 0.5 m3/hr. | 1 |  |  |
| 2.11 | Main Control Panel Main control panel for all hemodialysis equipment complete with contactors, overloads, relays, TDS monitor, alarm for water level. Ref. Main Control Panel | 1 |  |  |
| 2.12 | Portable Skid Unit skid made of epoxy coated steel, with dimensions not more than 1.5-m length x 0.9-m width x 1.5-m height. | 1 |  |  |

Payment terms 30 days accepted: ☐ Yes

Bidder’s discount for accelerated payment: ____% of total firm price for each calendar day less than thirty (30) days

List of subcontractors or suppliers

Bidder must identify the names of all subcontractors/suppliers who will be providing good/services under this Contract and the type of work being subcontracted, if applicable.

- _[Full legal name and address of subcontractors]___________

- _________________________________________________

- _________________________________________________

I, the undersigned, certify that I am duly authorized by [insert full name of Bidder] to sign this quotation and bind [insert full name of Bidder] should UNOPS accept this quotation:

Name	: _____________________________________________________________

Title	: _____________________________________________________________

Date	: _____________________________________________________________

Signature	: _____________________________________________________________

Form C: Technical Quotation Form

RFQ reference no: [insert RFQ reference No.]

Name of Bidder: [insert name of Bidder]

Bidders are required to complete the Comparative Data Tables included in Section II: Schedule of Requirements to demonstrate compliance with UNOPS requirements and inserted below. Bidders are NOT allowed to make any change in the “UNOPS requirements” columns of the Comparative Data Tables. Such changes might disqualify your quotation.

Technical specifications for goods – Comparative Data Table

| Item No | UNOPS minimum technical requirements | Qty. | Is bid compliant? Bidder to complete | Details of goods offered. Bidder to complete | Brochure Page No. |
| --- | --- | --- | --- | --- | --- |
| 1 | Water Treatment Plant for Hemodialysis Equipment | 1 |  |  |  |
| 2 | Portable Water Treatment Plant for Hemodialysis Equipment | 1 |  |  |  |
|  | Name of Manufacturer |  |  | Insert details | Insert |
|  | Model/ catalogue number |  |  | Insert details | Insert |
|  | Country of Origin for the offered model |  |  | Insert details | Insert |
|  | Country where the manufacturer is based |  |  | Insert details | Insert |
|  | Delivery time |  |  | Insert details | Insert |
|  | Full warranty period |  |  | Insert details | Insert |
|  | FDA clearance OR CE Mark |  |  | Insert details | Insert |
| Technical specifications for items 1 and 2: |  |  |  |  |  |
| 1 | Sand Filter Design: Suspended solids & turbidity. Filter Media: a. Graged silica sand & supported gravel. b. High quality, resisting attrition and possessing durability and long life. Tank: a. Working Pressure: 6.9 bar (100 psi). b. Hydrostatically test at 150% of working pressure. c. Opening on top to replace filter media. a. Provide single tank. Controls: b. Piston type, motor driven control valve. c. Self-adjusting flow control to control the backwash and rinse rates. d. Time clock initiates backwash on a calendar clock basis. |  | ☐ Yes ☐ No | Insert details of goods offered, including specifications and brand/model offered if applicable | Insert |
| 2 | Carbon Filter Design: - Dechlorinates and absorbs dissolved organics. Filter Media: c. Activated carbon mesh & supported gravel. d. High quality, resisting attrition and possessing durability and long life. e. Shall not impart taste, odor, or color to the water. Tank: d. Working Pressure: 6.9 bar (100 psi). e. Hydrostatically test at 150% of working pressure. f. Opening on top to replace filter media. g. Provide single tank. Controls: a. Piston type, motor driven control valve. b. Self-adjusting flow control to control the backwash and rinse rates. c. Time clock initiates backwash on a calendar clock basis. |  | ☐ Yes ☐ No | Insert details of goods offered, including specifications and brand/model offered if applicable | Insert |
| 3 | Reverse Osmosis Unit Design Requirements: Provides water that is free of dissolved solids, bacteria, virus and pyrogenic contaminants. Design Parameters: a. The RO system shall produce minimum water flow as indicated in the drawings when operating at 60% recovery. b. The system shall use Thin-Film-Composite (TFC) membranes with salt rejection of 96-98% and > 99% rejection of organics > 150 molecular weight (mw). c. Membrane elements shall be provided with internal interconnectors and double O-Ring seals. Pump: a. Construction: Multi-stage centrifugal pump with stainless steel type 316 and Noryl impellers. d. Motor: 3 Hp, 208-230/ 460VAC, 3 phase. Member Housing: Side entry, stainless steel with internal load transfer device to prevent telescoping of membrane elements. Housing shall be mounted horizontally for ease of servicing. Accessories: a. Sampling valves and flow meters that permit monitoring of product water and reject water without line disconnection. b. Adjustable waste flow control with minimum flow preset at factory. c. Sanitation ports with valves on feed, permeate and concentrate lines. d. Automatic waste water flushing system based on timed cycles (field adjustable). e. Adjustable waste flow control. 5 micron pre-filter to be built on to the RO frame. Instrumentation: a. On/ off switch. b. Low feed water pressure alarm post 5 micron filter, with time delay. c. Built-in water quality monitor on permeate. d. Pressure gages for pre-filter, post-filter, pump discharge, and final pressure. e. Motor overload alarm with immediate shutdown. f. High temperature shutdown. g. Temperature monitor (panel mounted). |  | ☐ Yes ☐ No | Insert details of goods offered, including specifications and brand/model offered if applicable | Insert |
| 4 | Storage Tank and Accessories Storage Tank: a. Level control with low-level alarm. b. Dished bottom, flat top with sealed cover.PE. Tank shall be FDA approved. c. Capacity: 2000 liters (500 gallons) minimum. |  | ☐ Yes ☐ No | Insert details of goods offered, including specifications and brand/model offered if applicable | Insert |
| 5 | Ultraviolet Light Construction: a. Housing: Type 304 stainless steel with No.4 finish. b. Chamber: Type 316 stainless steel, passivated and electro polished. c. Provide with flanges on inlet and outlet. Design: a. Operating pressures: 830 kPa (120 psi) operating, 1240 kPa (180 psi) test pressure. b. Water temperature range: 2 to 38°C (35-100°F). c. Ambient temperature range: 7 to 55°C (45-130°F). d. Designed for continuous operation with 99% bacterial reduction. Controls: a. Interlocked with loop distribution pumps turn OFF whenever the pump goes OFF. b. LED UV lamp display providing continuous visual indication of lamp status. c. Running time meter (non-resettable) for recording operating hours. e. Tie UV sensor to pump for shutoff. |  | ☐ Yes ☐ No | Insert details of goods offered, including specifications and brand/model offered if applicable | Insert |
| 6 | Cation Bed resin / water softener Provide duplex sets, two in parallel. Operating Data: a. Capacity: 125,000 grains. b. Flow rate: as indicated in the drawings. c. Pressure Drop: 1. Minimum: 70kPa (10psi). 2. Nominal: 140kPa (20psi). Primary Separate Bed Cation/softening Unit Bed Cation/softener Unit: Provide cation unit consisting of a strongly acidic cation resin for the removal of hardness. Resin Trap Cartridge Filter Housing and Filters Resin Trap Cartridge Filter Housing: Similar in construction to pre-filter housing. Provide cartridge filter housing with liquid filled stainless steel pressure gages on inlet and outlet. Resin Trap Filter Cartridges: 5 micron absolute pre-rinsed, high quality, nonfiber releasing, with polypropylene core, designed for use with RO water. Provide O-ring connectors for fitting into the housing. Fiberglass-Reinforced Polyester Tank. Design: a. Base wall and head thickness calculations using a 10 to 1 safety factor. Provide vertical tanks with convex dished top heads and continuously supported flat bottoms. b. Tank Tie-Down Lugs: Provide four or more hold-down lugs for vertical tanks. |  | ☐ Yes ☐ No | Insert details of goods offered, including specifications and brand/model offered if applicable | Insert |
| 7 | Pumps Construction: a. Stainless steel, type 316; suction and discharge chambers, shaft and shaft seals. b. Ceramic; bearings. c. EPDM; O-rings. d. Noryl impellers. Design: a. Design working pressure: 16 bar (230 psi) (maximum) b. Pump: Horizontal with multi-stage impeller design. Centrifugal Pumps: Designed to meet the requirements of ANSI B-73.1 with passivated 316 stainless steel wetted parts, Viton, elastomers, and bellows- type mechanical seals. Provide 316 stainless steel, ceramic, or glass filled Teflon wetted seal components. |  | ☐ Yes ☐ No | Insert details of goods offered, including specifications and brand/model offered if applicable | Insert |
| 8 | Filters: Housings: a. Constructed from stainless steel type 304 or polypropylene. b. Designed for minimum 100 psi operating pressure. c. Holds multiple cartridges. d. Provide bypass valves around each housing to allow for servicing without shutdown. Biological Cartridges: a. Designed to filter micron particles. e. Designed to filter 0.2-micron particles with maximum of 34kPa (5-psi) pressure drop. Polycarbonate media. 0.2 micron. Sediment Cartridges: Construct of polypropylene. Provide primary pre-filters with string wound on a polypropylene center core and 5 micron absolute polypropylene membrane secondary prefilters. Carbon cartridges: Consist of specially processed, granular, highly activated carbon to provide removal of a broad spectrum of low molecular weight organics, specific non-polar high molecular weight organics, free chlorine, and partially dissolved gases. a. Provide 12 by 40 granular carbon mesh with a total surface area of 1000m²/ g. Iodine number shall be 1000 minimum, molasses number shall be 230 minimum, and abrasion number shall be 75 minimum. b. Precondition activated carbon by hydration and backwashing to remove fines. Do not use dry, unconditioned activated carbon in tank. |  | ☐ Yes ☐ No | Insert details of goods offered, including specifications and brand/model offered if applicable | Insert |
| 9 | System Instrumentation Instrumentation and monitoring shall include but not be limited to the following: a. Feed water flow meter. b. Pressure gage on inlet and outlet of pre-filters, resin traps, and final filters. c. Flow monitor on outlet. d. Pressure gage on distribution/ recirculation pumps discharge. e. Pressure gages before and after the back pressure control valve. Provide ESP dedicated bacteria sample ports at the following locations: a. Outlet of water softener. b. Inlet to RO unit. c. Outlet 0.2 micron final filters. d. Return loop outlet. |  | ☐ Yes ☐ No | Insert details of goods offered, including specifications and brand/model offered if applicable | Insert |

General Requirements and Preambles:

1. The above BOQ is for the supply and install of a complete water treatment plant for hemodialysis department, including all the required components for proper operation and sufficient water feeding for 40 beds in operation at the same time.

2. Price shall include in addition to the above items, all required piping, power and control wiring and cables, sensors, measuring devises, instrumentations, and all required parts to put the plant into proper operational conditions.

3. Price shall include, engineering efforts for redesign the plant in order to match the required capacity as indicated in the drawings and commercial equipment selections in accordance with the technical specifications and subject to UNOPS engineer's review and approval.

5. All equipment’s and components shall be supported with certificates of origin."

6.  Read this Section in conjunction with other related tender documents, the Design Drawings and the Contract Conditions.

7. Complete the Detailed Design, manufacture, supply, install and warrant the work, complying with the visual intent indicated and specified design and performance requirements.

8. Where a particular material, product or supplier is specified, the material, product or supplier shall be deemed indicative representing the Engineer's Design Intent only. Complete the installation using the specified, or other product acceptable to the Engineer and confirmed in writing. Be fully responsible for the Detailed Design, and performance of the work.

9. Submit the following post contract documents:

9.1 Shop Drawings indicating equipment dimensions and plumbing diagrams along with design calculations to meet the required capacity and equipment selections.

9.2 Exchangeable tank, pipe, fitting, filter housings, and media specifications.

9.3 Supplementary Product Literature: Include a statement from the manufacturer for the design life of the system.

9.4 List of tests included.

9.5 Certified test data.

9.6 Outline technical specifications reflecting proposed materials and systems.

a.	Engineering data, installation instructions, and maintenance and operating instructions.

b.	Detailed disinfection and cleaning process.

9.7 A list of proposed suppliers and Subcontractors intended to be used.

9.8 Detailed Method Statement.

9.10 Summary of deviations from the Specification.

9.11 Warranties: two-year maintenance warrantee including consumable materials such as salts, chemicals, disinfectants, Etc.

10. Materials and accessories:

10.1 Back Pressure Regulating Valve

Designed to maintain specifically constant outlet pressure, as inlet flow and pressure varies. Pressure relief valve is not acceptable.

Pressure shall be adjustable from 70 to 170kPa (10-25psi), flow or as scheduled on the Design Drawings.

Construction

a.	Type 316L stainless steel and/ or plastic body and all wetted parts.

b.	Designed for 10 bar (150 psi) maximum working pressure.

10.2 Flow Meter

Construction: Inert plastic (polypropylene or PVDF).

11. Execution:

1	EXAMINATION

A	Verification of Conditions: Examine areas for compliance with requirements for installation and conditions affecting performance of the Work. Identify conditions detrimental to a proper and timely completion and notify the Engineer of the unsatisfactory conditions. Proceed with installation only after unsatisfactory conditions have been corrected.

2	INSTALLATION

A	Provide requisite trade labor necessary to install a complete operating system.

B	Install work in accordance with specific component manufacturer's instructions.

C	Maintain on Site supervision during the installation.

3	START-UP SERVICE

A	Provide the services of qualified personnel to supervise the installation and start-up of the entire system. When start-up is complete and the system is operational, notify the Employer when the acceptance test shall be started.

B	Provide chemicals, filters, and expendable materials necessary to perform start-up service.

4	TESTING AND CERTIFICATION

A	The system shall provide water quality as required by beneficiary.

B	Acceptance water quality test results shall be certified to Employer.

C	Any additional disinfection or testing necessary to meet acceptance shall be at the expense of the Contractor.

D	Provide equipment manufacturer's written certification that installation is in accordance with their recommendations.

5	INSTRUCTION OF EMPLOYER PERSONNEL

A	Provide a qualified technician on Site for not less than 2 working days to instruct Employer's personnel in the proper operation, care, and maintenance of the system. Ensure that Employer's personnel are fully qualified in all areas of operation, care, and maintenance.

B	Include a review of all O+M Manuals and Shop Drawings, explanation of the operation of each system and each piece of equipment, and a review of emergency and trouble-shooting techniques.

C	During operational instruction period, adjust equipment controls to simulate various problems and demonstrate their solutions.

D	Provide a qualified technician to return to the site for 1 working day approximately 6 months after Employer's beneficial occupancy. During that day, examine equipment operation, review O+M schedules, calibrate instruments, review operating data sheets, reinstruct Employer's personnel, and submit a written report on system performance and comments for review by Employer.

6	DISINFECTION

A	Conduct disinfection process after the equipment is operational and the building-piping loop has been pressure and leak tested.

1	Include the cost of disinfecting the equipment and building-piping loop to certify that the system performs in accordance with required parameters.

2	Contractor shall submit with the bid, a unit price valid for 1 year from the date of beneficial occupancy to perform additional disinfection processes at Employer's request.

B	Consult with the Engineer to schedule disinfection date.

C	Use semiconductor grade 30% unsterilized hydrogen peroxide diluted to 5% with semiconductor grade RO water as the disinfection agent. Sodium hypochlorite is not acceptable.

D	Place hydrogen peroxide disinfection solution in storage tanks, pump through 0.2 micron membrane filters into the piping system. Open valves and sample ports to purge distribution lines of gas. Take RO equipment off line during disinfection process.

E	Prior to starting operations assure protective equipment and safety shower eye wash is available for personnel protection.

F	Tag all distribution valves with the following: "DANGER - Persons Working On Equipment –Do Not Touch".

G	Recirculate hydrogen peroxide solution for 24 hours.

H	Open & close outlets & sample ports every 6 hours for 2 min.

I	At the end of the 24-hour recirculation period, open valves and sample ports and drain using nitrogen filtered to 0.05 micron to purge system.

J	Flush system with RO water filtered to 0.2 micron absolute.

K	Continue flushing until 18 megohm is achieved at each point of use.

L	At the completion of the disinfection process, the RO water remains on line.

M	Submit test report for the Engineer's review and acceptance. Arrange training of Employer's representatives in operation and maintenance of the system.

Delivery requirements –– Comparative Data Table

| UNOPS Requirements |  | Is quotation compliant? Bidder to complete | Details Bidder to complete |
| --- | --- | --- | --- |
| Delivery time | Bidder shall deliver the goods [4 weeks] after Contract signature. | ☐ Yes ☐ No | Insert details |
| Delivery place and Incoterms rules | DAP to Royal Medical Services (Medical City in Amman) Incoterms rules as per Incoterms 2010. | ☐ Yes ☐ No | Insert details |
| Consignee details | Royal Jordanian Army with notifying UNOPS | ☐ Yes ☐ No | Insert details |
| UNOPS Right to vary requirements | At the time the Contract is awarded, UNOPS reserves the right to vary the quantity of the goods and associated services specified above, provided this does not exceed +/- [20%] , without any change in the unit prices or other terms and conditions of the RFQ. | ☐ Yes ☐ No | Insert details |

00ax: +45 45 33 75 01

The offered goods and related services (if applicable) are in accordance with the required specifications and requirements specified in Section II: Schedule of Requirements.

☐ Yes   ☐ No

ANY DEVIATION MUST BE LISTED BELOW:

_________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________

Name	: _____________________________________________________________

Title	: _____________________________________________________________

Date	: _____________________________________________________________

Signature	: _____________________________________________________________

# Form D: Previous Experience Form – With all clients and not only UN or UNOPS

RFQ reference no: [insert RFQ reference No.]

Name of Bidder: [insert name of Bidder]

| Description of services/goods | Country | Total amount of Contract | Contract Identification and Title and Contact details of Client (Name, Address, telephone, email, fax) | Year project was undertaken |
| --- | --- | --- | --- | --- |

Name	: _____________________________________________________________

Title	: _____________________________________________________________

Date	: _____________________________________________________________

Signature	: _____________________________________________________________