## -Grand Total option B
| TITLE: LOT 1 SOLAR SCHEMES IN NCHELENGE AND BORDER POSTS | Bill AMOUNT
ITEM No. | D E S C R I P T I O N | AMOUNT
(ZMW)
BILL COLLECTION SHEET OPTION A - SOLAR AND MAINS POWER SCHEMES
SUB-BILL
Bill No.P&G: | PRELIMINARY & GENERAL ITEMS | 220000
Bill No. SCH1: | Mantapala Ntoto Primary School | 0
Bill No. SCH2: | Kafutuma Primary | 0
Bill No. SCH3: | Kampampi Primary School | 0
Bill No. SCH4: | Kashikishi Primary School | 0
Bill No. SCH5: | Nchelenge Secondary School | 0
Bill No. SCH6: | Kashita Secondary School | 0
Bill No. SCH7: | Kenani Primary School | 0
Bill No. HC1: | Kambwali RHC | 0
Bill No. HC2: | Kafutuma RHC | 0
Bill No. HC3: | Chabilikila RHC | 0
Bill No. HC4: | Mulwe RHC | 0
Bill No. HC6: | Kapambwe RHC | 0
Bill No. MKT1: | Kashikishi Market | 0
Bill No. TC1: | Kaputa Reception Centre | 0
Bill No. TC2 | Lambwe Chomba Reception Centre | 0
Bill No. TC3: | Lupiya Reception Centre | 0
Bill No. TC4: | Mpulungu Reception Centre | 0
| BILL OF QUANTITIES TOTAL | 220000
| 10% Contigencies | 22000
| TOTAL WORKS | 242000

## -Grand Total option A
| TITLE: LOT 1 SOLAR SCHEMES IN NCHELENGE AND BORDER POSTS | Bill AMOUNT
ITEM No. | D E S C R I P T I O N | AMOUNT
(ZMW)
BILL COLLECTION SHEET OPTION A - SOLAR SCHEMES ONLY
SUB-BILL
Bill No.P&G: | PRELIMINARY & GENERAL ITEMS | 220000
Bill No. SCH1: | Mantapala Ntoto Primary School | 0
Bill No. SCH2: | Kafutuma Primary | 0
Bill No. SCH3: | Kampampi Primary School | 0
Bill No. SCH4: | Kashikishi Primary School | 0
Bill No. SCH5: | Nchelenge Secondary School | 0
Bill No. SCH6: | Kashita Secondary School | 0
Bill No. SCH8: | Kenani Primary School | 0
Bill No. HC1: | Kambwali RHC | 0
Bill No. HC2: | Kafutuma RHC | 0
Bill No. HC3: | Chabilikila RHC | 0
Bill No. HC4: | Mulwe RHC | 0
Bill No. HC5: | St Pauls Hospital Staff Houses | 0
Bill No. HC6: | Kapambwe RHC | 0
Bill No. MKT1: | Kashikishi Market | 0
Bill No. TC1: | Kaputa Reception Centre | 0
Bill No. TC2 | Lambwe Chomba Reception Centre | 0
Bill No. TC3: | Lupiya Reception Centre | 0
Bill No. TC4: | Mpulungu Reception Centre | 0
| BILL OF QUANTITIES TOTAL | 220000
| 10% Contigencies | 22000
| Taxes (VAT @ 16%) | 35200
| TOTAL WORKS | 277200

## P&Gs
UNICEF
Solar Powered Borehole Schemes in institutions in Nchelenge (Mantapala) Refugee Camp & Host Communities
Bill No.P&G:
Item | Description | Unit | Qty | Rate (ZMW) | Amount (ZMW)
Bill No. 1: Preliminary and general |  |  |  |  | 220000
1.1 | Allow for all sureties and insurance cover; site establishment (Including time-related costs); offices; workshops; storage sheds; living accommodation; compliance with labour regulations; ablution facilities; water supplies, power and communication; site notice boards etc. | LS | 1 |  | 0
1.2 | Provisional sum for material testing | PS | 1 | 20000 | 20000
1.3 | Compliance with Environmental and Social Safeguards (EP) | LS | 1 |  | 0
1.4 | Compliance with Health and Safety Safeguards (HS) | LS | 1 |  | 0
1.5 | Repair of existing water supplies (solar related systems) | PS | 1 | 200000 | 200000
1.6 | Supply and install 2 x Solar Powered Light Poles with batteries (as per standard drawing) | no. | 17 |  | 0
| Sub-total |  |  |  | 220000
Contingencies (10%)
Taxes (VAT @16%)
| Total |  |  |  | 220000

## Ntoto Primary
UNICEF
Solar Powered Borehole Schemes in institutions in Nchelenge (Mantapala) Refugee Camp & Host Communities
Mantapala Ntoto Primary School
Bill No. SCH1:
Item | Description | Unit | Qty | Rate (ZMW) | Amount (ZMW)
Bill No. 1: Setting out, Demolition and Site Clearance |  |  |  |  | 0
1.1 | In collaboration with the Inspector of Works, and based upon pipe lengths and alignment shown on layout plan, agree upon final alignment of pipelines, road crossings, location of all tees, bends, isolating valves, air valves, washouts, tapstands, and consumer connection offtakes. Set out pipeline centre-lines, survey, agree upon Starting Surfaces, and final lengths and produce final plans at horizontal scale of 1:200 for approval before proceeding further. | LS | 1 |  | 0
1.2 | General Clearance for urban land & rough grass land along pipeline wayleaves (trench width plus 0.5 m on either side) | ha | 0.2 |  | 0
1.3 | Removal of tree stumps within approved alignment. PROVISIONAL SUM | nr | 1 |  | 0
1.4 | Cut down and remove trees and tree stumps within approved alignment only if specifically directed to do so by Inspector of Works following agreement from the Host Community PROVISIONAL SUM | nr | 1 |  | 0
Bill No. 2: Excavation and backfilling of trenches - all pipelines |  |  |  |  | 0
2.1 | Excavate test pits along centre line of proposed pipeline to depth of 1m at least every 50 m | nr | 12 |  | 0
2.2 | Excavate and trim trench bed to depth not exceeding 1 m to ensure minimum cover provided to pipeline is not less than 600 mm | m | 511.2 |  | 0
2.3 | E. O. item 2.2 at road crossings. Excavate and trim trench to additional depth not exceeding 1.5 m to ensure minimum cover provided to the pipeline is 900 mm | m | 56.8 |  | 0
2.4 | Over excavate trench by a further depth of 150mm in areas identified by the Inspector of Works as requiring imported granular backfill RATE ONLY | m3 | 5.112 |  | 0
2.5 | Import, place and compact granular backfill in areas identified by the Inspector of Works as requiring imported granular backfill. RATE ONLY, | m3 | 5.112 |  | 0
2.6 | Place and compact sidefill and backfill using selected excavated material free of stones and tree roots to depth 300 mm above crown of pipe, and after compaction, other excavated material thereafter to final surface | m | 511.2 |  | 0
2.7 | Dispose of all surplus excavated material off-site as directed | LS | 1 |  | 0
Bill No. 3: Supply and Installation of rising main- borehole to elevated water tank |  |  |  |  | 0
All PE compression joints and fittings shall be supplied complete with suitable pipe joint stiffeners. All steel fittings shall be epoxy coated and all nuts and bolts galvanised. Rate shall include supply, lay, bed, joint , pressure test, sterilize and flushing of HDPE pipelines
3.1 | Raw water rising main from borehole to the Elevated Tank , HDPE DN50 (OD 63), SDR11, PN 16 | m | 236 |  | 0
3.2 | Compression fitting, elbow 90o DN 50mm | nr | 1
3.3 | Gate Valve, double flange, handwheel operated 50 mm non-rising spindle type, with 1 No. flanged restraining adapters st. fl. to PE DN 50, installed above ground within tank inlet riser pipe | set | 1 |  | 0
3.4 | Supply and Installation of DN 40 parallel bulk water meter with magnetic transmission and dry recording head , metrological class B, minimum display 1 m3/hr to specification, suitable for vertical mounting, within water tank inlet riser pipe complete with strainer (metallic double flanged body c/w lockable meter box pipe surround). The meter assembly shall comprise: 1 No. DN50 to DN40 reducer, 1 DN40 500mm long straight pipe length, 1 DN 40 mm double flanged vertically mounted parallel bulk type meter, located approximately 1.5 m above ground level, 1 DN 40 250 mm straight pipe length, and one DN40 to DN50 reducer. | set | 1 |  | 0
| Carry forward |  |  |  | 0
| Brought forward |  |  |  | 0
Bill No. 4: Tanks, Tankstands and Tap Stands |  |  |  |  | 0
Bidder shall supply outline details of water tank stand and tank c/w, pipework and fittings.
Water tank stand manufacturer:
HDPE cylindrical tank manufacturer:
HDPE cylindrical tank supplier (if different):
Contractor shall supply full set of structural calculations and drawings for water tank stand certified by a registered structural engineer for written approval prior to fabrication.
4.1 | Conduct geotechnical investigations and design foundation and tank stand for the elevated tank | LS | 1 |  | 0
4.2 | Tank reinforced concrete foundations 1 m x 1m x 1.5 m deep inc. excavation, shuttering, concreting, curing, backfilling and disposal of excess spoil material from site | nr | 6 |  | 0
Supply and install 2 No. HDPE cylindrical tank on Contractor designed six vertical members) mild steel tankstand c/w with inlet float valves, all inflow, valved connecting, outflow, overflow, and scour (washout) pipework, fittings, adaptors and 6m high steel stand c/w access ladder and lightning arrestor.
4.3 | Capacity 10m3.(two no. of 5m3) | nr | 1 |  | 0
4.4 | Supply and paint all mild steel in tank stand with two coats of zinc 82% rich paint in dry film | LS | 1 |  | 0
4.5 | Leak testing and disinfection of tank and pipework | nr | 1 |  | 0
4.6 | Provide and install float level indicator gauge on side of tank readable from ground level adjacent to tank | nr | 1 |  | 0
4.7 | Provide and install chlorine cartridge type inline doser in lockable chamber at start of tank outlet pipe c/w twelve months supply of chlorine cartridges. | LS | 1 |  | 0
4.8 | Provide materials for and construct tap stand and associated drainage | nr | 4 |  | 0
Bill No. 5: Supply and Install Water Distribution Network |  |  |  |  | 0
All PE compression joints and fittings shall be supplied complete with suitable pipe joint stiffeners. All steel fittings shall be epoxy coated and all nuts and bolts galvanised. Rate shall include supply, lay, bed, joint , pressure test, sterilize and flushing of HDPE pipelines
5.1 | Network reticulation pipework HDPE DN50 (OD 63), SDR17, PN 10 | m | 109 |  | 0
5.2 | Unequal reducing tee compression fitting DN 50 x 50 x 32 mm | nr | 3 |  | 0
5.3 | Compression reducer coupling 50mm x 40mm | nr | 3 |  | 0
5.4 | Network reticulation pipework HDPE DN 40mm, SDR17, PN 10 | m | 118 |  | 0
5.5 | Network reticulation pipework HDPE DN 32mm, SDR17, PN 10 | m | 105 |  | 0
5.6 | Compression fitting, elbow 45o DN 40mm | nr | 3 |  | 0
5.7 | End cap DN 32mm (compression type) | nr | 4 |  | 0
5.8 | Supply and install GI pipes 25mm dia c/w fittings to tap stands c/w isolating stop cock | nr | 4 |  | 0
5.9 | Supply and install heavy weight brass garden bib tap (non-lever arm type) | nr | 8 |  | 0
5.1 | Compression tee DN 32 x 32 x 1" male branch to connect to tap stand pipework | nr | 4 |  | 0
5.11 | Gate Valve, double flange, 40 mm non-rising spindle type, with 2 No. flanged restraining adapters st. fl. to PE DN 40, complete with valve riser and valve box to suit | nr | 1 |  | 0
Air valve assembly consisting of 1 No. compression tee with threaded male 1 1/2" branch vertically upwards, 1 No. female to male thr. spigot, 1 No. Stopcock, thr. dble. socket 1", and 1 No. Single air valve, thr. female 1". RATE ONLY
5.12.1 | Compression tee DN 50 x 50 x 1 1/2" male br., 1 No. female to male 1 1/2" to 1" thr. spigot | set | 1
5.12.2 | Compression tee DN 40 x 40 x 1 1/2" male br., 1 No. female to male 1 1/2" to 1" thr. Spigot | set | 1
5.12.3 | Compression tee DN 32 x 32 x 1" male br, 1 No. female to male 1" to 1" thr. spigot | set | 1
| Carry forward |  |  |  | 0
| Brought forward |  |  |  | 0
Bill No. 6: Concrete Works to all Pipelines |  |  |  |  | 0
All unreinforced concrete works shall be in medium strength concrete unless otherwise indicated.Where bends less than 45o are obtained by bending the pipe, radius not less than 35 x pipe diameter, and provided there is no compression joint with 5 metres of either end of radius, no separate thrust block is required.
6.1 | Over excavate in trench bed at all gate valves, air valve assemblies and steel fittings and cast support slab to full width of trench with other dimensions being the length of the valve or the fitting between flanges or between the compression tightening nuts and depth below trench bed of 150 mm | nr | 1 |  | 0
6.2 | At all 45o and 90o bends, pipeline tees, and end caps provide and subsequently remove shuttering and cast thrust blocks against undisturbed trench bed and trench wall | nr | 7 |  | 0
6.3 | Supply all materials and cast and complete air-valve chamber. RATE ONLY | nr | 1
| Sub-total Bill Nos 1 to 6 |  |  |  | 0
| Contingencies (10%) Bills No 1 to 6 |  |  |  | 0
| Taxes (VAT @16%) Bills Nos 1 to 6 |  |  |  | 0
| Total Bills Nos 1 to 6 |  |  |  | 0
Bill 7A | Electromechanical - OPTION A Solar Powered |  |  |  | 0
Bidder shall supply all the information and rates for both Alternatives for the offer to be considered. Final decision on the main power source (Option A ZESCO mains power from institutions incoming distribution board, or Option B from Solar Array will be confirmed during negotiation prior to award.
proposed submersible hybrid DC/AC pumpset manufacturer and agent:
proposed standby generator manufacturer and agent:
| confirm manufactures brochures included with bid |  | yes / no
No change from these manufacturers or agents shall be permitted without prior written approval from the Consultant
Submersible 48 VDC Borehole Pump
7.1 | Supply and install a hybrid DC/AC borehole submersible pump suitable for a borehole of ID 5" capable of being powered from either a 48 VDC or a nominal 230 VAC source c/w shroud and cabled connection to power sources located within 10 m of borehole head, pumping into an overhead tank with top water inlet 14 m above ground.. . |  | nr | 1
Information provided to guide Bidder
| Ground elevation at borehole (approximate) | masl | 955
| Yield | m3/hr | 1
| Pump installation level below ground surface | m | tbc
| Riser pipe diameter | mm | DN 50
| Dynamic water level below ground surface | m | tbc
| Top water level in overhead tank | masl | 974
Information to be provided by Bidder
| Manufacturers Pump reference No. | ref.
| Maximum flow at Installation indicated above | m3/hr
| Maximum pump head at installation indicated above | m3/hr
| Optimum flow at Installation indicated above | m3/hr
| Optimum head at Installation indicated above | m3/hr
| Pump efficiency at installation | %
| Input power required by pump | W
| Output power required by solar array | W
| No. of solar panels and arrays offered and guaranteed to meet requirement | nr
7.2 | Solar arrays to meet requirements c/w security fence and gate and lightning protection as per Drawing to be included in this Option
7.2.1 | Supply, install, erect and connect solar arrays to meet requirements c/w lightning protection as per Drawing and Specification | nr | 1 |  | 0
7.2.2 | Provide all materials and construct fenced and gated compound to contain solar array and associated chambers to Specification | LS | 1 |  | 0
7.2.3 | Supply and install DN 25 water pipe take-off from rising mainand standpipe for solar cleansing system | LS | 1 |  | 0
7.2.4 | Provide solar array cleansing step ladder and extendable washer to Specification | LS | 1 |  | 0
Supply and Installation of 220 VAC standby generator of rated power
7.3 | Supply, Install and connect by manually operated changeover switch standby generator capable of providing the VAC power required to operate the submersible borehole pump as specified above at half-load c/w roofed lockable waterproof steel protection cabinet. | nr | 1 |  | 0
Information to be provided by Bidder
Manufacturers Generator Set reference No.
| Output kVA at 1500rpm, 220V, single-phase, 50Hz, with power factor of 1.0 | kVA
| Fuel type (petrol/diesel) | type
| Fuel tank capacity | l
Air or water cooled
7.4 | External 230 VAC Power Source to be included in Option B
0
| Sub-total Bill No 7A |  |  |  | 0
| Contingencies (10%) Bill No 7A |  |  |  | 0
| Taxes (VAT @16%) Bill No 7A |  |  |  | 0
| Total Bill No 7A |  |  |  | 0
Bill 7B | Electromechanical - OPTION B Mains electric powered |  |  |  | 0
Bidder shall supply all the information and rates for both Alternatives for the offer to be considered. Final decision on the main power source (Option A ZESCO mains power from institutions incoming distribution board, or Option B from Solar Array will be confirmed during negotiation prior to award.
proposed submersible hybrid DC/AC pumpset manufacturer and agent:
proposed standby generator manufacturer and agent:
| confirm manufactures brochures included with bid |  | yes / no
No change from these manufacturers or agents shall be permitted without prior written approval from the Consultant
Submersible 48 VDC Borehole Pump
7.1 | Supply and install a hybrid DC/AC borehole submersible pump suitable for a borehole of ID 5" capable of being powered from either a 48 VDC or a nominal 230 VAC source c/w shroud and cabled connection to power sources located within 10 m of borehole head, pumping into an overhead tank with top water inlet 14 m above ground.. . |  | nr | 1
Information provided to guide Bidder
| Ground elevation at borehole (approximate) | masl | 955
| Yield | m3/hr | 1
| Pump installation level below ground surface | m | tbc
| Riser pipe diameter | mm | DN 50
| Dynamic water level below ground surface | m | tbc
| Top water level in overhead tank | masl | 974
Information to be provided by Bidder
| Manufacturers Pump reference No. | ref.
| Maximum flow at Installation indicated above | m3/hr
| Maximum pump head at installation indicated above | m3/hr
| Optimum flow at Installation indicated above | m3/hr
| Optimum head at Installation indicated above | m3/hr
| Pump efficiency at installation | %
| Input power required by pump | W
| Output power required by mains electrical supply | W
7.2 | Solar arrays to be included in Option A
Supply and Installation of 220 VAC standby generator of rated power
7.3 | Supply, Install and connect by manually operated changeover switch standby generator capable of providing the VAC power required to operate the submersible borehole pump as specified above at half-load c/w roofed lockable waterproof steel protection cabinet. | nr | 1 |  | 0
Information to be provided by Bidder
Manufacturers Generator Set reference No.
| Output kVA at 1500rpm, 220V, single-phase, 50Hz, with power factor of 1.0 | kVA
| Fuel type (petrol/diesel) | type
| Fuel tank capacity | l
Air or water cooled
External 230 VAC Power Source
7.4 | Underground armoured cable c/w all internal building works, and making good, outside excavation, backfilling and protective concrete cover slabs from Main Distribution Board |  | 0
7.4.1 | All ancilliary work excludng outside excavation, and backfilling, supply and installation of underground armoured cable and protective concrete cover slabs | nr | 1 |  | 0
7.4.2 | External excavation, and backfilling, supply and installation of underground armoured cable and protective concrete cover slabs, minimum cover to cable 600 mm. Length subject to reconfirmation prior to award. | m | 162 |  | 0
| Sub-total Bill No 7B |  |  |  | 0
| Contingencies (10%) Bill No 7B |  |  |  | 0
| Taxes (VAT @16%) Bill No 7B |  |  |  | 0
| Total Bill No 7B |  |  |  | 0

## Kafutuma Primary
UNICEF
Solar Powered Borehole Schemes in institutions in Nchelenge (Mantapala) Refugee Camp & Host Communities
Kafutuma Primary
Bill No. SCH2:
Item | Description | Unit | Qty | Rate (ZMW) | Amount (ZMW)
Bill No. out, Demolition and Site Clearance |  |  |  |  | 0
1.1 | In collaboration with the Inspector of Works, and based upon pipe lengths and alignment shown on layout plan, agree upon final alignment of pipelines, road crossings, location of all tees, bends, isolating valves, air valves, washouts, tapstands, and consumer connection offtakes. Set out pipeline centre-lines, survey, agree upon Starting Surfaces, and final lengths and produce final plans at horizontal scale of 1:200 for approval before proceeding further. | LS | 1 |  | 0
1.2 | General Clearance for urban land & rough grass land along pipeline wayleaves (trench width plus 0.5 m on either side) | ha | 0.1 |  | 0
1.3 | Removal of tree stumps within approved alignment. PROVISIONAL SUM | nr | 1 |  | 0
1.4 | Cut down and remove trees and tree stumps within approved alignment only if specifically directed to do so by Inspector of Works following agreement from the Host Community PROVISIONAL SUM | nr | 1 |  | 0
Bill No. 2: Excavation and backfilling of trenches - all pipelines |  |  |  |  | 0
2.1 | Excavate test pits along centre line of proposed pipeline to depth of 1m at least every 50 m | nr | 4 |  | 0
2.2 | Excavate and trim trench bed to depth not exceeding 1 m to ensure minimum cover provided to pipeline is not less than 600 mm | m | 160.2 |  | 0
2.3 | E. O. item 2.2 at road crossings. Excavate and trim trench to additional depth not exceeding 1.5 m to ensure minimum cover provided to the pipeline is 900 mm | m | 17.8 |  | 0
2.4 | Over excavate trench by a further depth of 150mm in areas identified by the Inspector of Works as requiring imported granular backfill RATE ONLY | m3 | 1.602 |  | 0
2.5 | Import, place and compact granular backfill in areas identified by the Inspector of Works as requiring imported granular backfill. RATE ONLY, | m3 | 1.602 |  | 0
2.6 | Place and compact sidefill and backfill using selected excavated material free of stones and tree roots to depth 300 mm above crown of pipe, and after compaction, other excavated material thereafter to final surface | m | 160.2 |  | 0
2.7 | Dispose of all surplus excavated material off-site as directed | LS | 1 |  | 0
Bill No. 3: Supply and Installation of rising main- borehole to elevated water tank |  |  |  |  | 0
All PE compression joints and fittings shall be supplied complete with suitable pipe joint stiffeners. All steel fittings shall be epoxy coated and all nuts and bolts galvanised. Rate shall include supply, lay, bed, joint , pressure test, sterilize and flushing of HDPE pipelines
3.1 | Raw water rising main from borehole to the Elevated Tank , HDPE DN50 (OD 63), SDR17, PN 10 | m | 8 |  | 0
3.2 | Compression fitting, elbow 90o DN 50mm | nr | 1
3.3 | Gate Valve, double flange, handwheel operated 50 mm non-rising spindle type, with 1 No. flanged restraining adapters st. fl. to PE DN 50, installed above ground within tank inlet riser pipe | set | 1 |  | 0
3.4 | Supply and Installation of DN 40 parallel bulk water meter with magnetic transmission and dry recording head , metrological class B, minimum display 1 m3/hr to specification, suitable for vertical mounting, within water tank inlet riser pipe complete with strainer (metallic double flanged body c/w lockable meter box pipe surround). The meter assembly shall comprise: 1 No. DN50 to DN40 reducer, 1 DN40 500mm long straight pipe length, 1 DN 40 mm double flanged vertically mounted parallel bulk type meter, located approximately 1.5 m above ground level, 1 DN 40 250 mm straight pipe length, and one DN40 to DN50 reducer. | set | 1 |  | 0
| Carry forward |  |  |  | 0
| Brought forward |  |  |  | 0
Bill No. 4: Tanks, Tankstands and Tap Stands |  |  |  |  | 0
Bidder shall supply outline details of water tank stand and tank c/w, pipework and fittings.
water tank stand manufacturer:
HDPE cylindrical tank manufacturer:
HDPE cylindrical tank supplier (if different):
Contractor shall supply full set of structural calculations and drawings for water tank stand certified by a registered structural engineer for written approval prior to fabrication.
4.1 | Conduct geotechnical investigations and design foundation and tank stand for the elevated tank | LS | 1 |  | 0
4.2 | Tank reinforced concrete foundations 1 m x 1m x 1.5 m deep inc. excavation, shuttering, concreting, curing, backfilling and disposal of excess spoil material from site | nr | 6 |  | 0
Supply and install 2 No. HDPE cylindrical tank on Contractor designed six vertical members) mild steel tankstand c/w with inlet float valves, all inflow, valved connecting, outflow, overflow, and scour (washout) pipework, fittings, adaptors and 6m high steel stand c/w access ladder and lightning arrestor.
4.3 | Capacity 15m3. (2 no. 7.5 m3) | nr | 1 |  | 0
4.4 | Supply and paint all mild steel in tank stand with two coats of zinc 82% rich paint in dry film | LS | 1 |  | 0
4.5 | Leak testing and disinfection of tank and pipework | nr | 1 |  | 0
4.6 | Provide & install float level indicator gauge on side of tank readable from ground level adjacent to tank | nr | 1 |  | 0
4.7 | Provide and install chlorine cartridge type inline doser in lockable chamber at start of tank outlet pipe c/w twelve months supply of chlorine cartridges. | LS | 1 |  | 0
4.8 | Provide materials for and construct tap stand and associated drainage | nr | 3 |  | 0
Bill No. 5: Supply and Install Water Distribution Network |  |  |  |  | 0
All PE compression joints and fittings shall be supplied complete with suitable pipe joint stiffeners. All steel fittings shall be epoxy coated and all nuts and bolts galvanised. Rate shall include supply, lay, bed, joint , pressure test, sterilize and flushing of HDPE pipelines
5.1 | Network reticulation pipework HDPE DN50 (OD 63), SDR17, PN 10 | m | 11 |  | 0
5.2 | Equal tee compression fitting DN 50 x 50 x 50 mm | nr | 1 |  | 0
5.3 | Compression reducer coupling 50mm x 40mm | nr | 2 |  | 0
5.4 | Compression reducer coupling 50mm x 32mm | nr | 2 |  | 0
5.5 | Network reticulation pipework HDPE DN 32mm, SDR17, PN 10 | m | 159 |  | 0
5.6 | Compression fitting, elbow 90o DN 32mm | nr | 1 |  | 0
5.7 | End cap DN 32mm (compression type) | nr | 2 |  | 0
5.8 | Supply and install GI pipes 25mm dia c/w fittings to tap stands c/w isolating stop cock | nr | 3 |  | 0
5.9 | Supply and install heavy weight brass garden bib tap (non-lever arm type) | nr | 6 |  | 0
5.1 | Compression tee DN 32 x 32 x 1" male branch to connect to tap stand pipework | nr | 3 |  | 0
5.11 | Gate Valve, double flange, 40 mm non-rising spindle type, with 2 No. flanged restraining adapters st. fl. to PE DN 40, complete with valve riser and valve box to suit | nr | 1 |  | 0
Air valve assembly consisting of 1 No. compression tee with threaded male 1 1/2" branch vertically upwards, 1 No. female to male thr. spigot, 1 No. Stopcock, thr. dble. socket 1", and 1 No. Single air valve, thr. female 1". RATE ONLY
5.12.1 | Compression tee DN 50 x 50 x 1 1/2" male br., 1 No. female to male 1 1/2" to 1" thr. spigot | set | 0
5.12.2 | Compression tee DN 32 x 32 x 1" male br, 1 No. female to male 1" to 1" thr. spigot | set | 0
| Carry forward |  |  |  | 0
| Brought forward |  |  |  | 0
Bill No. 6: Concrete Works to all Pipelines |  |  |  |  | 0
All unreinforced concrete works shall be in medium strength concrete unless otherwise indicated. Where bends less than 45o are obtained by bending the pipe, radius not less than 35 x pipe diameter, and provided there is no compression joint with 5 metres of either end of radius, no separate thrust block is required.
6.1 | Over excavate in trench bed at all gate valves, air valve assemblies and steel fittings and cast support slab to full width of trench with other dimensions being the length of the valve or the fitting between flanges or between the compression tightening nuts and depth below trench bed of 150 mm | nr | 1 |  | 0
6.2 | At all 45o and 90o bends, pipeline tees, and end caps, provide and subsequently remove shuttering and cast thrust blocks against undisturbed trench bed and trench wall | nr | 5 |  | 0
6.3 | Supply all materials and cast and complete air-valve chamber. RATE ONLY | nr | 1
| Sub-total Bill Nos 1 to 6 |  |  |  | 0
| Contingencies (10%) Bills No 1 to 6 |  |  |  | 0
| Taxes (VAT @16%) Bills Nos 1 to 6 |  |  |  | 0
| Total Bills Nos 1 to 6 |  |  |  | 0
Bill 7A | Electromechanical - OPTION A Solar Powered |  |  |  | 0
Bidder shall supply all the information and rates for both Alternatives for the offer to be considered. Final decision on the main power source (Option A ZESCO mains power from institutions incoming distribution board, or Option B from Solar Array will be confirmed during negotiation prior to award.
proposed submersible hybrid DC/AC pumpset manufacturer and agent:
proposed standby generator manufacturer and agent:
| confirm manufactures brochures included with bid |  | yes / no
No change from these manufacturers or agents shall be permitted without prior written approval from the Consultant
Submersible 48 VDC Borehole Pump
7.1 | Supply and install a hybrid DC/AC borehole submersible pump suitable for a borehole of ID 5" capable of being powered from either a 48 VDC or a nominal 230 VAC source c/w cabled connection to power sources located within 10 m of borehole head, pumping into an overhead tank with top water inlet 14 m above ground.. . |  | nr | 1
Information provided to guide Bidder
| Ground elevation at borehole (approximate) | masl | 961
| Yield | m3/hr | 1.2
| Pump installation level below ground surface | m | 49
| Riser pipe diameter | mm | DN 50
| Dynamic water level below ground surface | m | 38.84
| Top water level in overhead tank | masl | 977
Information to be provided by Bidder
| Manufacturers Pump reference No. | ref.
| Maximum flow at Installation indicated above | m3/hr
| Maximum pump head at installation indicated above | m3/hr
| Optimum flow at Installation indicated above | m3/hr
| Optimum head at Installation indicated above | m3/hr
| Pump efficiency at installation | %
| Input power required by pump | W
| Output power required by solar array | W
| No. of solar panels and arrays offered and guaranteed to meet requirement | nr
7.2 | Solar arrays to meet requirements c/w security fence and gate and lightning protection as per Drawing to be included in this Option
7.2.1 | Supply, install, erect and connect solar arrays to meet requirements c/w lightning protection as per Drawing and Specification | nr | 1 |  | 0
7.2.2 | Provide all materials and construct fenced and gated compound to contain solar array and associated chambers to Specification. | LS | 1 |  | 0
7.2.3 | Supply and install DN 25 water pipe take-off from rising mainand sgtandpipe for solar cleansing system | LS | 1 |  | 0
7.2.4 | Provide solar array cleansing step ladder and extendable washer to Specification | LS | 1 |  | 0
Supply and Installation of 220 VAC standby generator of rated power
7.3 | Supply, Install and connect by manually operated changeover switch standby generator capable of providing the VAC power required to operate the submersible borehole pump as specified above at half-load c/w roofed lockable waterproof steel protection cabinet. | nr | 1 |  | 0
Information to be provided by Bidder
Manufacturers Generator Set reference No.
| Output kVA at 1500rpm, 220V, single-phase, 50Hz, with power factor of 1.0 | kVA
| Fuel type (petrol/diesel) | type
| Fuel tank capacity | l
Air or water cooled
7.4 | External 230 VAC Power Source to be included in Option B
| Sub-total Bill No 7A |  |  |  | 0
| Contingencies (10%) Bill No 7A |  |  |  | 0
| Taxes (VAT @16%) Bill No 7A |  |  |  | 0
| Total Bill No 7A |  |  |  | 0
Bill 7B | Electromechanical - OPTION B Mains electric poweredElectromechanical |  |  |  | 0
Bidder shall supply all the information and rates for both Alternatives for the offer to be considered. Final decision on the main power source (Option A ZESCO mains power from institutions incoming distribution board, or Option B from Solar Array will be confirmed during negotiation prior to award.
proposed submersible hybrid DC/AC pumpset manufacturer and agent:
proposed standby generator manufacturer and agent:
| confirm manufactures brochures included with bid |  | yes / no
No change from these manufacturers or agents shall be permitted without prior written approval from the Consultant
Submersible 48 VDC Borehole Pump
7.1 | Supply and install a hybrid DC/AC borehole submersible pump suitable for a borehole of ID 5" capable of being powered from either a 48 VDC or a nominal 230 VAC source c/w cabled connection to power sources located within 10 m of borehole head, pumping into an overhead tank with top water inlet 14 m above ground.. . |  | nr | 1
Information provided to guide Bidder
| Ground elevation at borehole (approximate) | masl | 961
| Yield | m3/hr | 1.2
| Pump installation level below ground surface | m | 49
| Riser pipe diameter | mm | DN 50
| Dynamic water level below ground surface | m | 38.84
| Top water level in overhead tank | masl | 977
Information to be provided by Bidder
| Manufacturers Pump reference No. | ref.
| Maximum flow at Installation indicated above | m3/hr
| Maximum pump head at installation indicated above | m3/hr
| Optimum flow at Installation indicated above | m3/hr
| Optimum head at Installation indicated above | m3/hr
| Pump efficiency at installation | %
| Input power required by pump | W
| Output power required by solar array | W
| No. of solar panels and arrays offered and guaranteed to meet requirement | nr
7.2 | Solar arrays to be included in Option A
Supply and Installation of 220 VAC standby generator of rated power
7.3 | Supply, Install and connect by manually operated changeover switch standby generator capable of providing the VAC power required to operate the submersible borehole pump as specified above at half-load c/w roofed lockable waterproof steel protection cabinet. | nr | 1 |  | 0
Information to be provided by Bidder
Manufacturers Generator Set reference No.
| Output kVA at 1500rpm, 220V, single-phase, 50Hz, with power factor of 1.0 | kVA
| Fuel type (petrol/diesel) | type
| Fuel tank capacity | l
Air or water cooled
External 230 VAC Power Source
7.4 | Underground armoured cable c/w all internal building works, and making good, outside excavation, backfilling and protective concrete cover slabs from Main Distribution Board |  | 0
7.4.1 | All ancilliary work excludng outside excavation, and backfilling, supply and installation of underground armoured cable and protective concrete cover slabs | nr | 1 |  | 0
7.4.2 | External excavation, and backfilling, supply and installation of underground armoured cable and protective concrete cover slabs, minimum cover to cable 600 mm. Length subject to reconfirmation prior to award. | m | 115 |  | 0
| Sub-total Bill No 7B |  |  |  | 0
| Contingencies (10%) Bill No 7B |  |  |  | 0
| Taxes (VAT @16%) Bill No 7B |  |  |  | 0
| Total Bill No 7B |  |  |  | 0

## Kampampi Primary
UNICEF
Solar Powered Borehole Schemes in institutions in Nchelenge (Mantapala) Refugee Camp & Host Communities
Kampampi Primary School
Bill No. SCH3:
Item | Description | Unit | Qty | Rate (ZMW) | Amount (ZMW)
Bill No. out, Demolition and Site Clearance |  |  |  |  | 0
1.1 | In collaboration with the Inspector of Works, and based upon pipe lengths and alignment shown on layout plan, agree upon final alignment of pipelines, road crossings, location of all tees, bends, isolating valves, air valves, washouts, tapstands, and consumer connection offtakes. Set out pipeline centre-lines, survey, agree upon Starting Surfaces, and final lengths and produce final plans at horizontal scale of 1:200 for approval before proceeding further. | LS | 1 |  | 0
1.2 | General Clearance for urban land & rough grass land along pipeline wayleaves (trench width plus 0.5 m on either side) | ha | 0.1 |  | 0
1.3 | Removal of tree stumps within approved alignment. PROVISIONAL SUM | nr | 1 |  | 0
1.4 | Cut down and remove trees and tree stumps within approved alignment only if specifically directed to do so by Inspector of Works following agreement from the Host Community PROVISIONAL SUM | nr | 1 |  | 0
Bill No. 2: Excavation and backfilling of trenches - all pipelines |  |  |  |  | 0
2.1 | Excavate test pits along centre line of proposed pipeline to depth of 1m at least every 50 m | nr | 9 |  | 0
2.2 | Excavate and trim trench bed to depth not exceeding 1 m to ensure minimum cover provided to pipeline is not less than 600 mm | m | 365.4 |  | 0
2.3 | E. O. item 2.2 at road crossings. Excavate and trim trench to additional depth not exceeding 1.5 m to ensure minimum cover provided to the pipeline is 900 mm | m | 40.6 |  | 0
2.4 | Over excavate trench by a further depth of 150mm in areas identified by the Inspector of Works as requiring imported granular backfill RATE ONLY | m3 | 3.654 |  | 0
2.5 | Import, place and compact granular backfill in areas identified by the Inspector of Works as requiring imported granular backfill. RATE ONLY, | m3 | 3.654 |  | 0
2.6 | Place and compact sidefill and backfill using selected excavated material free of stones and tree roots to depth 300 mm above crown of pipe, and after compaction, other excavated material thereafter to final surface | m | 365.4 |  | 0
2.7 | Dispose of all surplus excavated material off-site as directed | LS | 1 |  | 0
Bill No. 3: Supply and Installation of rising main- borehole to elevated water tank |  |  |  |  | 0
All PE compression joints and fittings shall be supplied complete with suitable pipe joint stiffeners. All steel fittings shall be epoxy coated and all nuts and bolts galvanised. Rate shall include supply, lay, bed, joint , pressure test, sterilize and flushing of HDPE pipelines
3.1 | Raw water rising main from borehole to the Elevated Tank , HDPE DN50 (OD 63), SDR17, PN 10 | m | 16 |  | 0
3.2 | Gate Valve, double flange, handwheel operated 50 mm non-rising spindle type, with 1 No. flanged restraining adapters st. fl. to PE DN 50, installed above ground within tank inlet riser pipe | set | 1 |  | 0
3.3 | Supply and Installation of DN 40 parallel bulk water meter with magnetic transmission and dry recording head , metrological class B, minimum display 1 m3/hr to specification, suitable for vertical mounting, within water tank inlet riser pipe complete with strainer (metallic double flanged body c/w lockable meter box pipe surround). The meter assembly shall comprise: 1 No. DN50 to DN40 reducer, 1 DN40 500mm long straight pipe length, 1 DN 40 mm double flanged vertically mounted parallel bulk type meter, located approximately 1.5 m above ground level, 1 DN 40 250 mm straight pipe length, and one DN40 to DN50 reducer. | set | 1 |  | 0
| Carry forward |  |  |  | 0
| Brought forward |  |  |  | 0
Bill No. 4: Tanks, Tankstands and Tap Stands |  |  |  |  | 0
Bidder shall supply outline details of water tank stand and tank c/w, pipework and fittings.
water tank stand manufacturer:
HDPE cylindrical tank manufacturer:
HDPE cylindrical tank supplier (if different):
Contractor shall supply full set of structural calculations and drawings for water tank stand certified by a registered structural engineer for written approval prior to fabrication.
4.1 | Conduct geotechnical investigations and design foundation and tank stand for the elevated tank | LS | 1 |  | 0
4.2 | Tank reinforced concrete foundations 1 m x 1m x 1.5 m deep inc. excavation, shuttering, concreting, curing, backfilling and disposal of excess spoil material from site | nr | 6 |  | 0
Supply and install 2 No. HDPE cylindrical tank on Contractor designed six vertical members) mild steel tankstand c/w with inlet float valves, all inflow, valved connecting, outflow, overflow, and scour (washout) pipework, fittings, adaptors and 6m high steel stand c/w access ladder and lightning arrestor.
4.3 | Capacity 10m3.(2 no. 5m3 tanks) | nr | 1 |  | 0
4.4 | Supply and paint all mild steel in tank stand with two coats of zinc 82% rich paint in dry film | LS | 1 |  | 0
4.5 | Leak testing and disinfection of tank and pipework | nr | 1 |  | 0
4.6 | Provide & install float level indicator gauge on side of tank readable from ground level adjacent to tank | nr | 1 |  | 0
4.7 | Provide and install chlorine cartridge type inline doser in lockable chamber at start of tank outlet pipe c/w twelve months supply of chlorine cartridges. | LS | 1 |  | 0
4.8 | Provide materials for and construct tap stand and associated drainage | nr | 4 |  | 0
Bill No. 5: Supply and Install Water Distribution Network |  |  |  |  | 0
All PE compression joints and fittings shall be supplied complete with suitable pipe joint stiffeners. All steel fittings shall be epoxy coated and all nuts and bolts galvanised. Rate shall include supply, lay, bed, joint , pressure test, sterilize and flushing of HDPE pipelines
5.1 | Network reticulation pipework HDPE DN50 (OD 63), SDR17, PN 10 | m | 153 |  | 0
5.2 | Equal tee compression fitting DN 50 x 50 x 50 mm | nr | 1 |  | 0
5.3 | Unequal reducing tee compression fitting DN 40 x 40 x 32 mm | nr | 2 |  | 0
5.4 | Compression reducer coupling 50mm x 40mm | nr | 3 |  | 0
5.5 | Compression reducer coupling 50mm x 32mm | nr | 1 |  | 0
5.6 | Network reticulation pipework HDPE DN 40mm, SDR17, PN 10 | m | 165 |  | 0
5.7 | Network reticulation pipework HDPE DN 32mm, SDR17, PN 10 | m | 72 |  | 0
5.8 | Compression fitting, elbow 90o DN 40mm | nr | 5 |  | 0
5.9 | End cap DN 32mm (compression type) | nr | 4 |  | 0
5.1 | Supply and install GI pipes 25mm dia c/w fittings to tap stands c/w isolating stop cock | nr | 4 |  | 0
5.11 | Supply and install heavy weight brass garden bib tap (non-lever arm type) | nr | 8 |  | 0
5.12 | Compression tee DN 32 x 32 x 1" male branch to connect to tap stand pipework | nr | 4 |  | 0
5.13 | Gate Valve, double flange, 40 mm non-rising spindle type, with 2 No. flanged restraining adapters st. fl. to PE DN 40, complete with valve riser and valve box to suit | nr | 2 |  | 0
Air valve assembly consisting of 1 No. compression tee with threaded male 1 1/2" branch vertically upwards, 1 No. female to male thr. spigot, 1 No. Stopcock, thr. dble. socket 1", and 1 No. Single air valve, thr. female 1". RATE ONLY
5.14.1 | Compression tee DN 50 x 50 x 1 1/2" male br., 1 No. female to male 1 1/2" to 1" thr. spigot | set | 0
5.14.2 | Compression tee DN 40 x 40 x 1 1/2" male br., 1 No. female to male 1 1/2" to 1" thr. Spigot | set | 0
5.14.3 | Compression tee DN 32 x 32 x 1" male br, 1 No. female to male 1" to 1" thr. spigot | set | 0
| Carry forward |  |  |  | 0
| Brought forward |  |  |  | 0
Bill No. 6: Concrete Works to all Pipelines |  |  |  |  | 0
All unreinforced concrete works shall be in medium strength concrete unless otherwise indicated.Where bends less than 45o are obtained by bending the pipe, radius not less than 35 x pipe diameter, and provided there is no compression joint with 5 metres of either end of radius, no separate thrust block is required.
6.1 | Over excavate in trench bed at all gate valves, air valve assemblies and steel fittings and cast support slab to full width of trench with other dimensions being the length of the valve or the fitting between flanges or between the compression tightening nuts and depth below trench bed of 150 mm | nr | 2 |  | 0
6.2 | At all 45o and 90o bends, pipeline tees, and end caps, provide and subsequently remove shuttering and cast thrust blocks against undisturbed trench bed and trench wall. | nr | 9 |  | 0
6.3 | Supply all materials and cast and complete air-valve chamber. RATE ONLY | nr | 1
| Sub-total Bill Nos 1 to 6 |  |  |  | 0
| Contingencies (10%) Bills No 1 to 6 |  |  |  | 0
| Taxes (VAT @16%) Bills Nos 1 to 6 |  |  |  | 0
| Total Bills Nos 1 to 6 |  |  |  | 0
Bill 7A | Electromechanical - OPTION A Solar Powered |  |  |  | 0
Bidder shall supply all the information and rates for both Alternatives for the offer to be considered. Final decision on the main power source (Option A ZESCO mains power from institutions incoming distribution board, or Option B from Solar Array will be confirmed during negotiation prior to award.
proposed submersible hybrid DC/AC pumpset manufacturer and agent:
proposed standby generator manufacturer and agent:
| confirm manufactures brochures included with bid |  | yes / no
No change from these manufacturers or agents shall be permitted without prior written approval from the Consultant
Submersible 48 VDC Borehole Pump
7.1 | Supply and install a hybrid DC/AC borehole submersible pump suitable for a borehole of ID 5" capable of being powered from either a 48 VDC or a nominal 230 VAC source c/w cabled connection to power sources located within 10 m of borehole head, pumping into an overhead tank with top water inlet 14 m above ground.. . |  | nr | 1
Information provided to guide Bidder
| Ground elevation at borehole (approximate) | masl | 948
| Yield | m3/hr | 1.5
| Pump installation level below ground surface | m | 44
| Riser pipe diameter | mm | DN 50
| Dynamic water level below ground surface | m | 27.12
| Top water level in overhead tank | masl | 962
Information to be provided by Bidder
| Manufacturers Pump reference No. | ref.
| Maximum flow at Installation indicated above | m3/hr
| Maximum pump head at installation indicated above | m3/hr
| Optimum flow at Installation indicated above | m3/hr
| Optimum head at Installation indicated above | m3/hr
| Pump efficiency at installation | %
| Input power required by pump | W
| Output power required by solar array | W
| No. of solar panels and arrays offered and guaranteed to meet requirement | nr
7.2 | Solar arrays to meet requirements c/w security fence and gate and lightning protection as per Drawing to be included in this Option
7.2.1 | Supply, install, erect and connect solar arrays to meet requirements c/w lightning protection as per Drawing and Specification | nr | 1 |  | 0
7.2.2 | Provide all materials and construct fenced and gated compound to contain solar array and associated chambers to Specification. | LS | 1 |  | 0
7.2.3 | Supply and install DN 25 water pipe take-off from rising mainand sgtandpipe for solar cleansing system | LS | 1 |  | 0
7.2.4 | Provide solar array cleansing step ladder and extendable washer to Specification | LS | 1 |  | 0
Supply and Installation of 220 VAC standby generator of rated power
7.3 | Supply, Install and connect by manually operated changeover switch standby generator capable of providing the VAC power required to operate the submersible borehole pump as specified above at half-load c/w roofed lockable waterproof steel protection cabinet. | nr | 1 |  | 0
Information to be provided by Bidder
Manufacturers Generator Set reference No.
| Output kVA at 1500rpm, 220V, single-phase, 50Hz, with power factor of 1.0 | kVA
| Fuel type (petrol/diesel) | type
| Fuel tank capacity | l
Air or water cooled
7.4 | External 230 VAC Power Source to be included in Option B
| Sub-total Bill No 7A |  |  |  | 0
| Contingencies (10%) Bill No 7A |  |  |  | 0
| Taxes (VAT @16%) Bill No 7A |  |  |  | 0
| Total Bill No 7A |  |  |  | 0
Bill 7B | Electromechanical - OPTION B Mains electric powered |  |  |  | 0
Bidder shall supply details of proposed pumpset c/w shroud, and standby generator for which there shall be a local agent
proposed submersible hybrid DC/AC pumpset manufacturer and agent:
proposed standby generator manufacturer and agent:
| confirm manufactures brochures included with bid |  | yes / no
Bidder shall supply all the information and rates for both Alternatives for the offer to be considered. Final decision on the main power source (Option A ZESCO mains power from institutions incoming distribution board, or Option B from Solar Array will be confirmed during negotiation prior to award.
Submersible 48 VDC Borehole Pump
7.1 | Supply and install a hybrid DC/AC borehole submersible pump suitable for a borehole of ID 5" capable of being powered from either a 48 VDC or a nominal 230 VAC source c/w cabled connection to power sources located within 10 m of borehole head, pumping into an overhead tank with top water inlet 14 m above ground.. . |  | nr | 1
Information provided to guide Bidder
| Ground elevation at borehole (approximate) | masl | 948
| Yield | m3/hr | 1.5
| Pump installation level below ground surface | m | 44
| Riser pipe diameter | mm | DN 50
| Dynamic water level below ground surface | m | 27.12
| Top water level in overhead tank | masl | 962
Information to be provided by Bidder
| Manufacturers Pump reference No. | ref.
| Maximum flow at Installation indicated above | m3/hr
| Maximum pump head at installation indicated above | m3/hr
| Optimum flow at Installation indicated above | m3/hr
| Optimum head at Installation indicated above | m3/hr
| Pump efficiency at installation | %
| Input power required by pump | W
| Output power required by solar array | W
| No. of solar panels and arrays offered and guaranteed to meet requirement | nr
7.2 | Solar arrays to be included in Option A
Supply and Installation of 220 VAC standby generator of rated power
7.3 | Supply, Install and connect by manually operated changeover switch standby generator capable of providing the VAC power required to operate the submersible borehole pump as specified above at half-load c/w roofed lockable waterproof steel protection cabinet. | nr | 1 |  | 0
Information to be provided by Bidder
Manufacturers Generator Set reference No.
| Output kVA at 1500rpm, 220V, single-phase, 50Hz, with power factor of 1.0 | kVA
| Fuel type (petrol/diesel) | type
| Fuel tank capacity | l
Air or water cooled
External 230 VAC Power Source
7.4 | Underground armoured cable c/w all internal building works, and making good, outside excavation, backfilling and protective concrete cover slabs from Main Distribution Board |  | 0
7.4.1 | All ancilliary work excludng outside excavation, and backfilling, supply and installation of underground armoured cable and protective concrete cover slabs | nr | 1 |  | 0
7.4.2 | External excavation, and backfilling, supply and installation of underground armoured cable and protective concrete cover slabs, minimum cover to cable 600 mm. Length subject to reconfirmation prior to award. | m | 125 |  | 0
| Sub-total Bill No 7B |  |  |  | 0
| Contingencies (10%) Bill No 7B |  |  |  | 0
| Taxes (VAT @16%) Bill No 7B |  |  |  | 0
| Total Bill No 7B |  |  |  | 0

## Kashikishi Primary
UNICEF
Solar Powered Borehole Schemes in institutions in Nchelenge (Mantapala) Refugee Camp & Host Communities
Kashikishi Primary School
Bill No. SCH4:
Item | Description | Unit | Qty | Rate (ZMW) | Amount (ZMW)
Bill No. out, Demolition and Site Clearance |  |  |  |  | 0
1.1 | In collaboration with the Inspector of Works, and based upon pipe lengths and alignment shown on layout plan, agree upon final alignment of pipelines, road crossings, location of all tees, bends, isolating valves, air valves, washouts, tapstands, and consumer connection offtakes. Set out pipeline centre-lines, survey, agree upon Starting Surfaces, and final lengths and produce final plans at horizontal scale of 1:200 for approval before proceeding further. | LS | 1 |  | 0
1.2 | General Clearance for urban land & rough grass land along pipeline wayleaves (trench width plus 0.5 m on either side) | ha | 0.1 |  | 0
1.3 | Removal of tree stumps within approved alignment. PROVISIONAL SUM | nr | 1 |  | 0
1.4 | Cut down and remove trees and tree stumps within approved alignment only if specifically directed to do so by Inspector of Works following agreement from the Host Community PROVISIONAL SUM | nr | 1 |  | 0
Bill No. 2: Excavation and backfilling of trenches - all pipelines |  |  |  |  | 0
2.1 | Excavate test pits along centre line of proposed pipeline to depth of 1m at least every 50 m | nr | 9 |  | 0
2.2 | Excavate and trim trench bed to depth not exceeding 1 m to ensure minimum cover provided to pipeline is not less than 600 mm | m | 379.8 |  | 0
2.3 | E. O. item 2.2 at road crossings. Excavate and trim trench to additional depth not exceeding 1.5 m to ensure minimum cover provided to the pipeline is 900 mm | m | 42.2 |  | 0
2.4 | Over excavate trench by a further depth of 150mm in areas identified by the Inspector of Works as requiring imported granular backfill RATE ONLY | m3 | 3.798 |  | 0
2.5 | Import, place and compact granular backfill in areas identified by the Inspector of Works as requiring imported granular backfill. RATE ONLY, | m3 | 3.798 |  | 0
2.6 | Place and compact sidefill and backfill using selected excavated material free of stones and tree roots to depth 300 mm above crown of pipe, and after compaction, other excavated material thereafter to final surface | m | 379.8 |  | 0
2.7 | Dispose of all surplus excavated material off-site as directed | LS | 1 |  | 0
Bill No. 3: Supply and Installation of rising main- borehole to elevated water tank |  |  |  |  | 0
All PE compression joints and fittings shall be supplied complete with suitable pipe joint stiffeners. All steel fittings shall be epoxy coated and all nuts and bolts galvanised. Rate shall include supply, lay, bed, joint , pressure test, sterilize and flushing of HDPE pipelines
3.1 | Raw water rising main from borehole to the Elevated Tank , HDPE DN50 (OD 63), SDR17, PN 10 | m | 135 |  | 0
3.2 | Compression fitting, elbow 45o DN 50mm | nr | 2 |  | 0
3.3 | Compression fitting, elbow 90o DN 50mm | nr | 1
3.4 | Gate Valve, double flange, handwheel operated 50 mm non-rising spindle type, with 1 No. flanged restraining adapters st. fl. to PE DN 50, installed above ground within tank inlet riser pipe | set | 1 |  | 0
3.5 | Supply and Installation of DN 40 parallel bulk water meter with magnetic transmission and dry recording head , metrological class B, minimum display 1 m3/hr to specification, suitable for vertical mounting, within water tank inlet riser pipe complete with strainer (metallic double flanged body c/w lockable meter box pipe surround). The meter assembly shall comprise: 1 No. DN50 to DN40 reducer, 1 DN40 500mm long straight pipe length, 1 DN 40 mm double flanged vertically mounted parallel bulk type meter, located approximately 1.5 m above ground level, 1 DN 40 250 mm straight pipe length, and one DN40 to DN50 reducer. | set | 1 |  | 0
| Carry forward |  |  |  | 0
| Brought forward |  |  |  | 0
Bill No. 4: Tanks, Tankstands and Tap Stands |  |  |  |  | 0
Bidder shall supply outline details of water tank stand and tank c/w, pipework and fittings.
water tank stand manufacturer:
HDPE cylindrical tank manufacturer:
HDPE cylindrical tank supplier (if different):
Contractor shall supply full set of structural calculations and drawings for water tank stand certified by a registered structural engineer for written approval prior to fabrication.
4.1 | Conduct geotechnical investigations and design foundation and tank stand for the elevated tank | LS | 1 |  | 0
4.2 | Tank reinforced concrete foundations 1 m x 1m x 1.5 m deep inc. excavation, shuttering, concreting, curing, backfilling and disposal of excess spoil material from site | nr | 6 |  | 0
Supply and install 2 No. HDPE cylindrical tank on Contractor designed six vertical members) mild steel tankstand c/w with inlet float valves, all inflow, valved connecting, outflow, overflow, and scour (washout) pipework, fittings, adaptors and 6m high steel stand c/w access ladder and lightning arrestor.
4.3 | Capacity 20m3.(2 no. 10m3 tanks) | nr | 1 |  | 0
4.4 | Supply and paint all mild steel in tank stand with two coats of zinc 82% rich paint in dry film | LS | 1 |  | 0
4.5 | Leak testing and disinfection of tank and pipework | nr | 1 |  | 0
4.6 | Provide & install float level indicator gauge on side of tank readable from ground level adjacent to tank | nr | 1 |  | 0
4.7 | Provide and install chlorine cartridge type inline doser in lockable chamber at start of tank outlet pipe c/w twelve months supply of chlorine cartridges. | LS | 1 |  | 0
4.8 | Provide materials for and construct tap stand and associated drainage | nr | 4 |  | 0
Bill No. 5: Supply and Install Water Distribution Network |  |  |  |  | 0
All PE compression joints and fittings shall be supplied complete with suitable pipe joint stiffeners. All steel fittings shall be epoxy coated and all nuts and bolts galvanised. Rate shall include supply, lay, bed, joint , pressure test, sterilize and flushing of HDPE pipelines
5.1 | Network reticulation pipework HDPE DN63, SDR17, PN 10 | m | 47 |  | 0
5.2 | Unequal reducing tee compression fitting DN 63 x 63 x 40 mm | nr | 1 |  | 0
5.3 | Unequal reducing tee compression fitting DN 63 x 63 x 32 mm | nr | 1 |  | 0
5.4 | Compression reducer coupling 63mm x 40mm | nr | 1 |  | 0
5.5 | Network reticulation pipework HDPE DN 40mm, SDR17, PN 10 | m | 208 |  | 0
5.6 | Network reticulation pipework HDPE DN 32mm, SDR17, PN 10 | m | 32 |  | 0
5.7 | Compression fitting, elbow 45o DN 32mm | nr | 1 |  | 0
5.8 | Compression fitting, elbow 90o DN 40mm | nr | 1 |  | 0
5.9 | End cap DN 32mm (compression type) | nr | 3 |  | 0
5.1 | Supply and install GI pipes 25mm dia c/w fittings to tap stands c/w isolating stop cock | nr | 4 |  | 0
5.11 | Supply and install heavy weight brass garden bib tap (non-lever arm type) | nr | 8 |  | 0
5.12 | Compression tee DN 32 x 32 x 1" male branch to connect to tap stand pipework | nr | 4 |  | 0
5.13 | Gate Valve, double flange, 40 mm non-rising spindle type, with 2 No. flanged restraining adapters st. fl. to PE DN 40, complete with valve riser and valve box to suit | nr | 2 |  | 0
Air valve assembly consisting of 1 No. compression tee with threaded male 1 1/2" branch vertically upwards, 1 No. female to male thr. spigot, 1 No. Stopcock, thr. dble. socket 1", and 1 No. Single air valve, thr. female 1". RATE ONLY
5.14.1 | Compression tee DN 50 x 50 x 1 1/2" male br., 1 No. female to male 1 1/2" to 1" thr. spigot | set | 0
5.14.2 | Compression tee DN 40 x 40 x 1 1/2" male br., 1 No. female to male 1 1/2" to 1" thr. Spigot | set | 0
5.14.3 | Compression tee DN 32 x 32 x 1" male br, 1 No. female to male 1" to 1" thr. spigot | set | 0
| Carry forward |  |  |  | 0
| Brought forward |  |  |  | 0
Bill No. 6: Concrete Works to all Pipelines |  |  |  |  | 0
All unreinforced concrete works shall be in medium strength concrete unless otherwise indicated. Where bends less than 45o are obtained by bending the pipe, radius not less than 35 x pipe diameter, and provided there is no compression joint with 5 metres of either end of radius, no separate thrust block is required.
6.1 | Over excavate in trench bed at all gate valves, air valve assemblies and steel fittings and cast support slab to full width of trench with other dimensions being the length of the valve or the fitting between flanges or between the compression tightening nuts and depth below trench bed of 150 mm | nr | 2 |  | 0
6.2 | At all 45o and 90o bends, pipeline tees, and endcap, provide and subsequently remove shuttering and cast thrust blocks against undisturbed trench bed and trench wall | nr | 8 |  | 0
6.3 | Supply all materials and cast and complete air-valve chamber. RATE ONLY | nr | 1
| Sub-total Bill Nos 1 to 6 |  |  |  | 0
| Contingencies (10%) Bills No 1 to 6 |  |  |  | 0
| Taxes (VAT @16%) Bills Nos 1 to 6 |  |  |  | 0
| Total Bills Nos 1 to 6 |  |  |  | 0
Bill 7A | Electromechanical - OPTION A Solar Powered |  |  |  | 0
Bidder shall supply all the information and rates for both Alternatives for the offer to be considered. Final decision on the main power source (Option A ZESCO mains power from institutions incoming distribution board, or Option B from Solar Array will be confirmed during negotiation prior to award.
proposed submersible hybrid DC/AC pumpset manufacturer and agent:
proposed standby generator manufacturer and agent:
| confirm manufactures brochures included with bid |  | yes / no
No change from these manufacturers or agents shall be permitted without prior written approval from the Consultant
Submersible 48 VDC Borehole Pump
7.1 | Supply and install a hybrid DC/AC borehole submersible pump suitable for a borehole of ID 5" capable of being powered from either a 48 VDC or a nominal 230 VAC source c/w cabled connection to power sources located within 10 m of borehole head, pumping into an overhead tank with top water inlet 14 m above ground.. . |  | nr | 1
Information provided to guide Bidder
| Ground elevation at borehole (approximate) | masl | 944
| Yield | m3/hr | 1.8
| Pump installation level below ground surface | m | 35
| Riser pipe diameter | mm | DN 50
| Dynamic water level below ground surface | m | 20.65
| Top water level in overhead tank | masl | 959
Information to be provided by Bidder
| Manufacturers Pump reference No. | ref.
| Maximum flow at Installation indicated above | m3/hr
| Maximum pump head at installation indicated above | m3/hr
| Optimum flow at Installation indicated above | m3/hr
| Optimum head at Installation indicated above | m3/hr
| Pump efficiency at installation | %
| Input power required by pump | W
| Output power required by solar array | W
| No. of solar panels and arrays offered and guaranteed to meet requirement | nr
7.2 | Solar arrays to meet requirements c/w security fence and gate and lightning protection as per Drawing to be included in this Option
7.2.1 | Supply, install, erect and connect solar arrays to meet requirements c/w lightning protection as per Drawing and Specification | nr | 1 |  | 0
7.2.2 | Provide all materials and construct fenced and gated compound to contain solar array and associated chambers to Specification. | LS | 1 |  | 0
7.2.3 | Supply and install DN 25 water pipe take-off from rising mainand sgtandpipe for solar cleansing system | LS | 1 |  | 0
7.2.4 | Provide solar array cleansing step ladder and extendable washer to Specification | LS | 1 |  | 0
Supply and Installation of 220 VAC standby generator of rated power
7.3 | Supply, Install and connect by manually operated changeover switch standby generator capable of providing the VAC power required to operate the submersible borehole pump as specified above at half-load c/w roofed lockable waterproof steel protection cabinet. | nr | 1 |  | 0
Information to be provided by Bidder
Manufacturers Generator Set reference No.
| Output kVA at 1500rpm, 220V, single-phase, 50Hz, with power factor of 1.0 | kVA
| Fuel type (petrol/diesel) | type
| Fuel tank capacity | l
Air or water cooled
7.4 | External 230 VAC Power Source to be included in Option B |  | 0
0
| Sub-total Bill No 7A |  |  |  | 0
| Contingencies (10%) Bill No 7A |  |  |  | 0
| Taxes (VAT @16%) Bill No 7A |  |  |  | 0
| Total Bill No 7A |  |  |  | 0
Bill 7B | Electromechanical - OPTION B Mains electric powered |  |  |  | 0
Bidder shall supply all the information and rates for both Alternatives for the offer to be considered. Final decision on the main power source (Option A ZESCO mains power from institutions incoming distribution board, or Option B from Solar Array will be confirmed during negotiation prior to award.
proposed submersible hybrid DC/AC pumpset manufacturer and agent:
proposed standby generator manufacturer and agent:
| confirm manufactures brochures included with bid |  | yes / no
No change from these manufacturers or agents shall be permitted without prior written approval from the Consultant
Submersible 48 VDC Borehole Pump
7.1 | Supply and install a hybrid DC/AC borehole submersible pump suitable for a borehole of ID 5" capable of being powered from either a 48 VDC or a nominal 230 VAC source c/w cabled connection to power sources located within 10 m of borehole head, pumping into an overhead tank with top water inlet 14 m above ground.. . |  | nr | 1
Information provided to guide Bidder
| Ground elevation at borehole (approximate) | masl | 944
| Yield | m3/hr | 1.8
| Pump installation level below ground surface | m | 35
| Riser pipe diameter | mm | DN 50
| Dynamic water level below ground surface | m | 20.65
| Top water level in overhead tank | masl | 959
Information to be provided by Bidder
| Manufacturers Pump reference No. | ref.
| Maximum flow at Installation indicated above | m3/hr
| Maximum pump head at installation indicated above | m3/hr
| Optimum flow at Installation indicated above | m3/hr
| Optimum head at Installation indicated above | m3/hr
| Pump efficiency at installation | %
| Input power required by pump | W
| Output power required by solar array | W
| No. of solar panels and arrays offered and guaranteed to meet requirement | nr
7.2 | Solar arrays to be included in Option A
Supply and Installation of 220 VAC standby generator of rated power
7.3 | Supply, Install and connect by manually operated changeover switch standby generator capable of providing the VAC power required to operate the submersible borehole pump as specified above at half-load c/w roofed lockable waterproof steel protection cabinet. | nr | 1 |  | 0
Information to be provided by Bidder
Manufacturers Generator Set reference No.
| Output kVA at 1500rpm, 220V, single-phase, 50Hz, with power factor of 1.0 | kVA
| Fuel type (petrol/diesel) | type
| Fuel tank capacity | l
Air or water cooled
External 230 VAC Power Source
7.4 | Underground armoured cable c/w all internal building works, and making good, outside excavation, backfilling and protective concrete cover slabs from Main Distribution Board |  | 0
7.4.1 | All ancilliary work excludng outside excavation, and backfilling, supply and installation of underground armoured cable and protective concrete cover slabs | nr | 1 |  | 0
7.4.2 | External excavation, and backfilling, supply and installation of underground armoured cable and protective concrete cover slabs, minimum cover to cable 600 mm. Length subject to reconfirmation prior to award. | m | 80 |  | 0
| Sub-total Bill No 7B |  |  |  | 0
| Contingencies (10%) Bill No 7B |  |  |  | 0
| Taxes (VAT @16%) Bill No 7B |  |  |  | 0
| Total Bill No 7B |  |  |  | 0

## Nchelenge Sec. Sch
UNICEF
Solar Powered Borehole Schemes in institutions in Nchelenge (Mantapala) Refugee Camp & Host Communities
Nchelenge Secondary School
Bill No. SCH5:
Item | Description | Unit | Qty | Rate (ZMW) | Amount (ZMW)
Bill No. out, Demolition and Site Clearance |  |  |  |  | 0
1.1 | In collaboration with the Inspector of Works, and based upon pipe lengths and alignment shown on layout plan, agree upon final alignment of pipelines, road crossings, location of all tees, bends, isolating valves, air valves, washouts, tapstands, and consumer connection offtakes. Set out pipeline centre-lines, survey, agree upon Starting Surfaces, and final lengths and produce final plans at horizontal scale of 1:200 for approval before proceeding further. | LS | 1 |  | 0
1.2 | General Clearance for urban land & rough grass land along pipeline wayleaves (trench width plus 0.5 m on either side) | ha | 0.2 |  | 0
1.3 | Removal of tree stumps within approved alignment. PROVISIONAL SUM | nr | 1 |  | 0
1.4 | Cut down and remove trees and tree stumps within approved alignment only if specifically directed to do so by Inspector of Works following agreement from the Host Community PROVISIONAL SUM | nr | 1 |  | 0
Bill No. 2: Excavation and backfilling of trenches - all pipelines |  |  |  |  | 0
2.1 | Excavate test pits along centre line of proposed pipeline to depth of 1m at least every 50 m | nr | 19 |  | 0
2.2 | Excavate and trim trench bed to depth not exceeding 1 m to ensure minimum cover provided to pipeline is not less than 600 mm | m | 846 |  | 0
2.3 | E. O. item 2.2 at road crossings. Excavate and trim trench to additional depth not exceeding 1.5 m to ensure minimum cover provided to the pipeline is 900 mm | m | 94 |  | 0
2.4 | Over excavate trench by a further depth of 150mm in areas identified by the Inspector of Works as requiring imported granular backfill RATE ONLY | m3 | 8.46 |  | 0
2.5 | Import, place and compact granular backfill in areas identified by the Inspector of Works as requiring imported granular backfill. RATE ONLY, | m3 | 8.46 |  | 0
2.6 | Place and compact sidefill and backfill using selected excavated material free of stones and tree roots to depth 300 mm above crown of pipe, and after compaction, other excavated material thereafter to final surface | m | 846 |  | 0
2.7 | Dispose of all surplus excavated material off-site as directed | LS | 1 |  | 0
Bill No. 3: Supply and Installation of rising main- borehole to elevated water tank |  |  |  |  | 0
All PE compression joints and fittings shall be supplied complete with suitable pipe joint stiffeners. All steel fittings shall be epoxy coated and all nuts and bolts galvanised. Rate shall include supply, lay, bed, joint , pressure test, sterilize and flushing of HDPE pipelines
3.1 | Raw water rising main from borehole to the Elevated Tank , HDPE DN50 (OD 63), SDR17, PN 10 | m | 72 |  | 0
3.2 | Compression fitting, elbow 90o DN 50mm | nr | 2
3.3 | Gate Valve, double flange, handwheel operated 50 mm non-rising spindle type, with 1 No. flanged restraining adapters st. fl. to PE DN 50, installed above ground within tank inlet riser pipe | set | 1 |  | 0
3.4 | Supply and Installation of DN 40 parallel bulk water meter with magnetic transmission and dry recording head , metrological class B, minimum display 1 m3/hr to specification, suitable for vertical mounting, within water tank inlet riser pipe complete with strainer (metallic double flanged body c/w lockable meter box pipe surround). The meter assembly shall comprise: 1 No. DN50 to DN40 reducer, 1 DN40 500mm long straight pipe length, 1 DN 40 mm double flanged vertically mounted parallel bulk type meter, located approximately 1.5 m above ground level, 1 DN 40 250 mm straight pipe length, and one DN40 to DN50 reducer. | set | 1 |  | 0
| Carry forward |  |  |  | 0
| Brought forward |  |  |  | 0
Bill No. 4: Tanks, Tankstands and Tap Stands |  |  |  |  | 0
Bidder shall supply outline details of water tank stand and tank c/w, pipework and fittings.
water tank stand manufacturer:
HDPE cylindrical tank manufacturer:
HDPE cylindrical tank supplier (if different):
Contractor shall supply full set of structural calculations and drawings for water tank stand certified by a registered structural engineer for written approval prior to fabrication.
4.1 | Conduct geotechnical investigations and design foundation and tank stand for the elevated tank | LS | 1 |  | 0
4.2 | Tank reinforced concrete foundations 1 m x 1m x 1.5 m deep inc. excavation, shuttering, concreting, curing, backfilling and disposal of excess spoil material from site | nr | 6 |  | 0
Supply and install 2 No. HDPE cylindrical tank on Contractor designed six vertical members) mild steel tankstand c/w with inlet float valves, all inflow, valved connecting, outflow, overflow, and scour (washout) pipework, fittings, adaptors and 6m high steel stand c/w access ladder and lightning arrestor.
4.3 | Capacity 10m3.(2 no. 5m3 tanks) | nr | 1 |  | 0
4.4 | Supply and paint all mild steel in tank stand with two coats of zinc 82% rich paint in dry film | LS | 1 |  | 0
4.5 | Leak testing and disinfection of tank and pipework | nr | 1 |  | 0
4.6 | Provide & install float level indicator gauge on side of tank readable from ground level adjacent to tank | nr | 1 |  | 0
4.7 | Provide and install chlorine cartridge type inline doser in lockable chamber at start of tank outlet pipe c/w twelve months supply of chlorine cartridges. | LS | 1 |  | 0
4.8 | Provide materials for and construct tap stand and associated drainage | nr | 2 |  | 0
Bill No. 5: Supply and Install Water Distribution Network |  |  |  |  | 0
All PE compression joints and fittings shall be supplied complete with suitable pipe joint stiffeners. All steel fittings shall be epoxy coated and all nuts and bolts galvanised. Rate shall include supply, lay, bed, joint , pressure test, sterilize and flushing of HDPE pipelines
5.1 | Network reticulation pipework HDPE DN63, SDR17, PN 10 | m | 312 |  | 0
5.2 | Equal tee compression fitting DN 63 x 63 x 63 mm | nr | 2 |  | 0
5.3 | Unequal reducing tee compression fitting DN 63 x 63 x 40 mm | nr | 1 |  | 0
5.4 | Compression reducer coupling 63mm x 40mm | nr | 6 |  | 0
5.6 | Compression reducer coupling 40mm x 32mm | nr | 2 |  | 0
5.7 | Network reticulation pipework HDPE DN 40mm, SDR17, PN 10 | m | 550 |  | 0
5.8 | Network reticulation pipework HDPE DN 32mm, SDR17, PN 10 | m | 6 |  | 0
5.9 | Compression fitting, elbow 45o DN 40mm | nr | 2 |  | 0
5.1 | Compression fitting, elbow 90o DN 63 mm | nr | 4 |  | 0
5.11 | Compression fitting, elbow 90o DN 40mm | nr | 1 |  | 0
5.12 | End cap DN 32mm (compression type) | nr | 4 |  | 0
5.13 | Saddle clamp 32mm x 3/4" to supply individual consumer connection | nr | 2 |  | 0
5.14 | Supply and install GI pipes 25mm dia c/w fittings to tap stands c/w isolating stop cock | nr | 2 |  | 0
5.15 | Supply and install heavy weight brass garden bib tap (non-lever arm type) | nr | 4 |  | 0
5.16 | Compression tee DN 32 x 32 x 1" male branch to connect to tap stand pipework | nr | 2 |  | 0
5.17 | Gate Valve, double flange, 40 mm non-rising spindle type, with 2 No. flanged restraining adapters st. fl. to PE DN 40, complete with valve riser and valve box to suit | nr | 3 |  | 0
Air valve assembly consisting of 1 No. compression tee with threaded male 1 1/2" branch vertically upwards, 1 No. female to male thr. spigot, 1 No. Stopcock, thr. dble. socket 1", and 1 No. Single air valve, thr. female 1". RATE ONLY
5.18.1 | Compression tee DN 50 x 50 x 1 1/2" male br., 1 No. female to male 1 1/2" to 1" thr. spigot | set | 0
5.18.2 | Compression tee DN 40 x 40 x 1 1/2" male br., 1 No. female to male 1 1/2" to 1" thr. Spigot | set | 0
| Carry forward |  |  |  | 0
| Brought forward |  |  |  | 0
Bill No. 6: Concrete Works to all Pipelines |  |  |  |  | 0
All unreinforced concrete works shall be in medium strength concrete unless otherwise indicated. Where bends less than 45o are obtained by bending the pipe, radius not less than 35 x pipe diameter, and provided theere is no compression joint with 5 metres of either end of radius, no separate thrust block is required.
6.1 | Over excavate in trench bed at all gate valves, air valve assemblies and steel fittings and cast support slab to full width of trench with other dimensions being the length of the valve or the fitting between flanges or between the compression tightening nuts and depth below trench bed of 150 mm | nr | 3 |  | 0
6.2 | At all 45o and 90o bends, pipeline tees, and end caps provide and subsequently remove shuttering and cast thrust blocks against undisturbed trench bed and trench wall | nr | 14 |  | 0
6.3 | Supply all materials and cast and complete air-valve chamber. RATE ONLY | nr | 1
| Sub-total Bill Nos 1 to 6 |  |  |  | 0
| Contingencies (10%) Bills No 1 to 6 |  |  |  | 0
| Taxes (VAT @16%) Bills Nos 1 to 6 |  |  |  | 0
| Total Bills Nos 1 to 6 |  |  |  | 0
Bill 7A | Electromechanical - OPTION A Solar Powered |  |  |  | 0
Bidder shall supply all the information and rates for both Alternatives for the offer to be considered. Final decision on the main power source (Option A ZESCO mains power from institutions incoming distribution board, or Option B from Solar Array will be confirmed during negotiation prior to award.
proposed submersible hybrid DC/AC pumpset manufacturer and agent:
proposed standby generator manufacturer and agent:
| confirm manufactures brochures included with bid |  | yes / no
No change from these manufacturers or agents shall be permitted without prior written approval from the Consultant
Submersible 48 VDC Borehole Pump
7.1 | Supply and install a hybrid DC/AC borehole submersible pump suitable for a borehole of ID 5" capable of being powered from either a 48 VDC or a nominal 230 VAC source c/w cabled connection to power sources located within 10 m of borehole head, pumping into an overhead tank with top water inlet 14 m above ground.. . |  | nr | 1
Information provided to guide Bidder
| Ground elevation at borehole (approximate) | masl | 957
| Yield | m3/hr | 1
| Pump installation level below ground surface | m | 44
| Riser pipe diameter | mm | DN 50
| Dynamic water level below ground surface | m | 38.06
| Top water level in overhead tank | masl | 973
Information to be provided by Bidder
| Manufacturers Pump reference No. | ref.
| Maximum flow at Installation indicated above | m3/hr
| Maximum pump head at installation indicated above | m3/hr
| Optimum flow at Installation indicated above | m3/hr
| Optimum head at Installation indicated above | m3/hr
| Pump efficiency at installation | %
| Input power required by pump | W
| Output power required by solar array | W
| No. of solar panels and arrays offered and guaranteed to meet requirement | nr
7.2 | Solar arrays to meet requirements c/w security fence and gate and lightning protection as per Drawing to be included in this Option
7.2.1 | Supply, install, erect and connect solar arrays to meet requirements c/w lightning protection as per Drawing and Specification | nr | 1 |  | 0
7.2.2 | Provide all materials and construct fenced and gated compound to contain solar array and associated chambers to Specification. | LS | 1 |  | 0
7.2.3 | Supply and install DN 25 water pipe take-off from rising mainand sgtandpipe for solar cleansing system | LS | 1 |  | 0
7.2.4 | Provide solar array cleansing step ladder and extendable washer to Specification | LS | 1 |  | 0
Supply and Installation of 220 VAC standby generator of rated power
7.3 | Supply, Install and connect by manually operated changeover switch standby generator capable of providing the VAC power required to operate the submersible borehole pump as specified above at half-load c/w roofed lockable waterproof steel protection cabinet. | nr | 1 |  | 0
Information to be provided by Bidder
Manufacturers Generator Set reference No.
| Output kVA at 1500rpm, 220V, single-phase, 50Hz, with power factor of 1.0 | kVA
| Fuel type (petrol/diesel) | type
| Fuel tank capacity | l
Air or water cooled
7.4 | External 230 VAC Power Source to be included in Option B
| Sub-total Bill No 7A |  |  |  | 0
| Contingencies (10%) Bill No 7A |  |  |  | 0
| Taxes (VAT @16%) Bill No 7A |  |  |  | 0
| Total Bill No 7A |  |  |  | 0
Bill 7B | Electromechanical - OPTION B Mains electric powered |  |  |  | 0
Bidder shall supply all the information and rates for both Alternatives for the offer to be considered. Final decision on the main power source (Option A ZESCO mains power from institutions incoming distribution board, or Option B from Solar Array will be confirmed during negotiation prior to award.
proposed submersible hybrid DC/AC pumpset manufacturer and agent:
proposed standby generator manufacturer and agent:
| confirm manufactures brochures included with bid |  | yes / no
No change from these manufacturers or agents shall be permitted without prior written approval from the Consultant
Submersible 48 VDC Borehole Pump
7.1 | Supply and install a hybrid DC/AC borehole submersible pump suitable for a borehole of ID 5" capable of being powered from either a 48 VDC or a nominal 230 VAC source c/w cabled connection to power sources located within 10 m of borehole head, pumping into an overhead tank with top water inlet 14 m above ground.. . |  | nr | 1
Information provided to guide Bidder
| Ground elevation at borehole (approximate) | masl | 957
| Yield | m3/hr | 1
| Pump installation level below ground surface | m | 44
| Riser pipe diameter | mm | DN 50
| Dynamic water level below ground surface | m | 38.06
| Top water level in overhead tank | masl | 973
Information to be provided by Bidder
| Manufacturers Pump reference No. | ref.
| Maximum flow at Installation indicated above | m3/hr
| Maximum pump head at installation indicated above | m3/hr
| Optimum flow at Installation indicated above | m3/hr
| Optimum head at Installation indicated above | m3/hr
| Pump efficiency at installation | %
| Input power required by pump | W
| Output power required by solar array | W
| No. of solar panels and arrays offered and guaranteed to meet requirement | nr
7.2 | Solar arrays to be included in Option A
Supply and Installation of 220 VAC standby generator of rated power
7.3 | Supply, Install and connect by manually operated changeover switch standby generator capable of providing the VAC power required to operate the submersible borehole pump as specified above at half-load c/w roofed lockable waterproof steel protection cabinet. | nr | 1 |  | 0
Information to be provided by Bidder
Manufacturers Generator Set reference No.
| Output kVA at 1500rpm, 220V, single-phase, 50Hz, with power factor of 1.0 | kVA
| Fuel type (petrol/diesel) | type
| Fuel tank capacity | l
Air or water cooled
External 230 VAC Power Source
7.4 | Underground armoured cable c/w all internal building works, and making good, outside excavation, backfilling and protective concrete cover slabs from Main Distribution Board |  | 0
7.4.1 | All ancilliary work excludng outside excavation, and backfilling, supply and installation of underground armoured cable and protective concrete cover slabs | nr | 1 |  | 0
7.4.2 | External excavation, and backfilling, supply and installation of underground armoured cable and protective concrete cover slabs, minimum cover to cable 600 mm. Length subject to reconfirmation prior to award. | m | 155 |  | 0
| Sub-total Bill No 7B |  |  |  | 0
| Contingencies (10%) Bill No 7B |  |  |  | 0
| Taxes (VAT @16%) Bill No 7B |  |  |  | 0
| Total Bill No 7B |  |  |  | 0

## Kashita Sec. Sch.
UNICEF
Solar Powered Borehole Schemes in institutions in Nchelenge (Mantapala) Refugee Camp & Host Communities
Kashita Secondary School
Bill No. SCH6:
Item | Description | Unit | Qty | Rate (ZMW) | Amount (ZMW)
Bill No. out, Demolition and Site Clearance |  |  |  |  | 0
1.1 | In collaboration with the Inspector of Works, and based upon pipe lengths and alignment shown on layout plan, agree upon final alignment of pipelines, road crossings, location of all tees, bends, isolating valves, air valves, washouts, tapstands, and consumer connection offtakes. Set out pipeline centre-lines, survey, agree upon Starting Surfaces, and final lengths and produce final plans at horizontal scale of 1:200 for approval before proceeding further. | LS | 1 |  | 0
1.2 | General Clearance for urban land & rough grass land along pipeline wayleaves (trench width plus 0.5 m on either side) | ha | 0.1 |  | 0
1.3 | Removal of tree stumps within approved alignment. PROVISIONAL SUM | nr | 1 |  | 0
1.4 | Cut down and remove trees and tree stumps within approved alignment only if specifically directed to do so by Inspector of Works following agreement from the Host Community PROVISIONAL SUM | nr | 1 |  | 0
Bill No. 2: Excavation and backfilling of trenches - all pipelines |  |  |  |  | 0
2.1 | Excavate test pits along centre line of proposed pipeline to depth of 1m at least every 50 m | nr | 6 |  | 0
2.2 | Excavate and trim trench bed to depth not exceeding 1 m to ensure minimum cover provided to pipeline is not less than 600 mm | m | 260.1 |  | 0
2.3 | E. O. item 2.2 at road crossings. Excavate and trim trench to additional depth not exceeding 1.5 m to ensure minimum cover provided to the pipeline is 900 mm | m | 28.9 |  | 0
2.4 | Over excavate trench by a further depth of 150mm in areas identified by the Inspector of Works as requiring imported granular backfill RATE ONLY | m3 | 2.601 |  | 0
2.5 | Import, place and compact granular backfill in areas identified by the Inspector of Works as requiring imported granular backfill. RATE ONLY, | m3 | 2.601 |  | 0
2.6 | Place and compact sidefill and backfill using selected excavated material free of stones and tree roots to depth 300 mm above crown of pipe, and after compaction, other excavated material thereafter to final surface | m | 260.1 |  | 0
2.7 | Dispose of all surplus excavated material off-site as directed | LS | 1 |  | 0
Bill No. 3: Supply and Installation of rising main- borehole to elevated water tank |  |  |  |  | 0
All PE compression joints and fittings shall be supplied complete with suitable pipe joint stiffeners. All steel fittings shall be epoxy coated and all nuts and bolts galvanised. Rate shall include supply, lay, bed, joint , pressure test, sterilize and flushing of HDPE pipelines
3.1 | Raw water rising main from borehole to the Elevated Tank , HDPE DN50 (OD 63), SDR17, PN 10 | m | 101 |  | 0
3.2 | Compression fitting, elbow 90o DN 50mm | nr | 3 |  | 0
3.3 | Gate Valve, double flange, handwheel operated 50 mm non-rising spindle type, with 1 No. flanged restraining adapters st. fl. to PE DN 50, installed above ground within tank inlet riser pipe | set | 1 |  | 0
3.4 | Supply and Installation of DN 40 parallel bulk water meter with magnetic transmission and dry recording head , metrological class B, minimum display 1 m3/hr to specification, suitable for vertical mounting, within water tank inlet riser pipe complete with strainer (metallic double flanged body c/w lockable meter box pipe surround). The meter assembly shall comprise: 1 No. DN50 to DN40 reducer, 1 DN40 500mm long straight pipe length, 1 DN 40 mm double flanged vertically mounted parallel bulk type meter, located approximately 1.5 m above ground level, 1 DN 40 250 mm straight pipe length, and one DN40 to DN50 reducer. | set | 1 |  | 0
| Carry forward |  |  |  | 0
| Brought forward |  |  |  | 0
Bill No. 4: Tanks, Tankstands and Tap Stands |  |  |  |  | 0
Bidder shall supply outline details of water tank stand and tank c/w, pipework and fittings.
water tank stand manufacturer:
HDPE cylindrical tank manufacturer:
HDPE cylindrical tank supplier (if different):
Contractor shall supply full set of structural calculations and drawings for water tank stand certified by a registered structural engineer for written approval prior to fabrication.
4.1 | Conduct geotechnical investigations and design foundation and tank stand for the elevated tank | LS | 1 |  | 0
4.2 | Tank reinforced concrete foundations 1 m x 1m x 1.5 m deep inc. excavation, shuttering, concreting, curing, backfilling and disposal of excess spoil material from site | nr | 6 |  | 0
Supply and install 2 No. HDPE cylindrical tank on Contractor designed six vertical members) mild steel tankstand c/w with inlet float valves, all inflow, valved connecting, outflow, overflow, and scour (washout) pipework, fittings, adaptors and 6m high steel stand c/w access ladder and lightning arrestor.
4.3 | Capacity 10m3.(2 no 5m3 tanks) | nr | 1 |  | 0
4.4 | Supply and paint all mild steel in tank stand with two coats of zinc 82% rich paint in dry film | LS | 1 |  | 0
4.5 | Leak testing and disinfection of tank and pipework | nr | 1 |  | 0
4.6 | Provide & install float level indicator gauge on side of tank readable from ground level adjacent to tank | nr | 1 |  | 0
4.7 | Provide and install chlorine cartridge type inline doser in lockable chamber at start of tank outlet pipe c/w twelve months supply of chlorine cartridges. | LS | 1 |  | 0
4.8 | Provide materials for and construct tap stand and associated drainage | nr | 3 |  | 0
Bill No. 5: Supply and Install Water Distribution Network |  |  |  |  | 0
All PE compression joints and fittings shall be supplied complete with suitable pipe joint stiffeners. All steel fittings shall be epoxy coated and all nuts and bolts galvanised. Rate shall include supply, lay, bed, joint , pressure test, sterilize and flushing of HDPE pipelines
5.1 | Network reticulation pipework HDPE DN50 (OD 63), SDR17, PN 10 | m | 53 |  | 0
5.2 | Unequal reducing tee compression fitting DN 50 x 50 x 40 mm | nr | 1 |  | 0
5.3 | Unequal reducing tee compression fitting DN 40 x 40 x 32 mm | nr | 1 |  | 0
5.4 | Compression reducer coupling 50mm x 40mm | nr | 3 |  | 0
5.5 | Network reticulation pipework HDPE DN 40mm, SDR17, PN 10 | m | 113 |  | 0
5.6 | Network reticulation pipework HDPE DN 32mm, SDR17, PN 10 | m | 22 |  | 0
5.7 | Compression fitting, elbow 90o DN 50mm | nr | 2 |  | 0
5.8 | Compression fitting, elbow 90o DN 40mm | nr | 1 |  | 0
5.9 | End cap DN 32mm (compression type) | nr | 3 |  | 0
5.1 | Supply and install GI pipes 25mm dia c/w fittings to tap stands c/w isolating stop cock | nr | 3 |  | 0
5.11 | Supply and install heavy weight brass garden bib tap (non-lever arm type) | nr | 6 |  | 0
5.12 | Compression tee DN 40 x 40 x 1" male branch to connect to tap stand pipework | nr | 2 |  | 0
5.13 | Compression tee DN 32 x 32 x 1" male branch to connect to tap stand pipework | nr | 1 |  | 0
5.14 | Gate Valve, double flange, 40 mm non-rising spindle type, with 2 No. flanged restraining adapters st. fl. to PE DN 40, complete with valve riser and valve box to suit | nr | 2 |  | 0
Air valve assembly consisting of 1 No. compression tee with threaded male 1 1/2" branch vertically upwards, 1 No. female to male thr. spigot, 1 No. Stopcock, thr. dble. socket 1", and 1 No. Single air valve, thr. female 1". RATE ONLY
5.15.1 | Compression tee DN 50 x 50 x 1 1/2" male br., 1 No. female to male 1 1/2" to 1" thr. spigot | set | 0
5.15.2 | Compression tee DN 40 x 40 x 1 1/2" male br., 1 No. female to male 1 1/2" to 1" thr. Spigot | set | 0
5.15.3 | Compression tee DN 32 x 32 x 1" male br, 1 No. female to male 1" to 1" thr. spigot | set | 0
| Carry forward |  |  |  | 0
| Brought forward |  |  |  | 0
Bill No. 6: Concrete Works to all Pipelines |  |  |  |  | 0
All unreinforced concrete works shall be in medium strength concrete unless otherwise indicated. Where bends less than 45o are obtained by bending the pipe, radius not less than 35 x pipe diameter, and provided there is no compression joint with 5 metres of either end of radius, no separate thrust block is required.
6.1 | Over excavate in trench bed at all gate valves, air valve assemblies and steel fittings and cast support slab to full width of trench with other dimensions being the length of the valve or the fitting between flanges or between the compression tightening nuts and depth below trench bed of 150 mm | nr | 2 |  | 0
6.2 | At all 45o and 90o bends, pipeline tees, and end caps, provide and subsequently remove shuttering and cast thrust blocks against undisturbed trench bed and trench wall | nr | 12 |  | 0
6.3 | Supply all materials and cast and complete air-valve chamber. RATE ONLY | nr | 1
| Sub-total Bill Nos 1 to 6 |  |  |  | 0
| Contingencies (10%) Bills No 1 to 6 |  |  |  | 0
| Taxes (VAT @16%) Bills Nos 1 to 6 |  |  |  | 0
| Total Bills Nos 1 to 6 |  |  |  | 0
Bill 7A | Electromechanical - OPTION A Solar Powered |  |  |  | 0
Bidder shall supply all the information and rates for both Alternatives for the offer to be considered. Final decision on the main power source (Option A ZESCO mains power from institutions incoming distribution board, or Option B from Solar Array will be confirmed during negotiation prior to award.
proposed submersible hybrid DC/AC pumpset manufacturer and agent:
proposed standby generator manufacturer and agent:
| confirm manufactures brochures included with bid |  | yes / no
No change from these manufacturers or agents shall be permitted without prior written approval from the Consultant
Submersible 48 VDC Borehole Pump
7.1 | Supply and install a hybrid DC/AC borehole submersible pump suitable for a borehole of ID 5" capable of being powered from either a 48 VDC or a nominal 230 VAC source c/w cabled connection to power sources located within 10 m of borehole head, pumping into an overhead tank with top water inlet 14 m above ground.. . |  | nr | 1
Information provided to guide Bidder
| Ground elevation at borehole (approximate) | masl | 958
| Yield | m3/hr | 0.65
| Pump installation level below ground surface | m | 40
| Riser pipe diameter | mm | DN 50
| Dynamic water level below ground surface | m | 27.06
| Top water level in overhead tank | masl | 973
Information to be provided by Bidder
| Manufacturers Pump reference No. | ref.
| Maximum flow at Installation indicated above | m3/hr
| Maximum pump head at installation indicated above | m3/hr
| Optimum flow at Installation indicated above | m3/hr
| Optimum head at Installation indicated above | m3/hr
| Pump efficiency at installation | %
| Input power required by pump | W
| Output power required by solar array | W
| No. of solar panels and arrays offered and guaranteed to meet requirement | nr
7.2 | Solar arrays to meet requirements c/w security fence and gate and lightning protection as per Drawing to be included in this Option
7.2.1 | Supply, install, erect and connect solar arrays to meet requirements c/w lightning protection as per Drawing and Specification | nr | 1 |  | 0
7.2.2 | Provide all materials and construct fenced and gated compound to contain solar array and associated chambers to Specification. | LS | 1 |  | 0
7.2.3 | Supply and install DN 25 water pipe take-off from rising mainand sgtandpipe for solar cleansing system | LS | 1 |  | 0
7.2.4 | Provide solar array cleansing step ladder and extendable washer to Specification | LS | 1 |  | 0
Supply and Installation of 220 VAC standby generator of rated power
7.3 | Supply, Install and connect by manually operated changeover switch standby generator capable of providing the VAC power required to operate the submersible borehole pump as specified above at half-load c/w roofed lockable waterproof steel protection cabinet. | nr | 1 |  | 0
Information to be provided by Bidder
Manufacturers Generator Set reference No.
| Output kVA at 1500rpm, 220V, single-phase, 50Hz, with power factor of 1.0 | kVA
| Fuel type (petrol/diesel) | type
| Fuel tank capacity | l
Air or water cooled
7.4 | External 230 VAC Power Source to be included in Option B
| Sub-total Bill No 7A |  |  |  | 0
| Contingencies (10%) Bill No 7A |  |  |  | 0
| Taxes (VAT @16%) Bill No 7A |  |  |  | 0
| Total Bill No 7A |  |  |  | 0
Bill 7B | Electromechanical - OPTION B Mains electric powered |  |  |  | 0
Bidder shall supply all the information and rates for both Alternatives for the offer to be considered. Final decision on the main power source (Option A ZESCO mains power from institutions incoming distribution board, or Option B from Solar Array will be confirmed during negotiation prior to award.
proposed submersible hybrid DC/AC pumpset manufacturer and agent:
proposed standby generator manufacturer and agent:
| confirm manufactures brochures included with bid |  | yes / no
No change from these manufacturers or agents shall be permitted without prior written approval from the Consultant
Submersible 48 VDC Borehole Pump
7.1 | Supply and install a hybrid DC/AC borehole submersible pump suitable for a borehole of ID 5" capable of being powered from either a 48 VDC or a nominal 230 VAC source c/w cabled connection to power sources located within 10 m of borehole head, pumping into an overhead tank with top water inlet 14 m above ground.. . |  | nr | 1
Information provided to guide Bidder
| Ground elevation at borehole (approximate) | masl | 958
| Yield | m3/hr | 0.65
| Pump installation level below ground surface | m | 40
| Riser pipe diameter | mm | DN 50
| Dynamic water level below ground surface | m | 27.06
| Top water level in overhead tank | masl | 973
Information to be provided by Bidder
| Manufacturers Pump reference No. | ref.
| Maximum flow at Installation indicated above | m3/hr
| Maximum pump head at installation indicated above | m3/hr
| Optimum flow at Installation indicated above | m3/hr
| Optimum head at Installation indicated above | m3/hr
| Pump efficiency at installation | %
| Input power required by pump | W
| Output power required by solar array | W
| No. of solar panels and arrays offered and guaranteed to meet requirement | nr
7.2 | Solar arrays to be included in Option A
Supply and Installation of 220 VAC standby generator of rated power
7.3 | Supply, Install and connect by manually operated changeover switch standby generator capable of providing the VAC power required to operate the submersible borehole pump as specified above at half-load c/w roofed lockable waterproof steel protection cabinet. | nr | 1 |  | 0
Information to be provided by Bidder
Manufacturers Generator Set reference No.
| Output kVA at 1500rpm, 220V, single-phase, 50Hz, with power factor of 1.0 | kVA
| Fuel type (petrol/diesel) | type
| Fuel tank capacity | l
Air or water cooled
External 230 VAC Power Source
7.4 | Underground armoured cable c/w all internal building works, and making good, outside excavation, backfilling and protective concrete cover slabs from Main Distribution Board |  | 0
7.4.1 | All ancilliary work excludng outside excavation, and backfilling, supply and installation of underground armoured cable and protective concrete cover slabs | nr | 1 |  | 0
7.4.2 | External excavation, and backfilling, supply and installation of underground armoured cable and protective concrete cover slabs, minimum cover to cable 600 mm. Length subject to reconfirmation prior to award. | m | 115 |  | 0
| Sub-total Bill No 7B |  |  |  | 0
| Contingencies (10%) Bill No 7B |  |  |  | 0
| Taxes (VAT @16%) Bill No 7B |  |  |  | 0
| Total Bill No 7B |  |  |  | 0

## Kenani Pr Sch
UNICEF
Solar Powered Borehole Schemes in institutions in Nchelenge (Mantapala) Refugee Camp & Host Communities
Kenani Primary School
Bill No. SCH7
Item | Description | Unit | Qty | Rate (ZMW) | Amount (ZMW)
Bill No. out, Demolition and Site Clearance |  |  |  |  | 0
1.1 | In collaboration with the Inspector of Works, and based upon pipe lengths and alignment shown on layout plan, agree upon final alignment of pipelines, road crossings, location of all tees, bends, isolating valves, air valves, washouts, tapstands, and consumer connection offtakes. Set out pipeline centre-lines, survey, agree upon Starting Surfaces, and final lengths and produce final plans at horizontal scale of 1:200 for approval before proceeding further. | LS | 1 |  | 0
1.2 | General Clearance for urban land & rough grass land along pipeline wayleaves (trench width plus 0.5 m on either side) | ha | 0.1 |  | 0
1.3 | Removal of tree stumps within approved alignment. PROVISIONAL SUM | nr | 1 |  | 0
1.4 | Cut down and remove trees and tree stumps within approved alignment only if specifically directed to do so by Inspector of Works following agreement from the Host Community PROVISIONAL SUM | nr | 1 |  | 0
Bill No. 2: Excavation and backfilling of trenches - all pipelines |  |  |  |  | 0
2.1 | Excavate test pits along centre line of proposed pipeline to depth of 1m at least every 50 m | nr | 6 |  | 0
2.2 | Excavate and trim trench bed to depth not exceeding 1 m to ensure minimum cover provided to pipeline is not less than 600 mm | m | 260.1 |  | 0
2.3 | E. O. item 2.2 at road crossings. Excavate and trim trench to additional depth not exceeding 1.5 m to ensure minimum cover provided to the pipeline is 900 mm | m | 28.9 |  | 0
2.4 | Over excavate trench by a further depth of 150mm in areas identified by the Inspector of Works as requiring imported granular backfill RATE ONLY | m3 | 2.601 |  | 0
2.5 | Import, place and compact granular backfill in areas identified by the Inspector of Works as requiring imported granular backfill. RATE ONLY, | m3 | 2.601 |  | 0
2.6 | Place and compact sidefill and backfill using selected excavated material free of stones and tree roots to depth 300 mm above crown of pipe, and after compaction, other excavated material thereafter to final surface | m | 260.1 |  | 0
2.7 | Dispose of all surplus excavated material off-site as directed | LS | 1 |  | 0
Bill No. 3: Supply and Installation of rising main- borehole to elevated water tank |  |  |  |  | 0
All PE compression joints and fittings shall be supplied complete with suitable pipe joint stiffeners. All steel fittings shall be epoxy coated and all nuts and bolts galvanised. Rate shall include supply, lay, bed, joint , pressure test, sterilize and flushing of HDPE pipelines
3.1 | Raw water rising main from borehole to the Elevated Tank , HDPE DN50 (OD 63), SDR17, PN 10 | m | 14 |  | 0
3.2 | Gate Valve, double flange, handwheel operated 50 mm non-rising spindle type, with 1 No. flanged restraining adapters st. fl. to PE DN 50, installed above ground within tank inlet riser pipe | set | 1 |  | 0
3.3 | Supply and Installation of DN 40 parallel bulk water meter with magnetic transmission and dry recording head , metrological class B, minimum display 1 m3/hr to specification, suitable for vertical mounting, within water tank inlet riser pipe complete with strainer (metallic double flanged body c/w lockable meter box pipe surround). The meter assembly shall comprise: 1 No. DN50 to DN40 reducer, 1 DN40 500mm long straight pipe length, 1 DN 40 mm double flanged vertically mounted parallel bulk type meter, located approximately 1.5 m above ground level, 1 DN 40 250 mm straight pipe length, and one DN40 to DN50 reducer. | set | 1 |  | 0
| Carry forward |  |  |  | 0
| Brought forward |  |  |  | 0
Bill No. 4: Tanks, Tankstands and Tap Stands |  |  |  |  | 0
Bidder shall supply outline details of water tank stand and tank c/w, pipework and fittings.
water tank stand manufacturer:
HDPE cylindrical tank manufacturer:
HDPE cylindrical tank supplier (if different):
Contractor shall supply full set of structural calculations and drawings for water tank stand certified by a registered structural engineer for written approval prior to fabrication.
4.1 | Conduct geotechnical investigations and design foundation and tank stand for the elevated tank | LS | 1 |  | 0
4.2 | Tank reinforced concrete foundations 1 m x 1m x 1.5 m deep inc. excavation, shuttering, concreting, curing, backfilling and disposal of excess spoil material from site | nr | 6 |  | 0
Supply and install 2 No. HDPE cylindrical tank on Contractor designed six vertical members) mild steel tankstand c/w with inlet float valves, all inflow, valved connecting, outflow, overflow, and scour (washout) pipework, fittings, adaptors and 6m high steel stand c/w access ladder and lightning arrestor.
4.3 | Capacity 15m3. (2 no. 7.5 m3 tanks) | nr | 1 |  | 0
4.4 | Supply and paint all mild steel in tank stand with two coats of zinc 82% rich paint in dry film | LS | 1 |  | 0
4.5 | Leak testing and disinfection of tank and pipework | nr | 1 |  | 0
4.6 | Provide & install float level indicator gauge on side of tank readable from ground level adjacent to tank | nr | 1 |  | 0
4.7 | Provide and install chlorine cartridge type inline doser in lockable chamber at start of tank outlet pipe c/w twelve months supply of chlorine cartridges. | LS | 1 |  | 0
4.8 | Provide materials for and construct tap stand and associated drainage | nr | 3 |  | 0
Bill No. 5: Supply and Install Water Distribution Network |  |  |  |  | 0
All PE compression joints and fittings shall be supplied complete with suitable pipe joint stiffeners. All steel fittings shall be epoxy coated and all nuts and bolts galvanised. Rate shall include supply, lay, bed, joint , pressure test, sterilize and flushing of HDPE pipelines
5.1 | Network reticulation pipework HDPE DN50 (OD 63), SDR17, PN 10 | m | 165 |  | 0
5.2 | Equal tee compression fitting DN 50 x 50 x 50 mm | nr | 2 |  | 0
5.3 | Compression reducer coupling 50mm x 40mm | nr | 3 |  | 0
5.4 | Network reticulation pipework HDPE DN 40mm, SDR17, PN 10 | m | 146 |  | 0
5.5 | Compression fitting, elbow 90o DN 50mm | nr | 2 |  | 0
5.6 | Compression fitting, elbow 90o DN 40mm | nr | 1 |  | 0
5.7 | End cap DN 32mm (compression type) | nr | 3 |  | 0
5.8 | Supply and install GI pipes 25mm dia c/w fittings to tap stands c/w isolating stop cock | nr | 3 |  | 0
5.9 | Supply and install heavy weight brass garden bib tap (non-lever arm type) | nr | 6 |  | 0
5.1 | Compression tee DN 40 x 40 x 1" male branch to connect to tap stand pipework | nr | 3 |  | 0
5.11 | Gate Valve, double flange, 40 mm non-rising spindle type, with 2 No. flanged restraining adapters st. fl. to PE DN 40, complete with valve riser and valve box to suit | nr | 1 |  | 0
Air valve assembly consisting of 1 No. compression tee with threaded male 1 1/2" branch vertically upwards, 1 No. female to male thr. spigot, 1 No. Stopcock, thr. dble. socket 1", and 1 No. Single air valve, thr. female 1". RATE ONLY
5.15.1 | Compression tee DN 50 x 50 x 1 1/2" male br., 1 No. female to male 1 1/2" to 1" thr. spigot | set | 0
5.15.2 | Compression tee DN 40 x 40 x 1 1/2" male br., 1 No. female to male 1 1/2" to 1" thr. Spigot | set | 0
| Carry forward |  |  |  | 0
| Brought forward |  |  |  | 0
Bill No. 6: Concrete Works to all Pipelines |  |  |  |  | 0
All unreinforced concrete works shall be in medium strength concrete unless otherwise indicated. Where bends less than 45o are obtained by bending the pipe, radius not less than 35 x pipe diameter, and provided there is no compression joint with 5 metres of either end of radius, no separate thrust block is required.
6.1 | Over excavate in trench bed at all gate valves, air valve assemblies and steel fittings and cast support slab to full width of trench with other dimensions being the length of the valve or the fitting between flanges or between the compression tightening nuts and depth below trench bed of 150 mm | nr | 1 |  | 0
6.2 | At all 45o and 90o bends, pipeline tees, and end caps, provide and subsequently remove shuttering and cast thrust blocks against undisturbed trench bed and trench wall | nr | 5 |  | 0
6.3 | Supply all materials and cast and complete air-valve chamber. RATE ONLY | nr | 1 |  | 0
| Sub-total Bill Nos 1 to 6 |  |  |  | 0
| Contingencies (10%) Bills No 1 to 6 |  |  |  | 0
| Taxes (VAT @16%) Bills Nos 1 to 6 |  |  |  | 0
| Total Bills Nos 1 to 6 |  |  |  | 0
Bill 7A | Electromechanical - OPTION A Solar Powered |  |  |  | 0
Bidder shall supply all the information and rates for both Alternatives for the offer to be considered. Final decision on the main power source (Option A ZESCO mains power from institutions incoming distribution board, or Option B from Solar Array will be confirmed during negotiation prior to award.
proposed submersible hybrid DC/AC pumpset manufacturer and agent:
proposed standby generator manufacturer and agent:
| confirm manufactures brochures included with bid |  | yes / no
No change from these manufacturers or agents shall be permitted without prior written approval from the Consultant
Submersible Borehole Pump
7.1 | Supply and install a hybrid DC/AC borehole submersible pump suitable for a borehole of ID 5" capable of being powered from either a 48 VDC or a nominal 230 VAC source c/w cabled connection to power sources located within 10 m of borehole head, pumping into an overhead tank with top water inlet 14 m above ground.. . |  | nr | 1
Information provided to guide Bidder
| Ground elevation at borehole (approximate) | masl | 950
| Yield | m3/hr | 1.5
| Pump installation level below ground surface | m | tbc
| Riser pipe diameter | mm | DN 50
| Dynamic water level below ground surface | m | tbc
| Top water level in overhead tank | masl | 964
Information to be provided by Bidder
| Manufacturers Pump reference No. | ref.
| Maximum flow at Installation indicated above | m3/hr
| Maximum pump head at installation indicated above | m3/hr
| Optimum flow at Installation indicated above | m3/hr
| Optimum head at Installation indicated above | m3/hr
| Pump efficiency at installation | %
| Input power required by pump | W
| Output power required by solar array | W
| No. of solar panels and arrays offered and guaranteed to meet requirement | nr
7.2 | Solar arrays to meet requirements c/w security fence and gate and lightning protection as per Drawing to be included in this Option
7.2.1 | Supply, install, erect and connect solar arrays to meet requirements c/w lightning protection as per Drawing and Specification | nr | 1 |  | 0
7.2.2 | Provide all materials and construct fenced and gated compound to contain solar array and associated chambers to Specification. | LS | 1 |  | 0
7.2.3 | Supply and install DN 25 water pipe take-off from rising mainand sgtandpipe for solar cleansing system | LS | 1 |  | 0
7.2.4 | Provide solar array cleansing step ladder and extendable washer to Specification | LS | 1 |  | 0
Supply and Installation of 220 VAC standby generator of rated power
7.3 | Supply, Install and connect by manually operated changeover switch standby generator capable of providing the VAC power required to operate the submersible borehole pump as specified above at half-load c/w roofed lockable waterproof steel protection cabinet. | nr | 1 |  | 0
Information to be provided by Bidder
Manufacturers Generator Set reference No.
| Output kVA at 1500rpm, 220V, single-phase, 50Hz, with power factor of 1.0 | kVA
| Fuel type (petrol/diesel) and fuel tank capacity (l) | type
Air or water cooled
7.4 | External 230 VAC Power Source to be included in Option B
| Sub-total Bill No 7A |  |  |  | 0
| Contingencies (10%) Bill No 7A |  |  |  | 0
| Taxes (VAT @16%) Bill No 7A |  |  |  | 0
| Total Bill No 7A |  |  |  | 0
Bill 7B | Electromechanical - OPTION B Mains electric powered |  |  |  | 0
Bidder shall supply all the information and rates for both Alternatives for the offer to be considered. Final decision on the main power source (Option A ZESCO mains power from institutions incoming distribution board, or Option B from Solar Array will be confirmed during negotiation prior to award.
proposed submersible hybrid DC/AC pumpset manufacturer and agent:
proposed standby generator manufacturer and agent:
| confirm manufactures brochures included with bid |  | yes / no
No change from these manufacturers or agents shall be permitted without prior written approval from the Consultant
Submersible Borehole Pump
7.1 | Supply and install a hybrid DC/AC borehole submersible pump suitable for a borehole of ID 5" capable of being powered from either a 48 VDC or a nominal 230 VAC source c/w cabled connection to power sources located within 10 m of borehole head, pumping into an overhead tank with top water inlet 14 m above ground.. . |  | nr | 1
Information provided to guide Bidder
| Ground elevation at borehole (approximate) | masl | 950
| Yield | m3/hr | 1.5
| Pump installation level below ground surface | m | tbc
| Riser pipe diameter | mm | DN 50
| Dynamic water level below ground surface | m | tbc
| Top water level in overhead tank | masl | 964
Information to be provided by Bidder
| Manufacturers Pump reference No. | ref.
| Maximum flow at Installation indicated above | m3/hr
| Maximum pump head at installation indicated above | m3/hr
| Optimum flow at Installation indicated above | m3/hr
| Optimum head at Installation indicated above | m3/hr
| Pump efficiency at installation | %
| Input power required by pump | W
| Output power required by solar array | W
| No. of solar panels and arrays offered and guaranteed to meet requirement | nr
7.2 | Solar arrays to be included in Option A
Supply and Installation of 220 VAC standby generator of rated power
7.3 | Supply, Install and connect by manually operated changeover switch standby generator capable of providing the VAC power required to operate the submersible borehole pump as specified above at half-load c/w roofed lockable waterproof steel protection cabinet. | nr | 1 |  | 0
Information to be provided by Bidder
Manufacturers Generator Set reference No.
| Output kVA at 1500rpm, 220V, single-phase, 50Hz, with power factor of 1.0 | kVA
| Fuel type (petrol/diesel) and fuel tank capacity (l) | type
Air or water cooled
External 230 VAC Power Source
7.4 | Underground armoured cable c/w all internal building works, and making good, outside excavation, backfilling and protective concrete cover slabs from Main Distribution Board |  | 0
7.4.1 | All ancilliary work excludng outside excavation, and backfilling, supply and installation of underground armoured cable and protective concrete cover slabs | nr | 1 |  | 0
7.4.2 | External excavation, and backfilling, supply and installation of underground armoured cable and protective concrete cover slabs, minimum cover to cable 600 mm. Length subject to reconfirmation prior to award. | m | 146 |  | 0
| Sub-total Bill No 7B |  |  |  | 0
| Contingencies (10%) Bill No 7B |  |  |  | 0
| Taxes (VAT @16%) Bill No 7B |  |  |  | 0
| Total Bill No 7B |  |  |  | 0

## Kambwali RHC
UNICEF
Solar Powered Borehole Schemes in institutions in Nchelenge (Mantapala) Refugee Camp & Host Communities
Kambwali RHC
Bill No. HC1:
Item | Description | Unit | Qty | Rate (ZMW) | Amount (ZMW)
Bill No. out, Demolition and Site Clearance |  |  |  |  | 0
1.1 | In collaboration with the Inspector of Works, and based upon pipe lengths and alignment shown on layout plan, agree upon final alignment of pipelines, road crossings, location of all tees, bends, isolating valves, air valves, washouts, tapstands, and consumer connection offtakes. Set out pipeline centre-lines, survey, agree upon Starting Surfaces, and final lengths and produce final plans at horizontal scale of 1:200 for approval before proceeding further. | LS | 1 |  | 0
1.2 | General Clearance for urban land & rough grass land along pipeline wayleaves (trench width plus 0.5 m on either side) | ha | 0.1 |  | 0
1.3 | Removal of tree stumps within approved alignment. PROVISIONAL SUM | nr | 1 |  | 0
1.4 | Cut down and remove trees and tree stumps within approved alignment only if specifically directed to do so by Inspector of Works following agreement from the Host Community PROVISIONAL SUM | nr | 1 |  | 0
Bill No. 2: Excavation and backfilling of trenches - all pipelines |  |  |  |  | 0
2.1 | Excavate test pits along centre line of proposed pipeline to depth of 1m at least every 50 m | nr | 4 |  | 0
2.2 | Excavate and trim trench bed to depth not exceeding 1 m to ensure minimum cover provided to pipeline is not less than 600 mm | m | 158.4 |  | 0
2.3 | E. O. item 2.2 at road crossings. Excavate and trim trench to additional depth not exceeding 1.5 m to ensure minimum cover provided to the pipeline is 900 mm | m | 17.6 |  | 0
2.4 | Over excavate trench by a further depth of 150mm in areas identified by the Inspector of Works as requiring imported granular backfill RATE ONLY | m3 | 1.584 |  | 0
2.5 | Import, place and compact granular backfill in areas identified by the Inspector of Works as requiring imported granular backfill. RATE ONLY, | m3 | 1.584 |  | 0
2.6 | Place and compact sidefill and backfill using selected excavated material free of stones and tree roots to depth 300 mm above crown of pipe, and after compaction, other excavated material thereafter to final surface | m | 158.4 |  | 0
2.7 | Dispose of all surplus excavated material off-site as directed | LS | 1 |  | 0
Bill No. 3: Supply and Installation of rising main- borehole to elevated water tank |  |  |  |  | 0
All PE compression joints and fittings shall be supplied complete with suitable pipe joint stiffeners. All steel fittings shall be epoxy coated and all nuts and bolts galvanised. Rate shall include supply, lay, bed, joint , pressure test, sterilize and flushing of HDPE pipelines
3.1 | Raw water rising main from borehole to the Elevated Tank , HDPE DN50 (OD 63), SDR17, PN 10 | m | 86 |  | 0
3.2 | Compression fitting, elbow 90o DN 50mm | nr | 2
3.3 | Gate Valve, double flange, handwheel operated 50 mm non-rising spindle type, with 1 No. flanged restraining adapters st. fl. to PE DN 50, installed above ground within tank inlet riser pipe | set | 1 |  | 0
3.4 | Supply and Installation of DN 40 parallel bulk water meter with magnetic transmission and dry recording head , metrological class B, minimum display 1 m3/hr to specification, suitable for vertical mounting, within water tank inlet riser pipe complete with strainer (metallic double flanged body c/w lockable meter box pipe surround). The meter assembly shall comprise: 1 No. DN50 to DN40 reducer, 1 DN40 500mm long straight pipe length, 1 DN 40 mm double flanged vertically mounted parallel bulk type meter, located approximately 1.5 m above ground level, 1 DN 40 250 mm straight pipe length, and one DN40 to DN50 reducer. | set | 1 |  | 0
| Carry forward |  |  |  | 0
| Brought forward |  |  |  | 0
Bill No. 4: Tanks, Tankstands and Tap Stands |  |  |  |  | 0
Bidder shall supply outline details of water tank stand and tank c/w, pipework and fittings.
water tank stand manufacturer:
HDPE cylindrical tank manufacturer:
HDPE cylindrical tank supplier (if different):
Contractor shall supply full set of structural calculations and drawings for water tank stand certified by a registered structural engineer for written approval prior to fabrication.
4.1 | Conduct geotechnical investigations and design foundation and tank stand for the elevated tank | LS | 1 |  | 0
4.2 | Tank reinforced concrete foundations 1 m x 1m x 1.5 m deep inc. excavation, shuttering, concreting, curing, backfilling and disposal of excess spoil material from site | nr | 6 |  | 0
Supply and install 2 No. HDPE cylindrical tank on Contractor designed six vertical members) mild steel tankstand c/w with inlet float valves, all inflow, valved connecting, outflow, overflow, and scour (washout) pipework, fittings, adaptors and 6m high steel stand c/w access ladder and lightning arrestor.
4.3 | Capacity 10m3.(2 no. 5m3 tanks) | nr | 1 |  | 0
4.4 | Supply and paint all mild steel in tank stand with two coats of zinc 82% rich paint in dry film | LS | 1 |  | 0
4.5 | Leak testing and disinfection of tank and pipework | nr | 1 |  | 0
4.6 | Provide & install float level indicator gauge on side of tank readable from ground level adjacent to tank | nr | 1 |  | 0
4.7 | Provide and install chlorine cartridge type inline doser in lockable chamber at start of tank outlet pipe c/w twelve months supply of chlorine cartridges. | LS | 1 |  | 0
4.8 | Provide materials for and construct tap stand and associated drainage | nr | 3 |  | 0
Bill No. 5: Supply and Install Water Distribution Network |  |  |  |  | 0
All PE compression joints and fittings shall be supplied complete with suitable pipe joint stiffeners. All steel fittings shall be epoxy coated and all nuts and bolts galvanised. Rate shall include supply, lay, bed, joint , pressure test, sterilize and flushing of HDPE pipelines
5.1 | Equal tee compression fitting DN 40 x 40 x 40 mm | nr | 1 |  | 0
5.2 | Unequal reducing tee compression fitting DN 40 x 40 x 32 mm | nr | 1 |  | 0
5.3 | Network reticulation pipework HDPE DN 40mm, SDR17, PN 10 | m | 73 |  | 0
5.4 | Network reticulation pipework HDPE DN 32mm, SDR17, PN 10 | m | 17 |  | 0
5.5 | Compression fitting, elbow 90o DN 40mm | nr | 1 |  | 0
5.6 | End cap DN 32mm (compression type) | nr | 2 |  | 0
5.7 | Saddle clamp 32mm x 3/4" to supply individual consumer connection | nr | 1 |  | 0
5.8 | Supply and install GI pipes 25mm dia c/w fittings to tap stands c/w isolating stop cock | nr | 3 |  | 0
5.9 | Supply and install heavy weight brass garden bib tap (non-lever arm type) | nr | 6 |  | 0
5.1 | Compression tee DN 32 x 32 x 1" male branch to connect to tap stand pipework | nr | 3 |  | 0
5.11 | Gate Valve, double flange, 40 mm non-rising spindle type, with 2 No. flanged restraining adapters st. fl. to PE DN 40, complete with valve riser and valve box to suit | nr | 2 |  | 0
5.12 | Allow for internal plumbing from pipeline to ablution facilities. Prime Cost | sum | 1 | 20000 | 20000
Air valve assembly consisting of 1 No. compression tee with threaded male 1 1/2" branch vertically upwards, 1 No. female to male thr. spigot, 1 No. Stopcock, thr. dble. socket 1", and 1 No. Single air valve, thr. female 1". RATE ONLY
5.13 | Compression tee DN 40 x 40 x 1 1/2" male br., 1 No. female to male 1 1/2" to 1" thr. Spigot | set | 0
| Carry forward |  |  |  | 0
| Brought forward |  |  |  | 0
Bill No. 6: Concrete Works to all Pipelines |  |  |  |  | 0
All unreinforced concrete works shall be in medium strength concrete unless otherwise indicated. Where bends less than 45o are obtained by bending the pipe, radius not less than 35 x pipe diameter, and provided theere is no compression joint with 5 metres of either end of radius, no separate thrust block is required.
6.1 | Over excavate in trench bed at all gate valves, air valve assemblies and steel fittings and cast support slab to full width of trench with other dimensions being the length of the valve or the fitting between flanges or between the compression tightening nuts and depth below trench bed of 150 mm | nr | 2 |  | 0
6.2 | At all 45o and 90o bends and pipeline tees, and end caps, provide and subsequently remove shuttering and cast thrust blocks against undisturbed trench bed and trench wall | nr | 8 |  | 0
6.3 | Supply all materials and cast and complete air-valve chamber. RATE ONLY | nr | 1
| Sub-total Bill Nos 1 to 6 |  |  |  | 0
| Contingencies (10%) Bills No 1 to 6 |  |  |  | 0
| Taxes (VAT @16%) Bills Nos 1 to 6 |  |  |  | 0
| Total Bills Nos 1 to 6 |  |  |  | 0
Bill 7A | Electromechanical - OPTION A Solar Powered |  |  |  | 0
Bidder shall supply all the information and rates for both Alternatives for the offer to be considered. Final decision on the main power source (Option A ZESCO mains power from institutions incoming distribution board, or Option B from Solar Array will be confirmed during negotiation prior to award.
proposed submersible hybrid DC/AC pumpset manufacturer and agent:
proposed standby generator manufacturer and agent:
| confirm manufactures brochures included with bid |  | yes / no
No change from these manufacturers or agents shall be permitted without prior written approval from the Consultant
Submersible 48 VDC Borehole Pump
7.1 | Supply and install a hybrid DC/AC borehole submersible pump suitable for a borehole of ID 5" capable of being powered from either a 48 VDC or a nominal 230 VAC source c/w cabled connection to power sources located within 10 m of borehole head, pumping into an overhead tank with top water inlet 14 m above ground.. . |  | nr | 1
Information provided to guide Bidder
| Ground elevation at borehole (approximate) | masl | 955
| Yield | m3/hr | 2.8
| Pump installation level below ground surface | m | 44
| Riser pipe diameter | mm | DN 50
| Dynamic water level below ground surface | m | 32.18
| Top water level in overhead tank | masl | 970
Information to be provided by Bidder
| Manufacturers Pump reference No. | ref.
| Maximum flow at Installation indicated above | m3/hr
| Maximum pump head at installation indicated above | m3/hr
| Optimum flow at Installation indicated above | m3/hr
| Optimum head at Installation indicated above | m3/hr
| Pump efficiency at installation | %
| Input power required by pump | W
| Output power required by solar array | W
| No. of solar panels and arrays offered and guaranteed to meet requirement | nr
7.2 | Solar arrays to meet requirements c/w security fence and gate and lightning protection as per Drawing to be included in this Option
7.2.1 | Supply, install, erect and connect solar arrays to meet requirements c/w lightning protection as per Drawing and Specification | nr | 1 |  | 0
7.2.2 | Provide all materials and construct fenced and gated compound to contain solar array and associated chambers to Specification. | LS | 1 |  | 0
7.2.3 | Supply and install DN 25 water pipe take-off from rising mainand sgtandpipe for solar cleansing system | LS | 1 |  | 0
7.2.4 | Provide solar array cleansing step ladder and extendable washer to Specification | LS | 1 |  | 0
Supply and Installation of 220 VAC standby generator of rated power
7.3 | Supply, Install and connect by manually operated changeover switch standby generator capable of providing the VAC power required to operate the submersible borehole pump as specified above at half-load c/w roofed lockable waterproof steel protection cabinet. | nr | 1 |  | 0
Information to be provided by Bidder
Manufacturers Generator Set reference No.
| Output kVA at 1500rpm, 220V, single-phase, 50Hz, with power factor of 1.0 | kVA
| Fuel type (petrol/diesel) | type
| Fuel tank capacity | l
Air or water cooled
7.4 | External 230 VAC Power Source to be included in Option B
| Sub-total Bill No 7A |  |  |  | 0
| Contingencies (10%) Bill No 7A |  |  |  | 0
| Taxes (VAT @16%) Bill No 7A |  |  |  | 0
| Total Bill No 7A |  |  |  | 0
Bill 7B | Electromechanical - OPTION B Mains electric powered |  |  |  | 0
Bidder shall supply all the information and rates for both Alternatives for the offer to be considered. Final decision on the main power source (Option A ZESCO mains power from institutions incoming distribution board, or Option B from Solar Array will be confirmed during negotiation prior to award.
proposed submersible hybrid DC/AC pumpset manufacturer and agent:
proposed standby generator manufacturer and agent:
| confirm manufactures brochures included with bid |  | yes / no
No change from these manufacturers or agents shall be permitted without prior written approval from the Consultant
Submersible 48 VDC Borehole Pump
7.1 | Supply and install a hybrid DC/AC borehole submersible pump suitable for a borehole of ID 5" capable of being powered from either a 48 VDC or a nominal 230 VAC source c/w cabled connection to power sources located within 10 m of borehole head, pumping into an overhead tank with top water inlet 14 m above ground.. . |  | nr | 1
Information provided to guide Bidder
| Ground elevation at borehole (approximate) | masl | 955
| Yield | m3/hr | 2.8
| Pump installation level below ground surface | m | 44
| Riser pipe diameter | mm | DN 50
| Dynamic water level below ground surface | m | 32.18
| Top water level in overhead tank | masl | 970
Information to be provided by Bidder
| Manufacturers Pump reference No. | ref.
| Maximum flow at Installation indicated above | m3/hr
| Maximum pump head at installation indicated above | m3/hr
| Optimum flow at Installation indicated above | m3/hr
| Optimum head at Installation indicated above | m3/hr
| Pump efficiency at installation | %
| Input power required by pump | W
| Output power required by solar array | W
| No. of solar panels and arrays offered and guaranteed to meet requirement | nr
7.2 | Solar arrays to be included in Option A
7.2.1 | Supply, install, erect and connect solar arrays to meet requirements c/w lightning protection as per Drawing and Specification | nr | 1 |  | 0
7.2.2 | Provide all materials and construct fenced and gated compound to contain solar array and associated chambers to Specification. | LS | 1 |  | 0
7.2.3 | Supply and install DN 25 water pipe take-off from rising mainand sgtandpipe for solar cleansing system | LS | 1 |  | 0
7.2.4 | Provide solar array cleansing step ladder and extendable washer to Specification | LS | 1 |  | 0
Supply and Installation of 220 VAC standby generator of rated power
7.3 | Supply, Install and connect by manually operated changeover switch standby generator capable of providing the VAC power required to operate the submersible borehole pump as specified above at half-load c/w roofed lockable waterproof steel protection cabinet. | nr | 1 |  | 0
Information to be provided by Bidder
Manufacturers Generator Set reference No.
| Output kVA at 1500rpm, 220V, single-phase, 50Hz, with power factor of 1.0 | kVA
| Fuel type (petrol/diesel) | type
| Fuel tank capacity | l
Air or water cooled
External 230 VAC Power Source
7.4 | Underground armoured cable c/w all internal building works, and making good, outside excavation, backfilling and protective concrete cover slabs from Main Distribution Board |  | 0
7.4.1 | All ancilliary work excludng outside excavation, and backfilling, supply and installation of underground armoured cable and protective concrete cover slabs | nr | 1 |  | 0
7.4.2 | External excavation, and backfilling, supply and installation of underground armoured cable and protective concrete cover slabs, minimum cover to cable 600 mm. Length subject to reconfirmation prior to award. | m | 95 |  | 0
| Sub-total Bill No 7B |  |  |  | 0
| Contingencies (10%) Bill No 7B |  |  |  | 0
| Taxes (VAT @16%) Bill No 7B |  |  |  | 0
| Total Bill No 7B |  |  |  | 0

## Kafutuma RHC
UNICEF
Solar Powered Borehole Schemes in institutions in Nchelenge (Mantapala) Refugee Camp & Host Communities
Kafutuma RHC
Bill No. HC2:
Item | Description | Unit | Qty | Rate (ZMW) | Amount (ZMW)
Bill No. out, Demolition and Site Clearance |  |  |  |  | 0
1.1 | In collaboration with the Inspector of Works, and based upon pipe lengths and alignment shown on layout plan, agree upon final alignment of pipelines, road crossings, location of all tees, bends, isolating valves, air valves, washouts, tapstands, and consumer connection offtakes. Set out pipeline centre-lines, survey, agree upon Starting Surfaces, and final lengths and produce final plans at horizontal scale of 1:200 for approval before proceeding further. | LS | 1 |  | 0
1.2 | General Clearance for urban land & rough grass land along pipeline wayleaves (trench width plus 0.5 m on either side) | ha | 0.1 |  | 0
1.3 | Removal of tree stumps within approved alignment. PROVISIONAL SUM | nr | 1 |  | 0
1.4 | Cut down and remove trees and tree stumps within approved alignment only if specifically directed to do so by Inspector of Works following agreement from the Host Community PROVISIONAL SUM | nr | 1 |  | 0
Bill No. 2: Excavation and backfilling of trenches - all pipelines |  |  |  |  | 0
2.1 | Excavate test pits along centre line of proposed pipeline to depth of 1m at least every 50 m | nr | 4 |  | 0
2.2 | Excavate and trim trench bed to depth not exceeding 1 m to ensure minimum cover provided to pipeline is not less than 600 mm | m | 157.5 |  | 0
2.3 | E. O. item 2.2 at road crossings. Excavate and trim trench to additional depth not exceeding 1.5 m to ensure minimum cover provided to the pipeline is 900 mm | m | 17.5 |  | 0
2.4 | Over excavate trench by a further depth of 150mm in areas identified by the Inspector of Works as requiring imported granular backfill RATE ONLY | m3 | 1.575 |  | 0
2.5 | Import, place and compact granular backfill in areas identified by the Inspector of Works as requiring imported granular backfill. RATE ONLY, | m3 | 1.575 |  | 0
2.6 | Place and compact sidefill and backfill using selected excavated material free of stones and tree roots to depth 300 mm above crown of pipe, and after compaction, other excavated material thereafter to final surface | m | 157.5 |  | 0
2.7 | Dispose of all surplus excavated material off-site as directed | LS | 1 |  | 0
Bill No. 3: Supply and Installation of rising main- borehole to elevated water tank |  |  |  |  | 0
All PE compression joints and fittings shall be supplied complete with suitable pipe joint stiffeners. All steel fittings shall be epoxy coated and all nuts and bolts galvanised. Rate shall include supply, lay, bed, joint , pressure test, sterilize and flushing of HDPE pipelines
3.1 | Raw water rising main from borehole to the Elevated Tank , HDPE DN50 (OD 63), SDR17, PN 10 | m | 71 |  | 0
3.2 | Gate Valve, double flange, handwheel operated 50 mm non-rising spindle type, with 1 No. flanged restraining adapters st. fl. to PE DN 50, installed above ground within tank inlet riser pipe | set | 1 |  | 0
3.3 | Supply and Installation of DN 40 parallel bulk water meter with magnetic transmission and dry recording head , metrological class B, minimum display 1 m3/hr to specification, suitable for vertical mounting, within water tank inlet riser pipe complete with strainer (metallic double flanged body c/w lockable meter box pipe surround). The meter assembly shall comprise: 1 No. DN50 to DN40 reducer, 1 DN40 500mm long straight pipe length, 1 DN 40 mm double flanged vertically mounted parallel bulk type meter, located approximately 1.5 m above ground level, 1 DN 40 250 mm straight pipe length, and one DN40 to DN50 reducer. | set | 1 |  | 0
| Carry forward |  |  |  | 0
| Brought forward |  |  |  | 0
Bill No. 4: Tanks, Tankstands and Tap Stands |  |  |  |  | 0
Bidder shall supply outline details of water tank stand and tank c/w, pipework and fittings.
water tank stand manufacturer:
HDPE cylindrical tank manufacturer:
HDPE cylindrical tank supplier (if different):
Contractor shall supply full set of structural calculations and drawings for water tank stand certified by a registered structural engineer for written approval prior to fabrication.
4.1 | Conduct geotechnical investigations and design foundation and tank stand for the elevated tank | LS | 1 |  | 0
4.2 | Tank reinforced concrete foundations 1 m x 1m x 1.5 m deep inc. excavation, shuttering, concreting, curing, backfilling and disposal of excess spoil material from site | nr | 6 |  | 0
Supply and install 2 No. HDPE cylindrical tank on Contractor designed six vertical members) mild steel tankstand c/w with inlet float valves, all inflow, valved connecting, outflow, overflow, and scour (washout) pipework, fittings, adaptors and 6m high steel stand c/w access ladder and lightning arrestor.
4.3 | Capacity 10m3.(2 no. 5m3 tanks) | nr | 1 |  | 0
4.4 | Supply and paint all mild steel in tank stand with two coats of zinc 82% rich paint in dry film | LS | 1 |  | 0
4.5 | Leak testing and disinfection of tank and pipework | nr | 1 |  | 0
4.6 | Provide & install float level indicator gauge on side of tank readable from ground level adjacent to tank | nr | 1 |  | 0
4.7 | Provide and install chlorine cartridge type inline doser in lockable chamber at start of tank outlet pipe c/w twelve months supply of chlorine cartridges. | LS | 1 |  | 0
4.8 | Provide materials for and construct tap stand and associated drainage | nr | 3 |  | 0
Bill No. 5: Supply and Install Water Distribution Network |  |  |  |  | 0
All PE compression joints and fittings shall be supplied complete with suitable pipe joint stiffeners. All steel fittings shall be epoxy coated and all nuts and bolts galvanised. Rate shall include supply, lay, bed, joint , pressure test, sterilize and flushing of HDPE pipelines
5.1 | Network reticulation pipework HDPE DN50 (OD 63), SDR17, PN 10 | m | 31 |  | 0
5.2 | Equal tee compression fitting DN 50 x 50 x 50 mm | nr | 1 |  | 0
5.3 | Unequal reducing tee compression fitting DN 40 x 40 x 32 mm | nr | 1 |  | 0
5.4 | Compression reducer coupling 50mm x 40mm | nr | 3 |  | 0
5.5 | Compression reducer coupling 50mm x 32mm | nr | 1 |  | 0
5.6 | Compression reducer coupling 40mm x 32mm | nr | 1 |  | 0
5.7 | Network reticulation pipework HDPE DN 40mm, SDR17, PN 10 | m | 27 |  | 0
5.8 | Network reticulation pipework HDPE DN 32mm, SDR17, PN 10 | m | 46 |  | 0
5.9 | Compression fitting, elbow 45o DN 50mm | nr | 1 |  | 0
5.1 | Compression fitting, elbow 90o DN 50mm | nr | 1 |  | 0
5.11 | Supply and install GI pipes 25mm dia c/w fittings to tap stands c/w isolating stop cock | nr | 3 |  | 0
5.12 | Supply and install heavy weight brass garden bib tap (non-lever arm type) | nr | 6 |  | 0
5.13 | Compression tee DN 40 x 40 x 1" male branch to connect to tap stand pipework | nr | 1 |  | 0
5.14 | Compression tee DN 32 x 32 x 1" male branch to connect to tap stand pipework | nr | 2 |  | 0
5.15 | Gate Valve, double flange, 40 mm non-rising spindle type, with 2 No. flanged restraining adapters st. fl. to PE DN 40, complete with valve riser and valve box to suit | nr | 1 |  | 0
5.16 | Allow for internal plumbing from pipeline to ablution facilities. Prime Cost | sum | 1 | 20000 | 20000
Air valve assembly consisting of 1 No. compression tee with threaded male 1 1/2" branch vertically upwards, 1 No. female to male thr. spigot, 1 No. Stopcock, thr. dble. socket 1", and 1 No. Single air valve, thr. female 1". RATE ONLY
5.17.1 | Compression tee DN 50 x 50 x 1 1/2" male br., 1 No. female to male 1 1/2" to 1" thr. spigot | set | 0
5.17.2 | Compression tee DN 40 x 40 x 1 1/2" male br., 1 No. female to male 1 1/2" to 1" thr. Spigot | set | 0
5.17.3 | Compression tee DN 32 x 32 x 1" male br, 1 No. female to male 1" to 1" thr. spigot | set | 0
| Carry forward |  |  |  | 0
| Brought forward |  |  |  | 0
Bill No. 6: Concrete Works to all Pipelines |  |  |  |  | 0
All unreinforced concrete works shall be in medium strength concrete unless otherwise indicated. Where bends less than 45o are obtained by bending the pipe, radius not less than 35 x pipe diameter, and provided there is no compression joint with 5 metres of either end of radius, no separate thrust block is required.
6.1 | Over excavate in trench bed at all gate valves, air valve assemblies and steel fittings and cast support slab to full width of trench with other dimensions being the length of the valve or the fitting between flanges or between the compression tightening nuts and depth below trench bed of 150 mm | nr | 1 |  | 0
6.2 | At all 45o and 90o bends, pipeline tees, and end caps, provide and subsequently remove shuttering and cast thrust blocks against undisturbed trench bed and trench wall | nr | 6 |  | 0
6.3 | Supply all materials and cast and complete air-valve chamber. RATE ONLY | nr | 1
| Sub-total Bill Nos 1 to 6 |  |  |  | 0
| Contingencies (10%) Bills No 1 to 6 |  |  |  | 0
| Taxes (VAT @16%) Bills Nos 1 to 6 |  |  |  | 0
| Total Bills Nos 1 to 6 |  |  |  | 0
Bill 7A | Electromechanical - OPTION A Solar Powered |  |  |  | 0
Bidder shall supply all the information and rates for both Alternatives for the offer to be considered. Final decision on the main power source (Option A ZESCO mains power from institutions incoming distribution board, or Option B from Solar Array will be confirmed during negotiation prior to award.
proposed submersible hybrid DC/AC pumpset manufacturer and agent:
proposed standby generator manufacturer and agent:
| confirm manufactures brochures included with bid |  | yes / no
No change from these manufacturers or agents shall be permitted without prior written approval from the Consultant
Submersible 48 VDC Borehole Pump
7.1 | Supply and install a hybrid DC/AC borehole submersible pump suitable for a borehole of ID 5" capable of being powered from either a 48 VDC or a nominal 230 VAC source c/w cabled connection to power sources located within 10 m of borehole head, pumping into an overhead tank with top water inlet 14 m above ground.. . |  | nr | 1
Information provided to guide Bidder
| Ground elevation at borehole (approximate) | masl | 961
| Yield | m3/hr | 2.4
| Pump installation level below ground surface | m | 49
| Riser pipe diameter | mm | DN 50
| Dynamic water level below ground surface | m | 38.84
| Top water level in overhead tank | masl | 977
Information to be provided by Bidder
| Manufacturers Pump reference No. | ref.
| Maximum flow at Installation indicated above | m3/hr
| Maximum pump head at installation indicated above | m3/hr
| Optimum flow at Installation indicated above | m3/hr
| Optimum head at Installation indicated above | m3/hr
| Pump efficiency at installation | %
| Input power required by pump | W
| Output power required by solar array | W
| No. of solar panels and arrays offered and guaranteed to meet requirement | nr
7.2 | Solar arrays to meet requirements c/w security fence and gate and lightning protection as per Drawing to be included in this Option
7.2.1 | Supply, install, erect and connect solar arrays to meet requirements c/w lightning protection as per Drawing and Specification | nr | 1 |  | 0
7.2.2 | Provide all materials and construct fenced and gated compound to contain solar array and associated chambers to Specification. | LS | 1 |  | 0
7.2.3 | Supply and install DN 25 water pipe take-off from rising mainand sgtandpipe for solar cleansing system | LS | 1 |  | 0
7.2.4 | Provide solar array cleansing step ladder and extendable washer to Specification | LS | 1 |  | 0
Supply and Installation of 220 VAC standby generator of rated power
7.3 | Supply, Install and connect by manually operated changeover switch standby generator capable of providing the VAC power required to operate the submersible borehole pump as specified above at half-load c/w roofed lockable waterproof steel protection cabinet. | nr | 1 |  | 0
Information to be provided by Bidder
Manufacturers Generator Set reference No.
| Output kVA at 1500rpm, 220V, single-phase, 50Hz, with power factor of 1.0 | kVA
| Fuel type (petrol/diesel) | type
| Fuel tank capacity | l
Air or water cooled
7.4 | External 230 VAC Power Source to be included in Option B
| Sub-total Bill No 7A |  |  |  | 0
| Contingencies (10%) Bill No 7A |  |  |  | 0
| Taxes (VAT @16%) Bill No 7A |  |  |  | 0
| Total Bill No 7A |  |  |  | 0
Bill 7B | Electromechanical - OPTION B Mains electric powered |  |  |  | 0
Bidder shall supply all the information and rates for both Alternatives for the offer to be considered. Final decision on the main power source (Option A ZESCO mains power from institutions incoming distribution board, or Option B from Solar Array will be confirmed during negotiation prior to award.
proposed submersible hybrid DC/AC pumpset manufacturer and agent:
proposed standby generator manufacturer and agent:
| confirm manufactures brochures included with bid |  | yes / no
No change from these manufacturers or agents shall be permitted without prior written approval from the Consultant
Submersible 48 VDC Borehole Pump
7.1 | Supply and install a hybrid DC/AC borehole submersible pump suitable for a borehole of ID 5" capable of being powered from either a 48 VDC or a nominal 230 VAC source c/w cabled connection to power sources located within 10 m of borehole head, pumping into an overhead tank with top water inlet 14 m above ground.. . |  | nr | 1
Information provided to guide Bidder
| Ground elevation at borehole (approximate) | masl | 961
| Yield | m3/hr | 2.4
| Pump installation level below ground surface | m | 49
| Riser pipe diameter | mm | DN 50
| Dynamic water level below ground surface | m | 38.84
| Top water level in overhead tank | masl | 977
Information to be provided by Bidder
| Manufacturers Pump reference No. | ref.
| Maximum flow at Installation indicated above | m3/hr
| Maximum pump head at installation indicated above | m3/hr
| Optimum flow at Installation indicated above | m3/hr
| Optimum head at Installation indicated above | m3/hr
| Pump efficiency at installation | %
| Input power required by pump | W
| Output power required by solar array | W
| No. of solar panels and arrays offered and guaranteed to meet requirement | nr
7.2 | Solar arrays to be included in Option A
Supply and Installation of 220 VAC standby generator of rated power
7.3 | Supply, Install and connect by manually operated changeover switch standby generator capable of providing the VAC power required to operate the submersible borehole pump as specified above at half-load c/w roofed lockable waterproof steel protection cabinet. | nr | 1 |  | 0
Information to be provided by Bidder
Manufacturers Generator Set reference No.
| Output kVA at 1500rpm, 220V, single-phase, 50Hz, with power factor of 1.0 | kVA
| Fuel type (petrol/diesel) | type
| Fuel tank capacity | l
Air or water cooled
External 230 VAC Power Source
7.4 | Underground armoured cable c/w all internal building works, and making good, outside excavation, backfilling and protective concrete cover slabs from Main Distribution Board |  | 0
7.4.1 | All ancilliary work excludng outside excavation, and backfilling, supply and installation of underground armoured cable and protective concrete cover slabs | nr | 1 |  | 0
7.4.2 | External excavation, and backfilling, supply and installation of underground armoured cable and protective concrete cover slabs, minimum cover to cable 600 mm. Length subject to reconfirmation prior to award. | m | 80 |  | 0
| Sub-total Bill No 7B |  |  |  | 0
| Contingencies (10%) Bill No 7B |  |  |  | 0
| Taxes (VAT @16%) Bill No 7B |  |  |  | 0
| Total Bill No 7B |  |  |  | 0

## Chabilikila RHC
UNICEF
Solar Powered Borehole Schemes in institutions in Nchelenge (Mantapala) Refugee Camp & Host Communities
Chabilikila RHC
Bill No. HC3:
Item | Description | Unit | Qty | Rate (ZMW) | Amount (ZMW)
Bill No. out, Demolition and Site Clearance |  |  |  |  | 0
1.1 | In collaboration with the Inspector of Works, and based upon pipe lengths and alignment shown on layout plan, agree upon final alignment of pipelines, road crossings, location of all tees, bends, isolating valves, air valves, washouts, tapstands, and consumer connection offtakes. Set out pipeline centre-lines, survey, agree upon Starting Surfaces, and final lengths and produce final plans at horizontal scale of 1:200 for approval before proceeding further. | LS | 1 |  | 0
1.2 | General Clearance for urban land & rough grass land along pipeline wayleaves (trench width plus 0.5 m on either side) | ha | 0.1 |  | 0
1.3 | Removal of tree stumps within approved alignment. PROVISIONAL SUM | nr | 1 |  | 0
1.4 | Cut down and remove trees and tree stumps within approved alignment only if specifically directed to do so by Inspector of Works following agreement from the Host Community PROVISIONAL SUM | nr | 1 |  | 0
Bill No. 2: Excavation and backfilling of trenches - all pipelines |  |  |  |  | 0
2.1 | Excavate test pits along centre line of proposed pipeline to depth of 1m at least every 50 m | nr | 3 |  | 0
2.2 | Excavate and trim trench bed to depth not exceeding 1 m to ensure minimum cover provided to pipeline is not less than 600 mm | m | 99.9 |  | 0
2.3 | E. O. item 2.2 at road crossings. Excavate and trim trench to additional depth not exceeding 1.5 m to ensure minimum cover provided to the pipeline is 900 mm | m | 11.1 |  | 0
2.4 | Over excavate trench by a further depth of 150mm in areas identified by the Inspector of Works as requiring imported granular backfill RATE ONLY | m3 | 0.999 |  | 0
2.5 | Import, place and compact granular backfill in areas identified by the Inspector of Works as requiring imported granular backfill. RATE ONLY, | m3 | 0.999 |  | 0
2.6 | Place and compact sidefill and backfill using selected excavated material free of stones and tree roots to depth 300 mm above crown of pipe, and after compaction, other excavated material thereafter to final surface | m | 99.9 |  | 0
2.7 | Dispose of all surplus excavated material off-site as directed | LS | 1 |  | 0
Bill No. 3: Supply and Installation of rising main- borehole to elevated water tank |  |  |  |  | 0
All PE compression joints and fittings shall be supplied complete with suitable pipe joint stiffeners. All steel fittings shall be epoxy coated and all nuts and bolts galvanised. Rate shall include supply, lay, bed, joint , pressure test, sterilize and flushing of HDPE pipelines
3.1 | Raw water rising main from borehole to the Elevated Tank , HDPE DN50 (OD 63), SDR17, PN 10 | m | 27 |  | 0
3.2 | Compression fitting, elbow 90o DN 50mm | nr | 1
3.3 | Gate Valve, double flange, handwheel operated 50 mm non-rising spindle type, with 1 No. flanged restraining adapters st. fl. to PE DN 50, installed above ground within tank inlet riser pipe | set | 1 |  | 0
3.4 | Supply and Installation of DN 40 parallel bulk water meter with magnetic transmission and dry recording head , metrological class B, minimum display 1 m3/hr to specification, suitable for vertical mounting, within water tank inlet riser pipe complete with strainer (metallic double flanged body c/w lockable meter box pipe surround). The meter assembly shall comprise: 1 No. DN50 to DN40 reducer, 1 DN40 500mm long straight pipe length, 1 DN 40 mm double flanged vertically mounted parallel bulk type meter, located approximately 1.5 m above ground level, 1 DN 40 250 mm straight pipe length, and one DN40 to DN50 reducer. | set | 1 |  | 0
| Carry forward |  |  |  | 0
| Brought forward |  |  |  | 0
Bill No. 4: Tanks, Tankstands and Tap Stands |  |  |  |  | 0
Bidder shall supply outline details of water tank stand and tank c/w, pipework and fittings.
water tank stand manufacturer:
HDPE cylindrical tank manufacturer:
HDPE cylindrical tank supplier (if different):
Contractor shall supply full set of structural calculations and drawings for water tank stand certified by a registered structural engineer for written approval prior to fabrication.
4.1 | Conduct geotechnical investigations and design foundation and tank stand for the elevated tank | LS | 1 |  | 0
4.2 | Tank reinforced concrete foundations 1 m x 1m x 1.5 m deep inc. excavation, shuttering, concreting, curing, backfilling and disposal of excess spoil material from site | nr | 6 |  | 0
Supply and install 2 No. HDPE cylindrical tank on Contractor designed six vertical members) mild steel tankstand c/w with inlet float valves, all inflow, valved connecting, outflow, overflow, and scour (washout) pipework, fittings, adaptors and 6m high steel stand c/w access ladder and lightning arrestor.
4.3 | Capacity 10m3.(2 no. 5m3 tanks) | nr | 1 |  | 0
4.4 | Supply and paint all mild steel in tank stand with two coats of zinc 82% rich paint in dry film | LS | 1 |  | 0
4.5 | Leak testing and disinfection of tank and pipework | nr | 1 |  | 0
4.6 | Provide & install float level indicator gauge on side of tank readable from ground level adjacent to tank | nr | 1 |  | 0
4.7 | Provide and install chlorine cartridge type inline doser in lockable chamber at start of tank outlet pipe c/w twelve months supply of chlorine cartridges. | LS | 1 |  | 0
4.8 | Provide materials for and construct tap stand and associated drainage | nr | 3 |  | 0
Bill No. 5: Supply and Install Water Distribution Network |  |  |  |  | 0
All PE compression joints and fittings shall be supplied complete with suitable pipe joint stiffeners. All steel fittings shall be epoxy coated and all nuts and bolts galvanised. Rate shall include supply, lay, bed, joint , pressure test, sterilize and flushing of HDPE pipelines
5.1 | Network reticulation pipework HDPE DN50 (OD 63), SDR17, PN 10 | m | 9 |  | 0
5.2 | Unequal reducing tee compression fitting DN 50 x 50 x 40 mm | nr | 1 |  | 0
5.3 | Compression reducer coupling 50mm x 40mm | nr | 3 |  | 0
5.4 | Compression reducer coupling 40mm x 32mm | nr | 2 |  | 0
5.5 | Network reticulation pipework HDPE DN 40mm, SDR17, PN 10 | m | 75 |  | 0
5.6 | Compression fitting, elbow 90o DN 50mm | nr | 1 |  | 0
5.7 | Compression fitting, elbow 90o DN 40mm | nr | 1 |  | 0
5.8 | End cap DN 32mm (compression type) | nr | 2 |  | 0
5.9 | Compression tee DN 40 x 40 x 1" male branch to connect to tap stand pipework | nr | 1 |  | 0
5.1 | Compression tee DN 32 x 32 x 1" male branch to connect to tap stand pipework | nr | 2 |  | 0
5.11 | Gate Valve, double flange, 40 mm non-rising spindle type, with 2 No. flanged restraining adapters st. fl. to PE DN 40, complete with valve riser and valve box to suit | nr | 1 |  | 0
5.12 | Allow for internal plumbing from pipeline to ablution facilities. Prime Cost | sum | 1 | 20000 | 20000
Air valve assembly consisting of 1 No. compression tee with threaded male 1 1/2" branch vertically upwards, 1 No. female to male thr. spigot, 1 No. Stopcock, thr. dble. socket 1", and 1 No. Single air valve, thr. female 1". RATE ONLY
5.13 | Compression tee DN 40 x 40 x 1 1/2" male br., 1 No. female to male 1 1/2" to 1" thr. Spigot | set | 0
| Carry forward |  |  |  | 0
| Brought forward |  |  |  | 0
Bill No. 6: Concrete Works to all Pipelines |  |  |  |  | 0
All unreinforced concrete works shall be in medium strength concrete unless otherwise indicated. Where bends less than 45o are obtained by bending the pipe, radius not less than 35 x pipe diameter, and provided there is no compression joint with 5 metres of either end of radius, no separate thrust block is required.
6.1 | Over excavate in trench bed at all gate valves, air valve assemblies and steel fittings and cast support slab to full width of trench with other dimensions being the length of the valve or the fitting between flanges or between the compression tightening nuts and depth below trench bed of 150 mm | nr | 1 |  | 0
6.2 | At all 45o and 90o bends, pipeline tees, and end caps, provide and subsequently remove shuttering and cast thrust blocks against undisturbed trench bed and trench wall. | nr | 6 |  | 0
6.2 | Supply all materials and cast and complete air-valve chamber. RATE ONLY | nr | 1
| Sub-total Bill Nos 1 to 6 |  |  |  | 0
| Contingencies (10%) Bills No 1 to 6 |  |  |  | 0
| Taxes (VAT @16%) Bills Nos 1 to 6 |  |  |  | 0
| Total Bills Nos 1 to 6 |  |  |  | 0
Bill 7A | Electromechanical - OPTION A Solar Powered |  |  |  | 0
Bidder shall supply all the information and rates for both Alternatives for the offer to be considered. Final decision on the main power source (Option A ZESCO mains power from institutions incoming distribution board, or Option B from Solar Array will be confirmed during negotiation prior to award.
proposed submersible hybrid DC/AC pumpset manufacturer and agent:
proposed standby generator manufacturer and agent:
| confirm manufactures brochures included with bid |  | yes / no
No change from these manufacturers or agents shall be permitted without prior written approval from the Consultant
Submersible 48 VDC Borehole Pump
7.1 | Supply and install a hybrid DC/AC borehole submersible pump suitable for a borehole of ID 5" capable of being powered from either a 48 VDC or a nominal 230 VAC source c/w cabled connection to power sources located within 10 m of borehole head, pumping into an overhead tank with top water inlet 14 m above ground.. . |  | nr | 1
Information provided to guide Bidder
| Ground elevation at borehole (approximate) | masl | 945
| Yield | m3/hr | 1
| Pump installation level below ground surface | m | 30
| Riser pipe diameter | mm | DN 50
| Dynamic water level below ground surface | m | 16.96
| Top water level in overhead tank | masl | 959
Information to be provided by Bidder
| Manufacturers Pump reference No. | ref.
| Maximum flow at Installation indicated above | m3/hr
| Maximum pump head at installation indicated above | m3/hr
| Optimum flow at Installation indicated above | m3/hr
| Optimum head at Installation indicated above | m3/hr
| Pump efficiency at installation | %
| Input power required by pump | W
| Output power required by solar array | W
| No. of solar panels and arrays offered and guaranteed to meet requirement | nr
7.2 | Solar arrays to meet requirements c/w security fence and gate and lightning protection as per Drawing to be included in this Option
7.2.1 | Supply, install, erect and connect solar arrays to meet requirements c/w lightning protection as per Drawing and Specification | nr | 1 |  | 0
7.2.2 | Provide all materials and construct fenced and gated compound to contain solar array and associated chambers to Specification. | LS | 1 |  | 0
7.2.3 | Supply and install DN 25 water pipe take-off from rising mainand sgtandpipe for solar cleansing system | LS | 1 |  | 0
7.2.4 | Provide solar array cleansing step ladder and extendable washer to Specification | LS | 1 |  | 0
Supply and Installation of 220 VAC standby generator of rated power
7.3 | Supply, Install and connect by manually operated changeover switch standby generator capable of providing the VAC power required to operate the submersible borehole pump as specified above at half-load c/w roofed lockable waterproof steel protection cabinet. | nr | 1 |  | 0
Information to be provided by Bidder
Manufacturers Generator Set reference No.
| Output kVA at 1500rpm, 220V, single-phase, 50Hz, with power factor of 1.0 | kVA
| Fuel type (petrol/diesel) | type
| Fuel tank capacity | l
Air or water cooled
7.4 | External 230 VAC Power Source to be included in Option B
| Sub-total Bill No 7A |  |  |  | 0
| Contingencies (10%) Bill No 7A |  |  |  | 0
| Taxes (VAT @16%) Bill No 7A |  |  |  | 0
| Total Bill No 7A |  |  |  | 0
Bill 7B | Electromechanical - OPTION B Mains electric powered |  |  |  | 0
Bidder shall supply all the information and rates for both Alternatives for the offer to be considered. Final decision on the main power source (Option A ZESCO mains power from institutions incoming distribution board, or Option B from Solar Array will be confirmed during negotiation prior to award.
proposed submersible hybrid DC/AC pumpset manufacturer and agent:
proposed standby generator manufacturer and agent:
| confirm manufactures brochures included with bid |  | yes / no
No change from these manufacturers or agents shall be permitted without prior written approval from the Consultant
Submersible 48 VDC Borehole Pump
7.1 | Supply and install a hybrid DC/AC borehole submersible pump suitable for a borehole of ID 5" capable of being powered from either a 48 VDC or a nominal 230 VAC source c/w cabled connection to power sources located within 10 m of borehole head, pumping into an overhead tank with top water inlet 14 m above ground.. . |  | nr | 1
Information provided to guide Bidder
| Ground elevation at borehole (approximate) | masl | 945
| Yield | m3/hr | 1
| Pump installation level below ground surface | m | 30
| Riser pipe diameter | mm | DN 50
| Dynamic water level below ground surface | m | 16.96
| Top water level in overhead tank | masl | 959
Information to be provided by Bidder
| Manufacturers Pump reference No. | ref.
| Maximum flow at Installation indicated above | m3/hr
| Maximum pump head at installation indicated above | m3/hr
| Optimum flow at Installation indicated above | m3/hr
| Optimum head at Installation indicated above | m3/hr
| Pump efficiency at installation | %
| Input power required by pump | W
| Output power required by solar array | W
| No. of solar panels and arrays offered and guaranteed to meet requirement | nr
7.2 | Solar arrays to be included in Option A
Supply and Installation of 220 VAC standby generator of rated power
7.3 | Supply, Install and connect by manually operated changeover switch standby generator capable of providing the VAC power required to operate the submersible borehole pump as specified above at half-load c/w roofed lockable waterproof steel protection cabinet. | nr | 1 |  | 0
Information to be provided by Bidder
Manufacturers Generator Set reference No.
| Output kVA at 1500rpm, 220V, single-phase, 50Hz, with power factor of 1.0 | kVA
| Fuel type (petrol/diesel) | type
| Fuel tank capacity | l
Air or water cooled
External 230 VAC Power Source
7.4 | Underground armoured cable c/w all internal building works, and making good, outside excavation, backfilling and protective concrete cover slabs from Main Distribution Board |  | 0
7.4.1 | All ancilliary work excludng outside excavation, and backfilling, supply and installation of underground armoured cable and protective concrete cover slabs | nr | 1 |  | 0
7.4.2 | External excavation, and backfilling, supply and installation of underground armoured cable and protective concrete cover slabs, minimum cover to cable 600 mm. Length subject to reconfirmation prior to award. | m | 40 |  | 0
| Sub-total Bill No 7B |  |  |  | 0
| Contingencies (10%) Bill No 7B |  |  |  | 0
| Taxes (VAT @16%) Bill No 7B |  |  |  | 0
| Total Bill No 7B |  |  |  | 0

## Mulwe RHC
UNICEF
Solar Powered Borehole Schemes in institutions in Nchelenge (Mantapala) Refugee Camp & Host Communities
Mulwe RHC
Bill No. HC4:
Item | Description | Unit | Qty | Rate (ZMW) | Amount (ZMW)
Bill No. out, Demolition and Site Clearance |  |  |  |  | 0
1.1 | In collaboration with the Inspector of Works, and based upon pipe lengths and alignment shown on layout plan, agree upon final alignment of pipelines, road crossings, location of all tees, bends, isolating valves, air valves, washouts, tapstands, and consumer connection offtakes. Set out pipeline centre-lines, survey, agree upon Starting Surfaces, and final lengths and produce final plans at horizontal scale of 1:200 for approval before proceeding further. | LS | 1 |  | 0
1.2 | General Clearance for urban land & rough grass land along pipeline wayleaves (trench width plus 0.5 m on either side) | ha | 0.1 |  | 0
1.3 | Removal of tree stumps within approved alignment. PROVISIONAL SUM | nr | 1 |  | 0
1.4 | Cut down and remove trees and tree stumps within approved alignment only if specifically directed to do so by Inspector of Works following agreement from the Host Community PROVISIONAL SUM | nr | 1 |  | 0
Bill No. 2: Excavation and backfilling of trenches - all pipelines |  |  |  |  | 0
2.1 | Excavate test pits along centre line of proposed pipeline to depth of 1m at least every 50 m | nr | 5 |  | 0
2.2 | Excavate and trim trench bed to depth not exceeding 1 m to ensure minimum cover provided to pipeline is not less than 600 mm | m | 187.2 |  | 0
2.3 | E. O. item 2.2 at road crossings. Excavate and trim trench to additional depth not exceeding 1.5 m to ensure minimum cover provided to the pipeline is 900 mm | m | 20.8 |  | 0
2.4 | Over excavate trench by a further depth of 150mm in areas identified by the Inspector of Works as requiring imported granular backfill RATE ONLY | m3 | 1.872 |  | 0
2.5 | Import, place and compact granular backfill in areas identified by the Inspector of Works as requiring imported granular backfill. RATE ONLY, | m3 | 1.872 |  | 0
2.6 | Place and compact sidefill and backfill using selected excavated material free of stones and tree roots to depth 300 mm above crown of pipe, and after compaction, other excavated material thereafter to final surface | m | 187.2 |  | 0
2.7 | Dispose of all surplus excavated material off-site as directed | LS | 1 |  | 0
Bill No. 3: Supply and Installation of rising main- borehole to elevated water tank |  |  |  |  | 0
All PE compression joints and fittings shall be supplied complete with suitable pipe joint stiffeners. All steel fittings shall be epoxy coated and all nuts and bolts galvanised. Rate shall include supply, lay, bed, joint , pressure test, sterilize and flushing of HDPE pipelines
3.1 | Raw water rising main from borehole to the Elevated Tank , HDPE DN50 (OD 63), SDR17, PN 10 | m | 63 |  | 0
3.2 | Gate Valve, double flange, handwheel operated 50 mm non-rising spindle type, with 1 No. flanged restraining adapters st. fl. to PE DN 50, installed above ground within tank inlet riser pipe | set | 1 |  | 0
3.3 | Supply and Installation of DN 40 parallel bulk water meter with magnetic transmission and dry recording head , metrological class B, minimum display 1 m3/hr to specification, suitable for vertical mounting, within water tank inlet riser pipe complete with strainer (metallic double flanged body c/w lockable meter box pipe surround). The meter assembly shall comprise: 1 No. DN50 to DN40 reducer, 1 DN40 500mm long straight pipe length, 1 DN 40 mm double flanged vertically mounted parallel bulk type meter, located approximately 1.5 m above ground level, 1 DN 40 250 mm straight pipe length, and one DN40 to DN50 reducer. | set | 1 |  | 0
| Carry forward |  |  |  | 0
| Brought forward |  |  |  | 0
Bill No. 4: Tanks, Tankstands and Tap Stands |  |  |  |  | 0
Bidder shall supply outline details of water tank stand and tank c/w, pipework and fittings.
water tank stand manufacturer:
HDPE cylindrical tank manufacturer:
HDPE cylindrical tank supplier (if different):
Contractor shall supply full set of structural calculations and drawings for water tank stand certified by a registered structural engineer for written approval prior to fabrication.
4.1 | Conduct geotechnical investigations and design foundation and tank stand for the elevated tank | LS | 1 |  | 0
4.2 | Tank reinforced concrete foundations 1 m x 1m x 1.5 m deep inc. excavation, shuttering, concreting, curing, backfilling and disposal of excess spoil material from site | nr | 6 |  | 0
Supply and install 2 No. HDPE cylindrical tank on Contractor designed six vertical members) mild steel tankstand c/w with inlet float valves, all inflow, valved connecting, outflow, overflow, and scour (washout) pipework, fittings, adaptors and 6m high steel stand c/w access ladder and lightning arrestor.
4.3 | Capacity 12m3.(2 no. 6m3 tanks) | nr | 1 |  | 0
4.4 | Supply and paint all mild steel in tank stand with two coats of zinc 82% rich paint in dry film | LS | 1 |  | 0
4.5 | Leak testing and disinfection of tank and pipework | nr | 1 |  | 0
4.6 | Provide & install float level indicator gauge on side of tank readable from ground level adjacent to tank | nr | 1 |  | 0
4.7 | Provide and install chlorine cartridge type inline doser in lockable chamber at start of tank outlet pipe c/w twelve months supply of chlorine cartridges. | LS | 1 |  | 0
4.8 | Provide materials for and construct tap stand and associated drainage | nr | 3 |  | 0
Bill No. 5: Supply and Install Water Distribution Network |  |  |  |  | 0
All PE compression joints and fittings shall be supplied complete with suitable pipe joint stiffeners. All steel fittings shall be epoxy coated and all nuts and bolts galvanised. Rate shall include supply, lay, bed, joint , pressure test, sterilize and flushing of HDPE pipelines
5.1 | Network reticulation pipework HDPE DN50 (OD 63), SDR17, PN 10 | m | 20 |  | 0
5.2 | Equal tee compression fitting DN 50 x 50 x 50 mm | nr | 1 |  | 0
5.3 | Compression reducer coupling 50mm x 40mm | nr | 2 |  | 0
5.4 | Compression reducer coupling 40mm x 32mm | nr | 2 |  | 0
5.5 | Network reticulation pipework HDPE DN 40mm, SDR17, PN 10 | m | 125 |  | 0
5.6 | Compression fitting, elbow 90o DN 40mm | nr | 1 |  | 0
5.7 | End cap DN 32mm (compression type) | nr | 2 |  | 0
5.8 | Supply and install GI pipes 25mm dia c/w fittings to tap stands c/w isolating stop cock | nr | 2 |  | 0
5.9 | Supply and install heavy weight brass garden bib tap (non-lever arm type) | nr | 4 |  | 0
5.1 | Compression tee DN 40 x 40 x 1" male branch to connect to tap stand pipework | nr | 1 |  | 0
5.11 | Compression tee DN 32 x 32 x 1" male branch to connect to tap stand pipework | nr | 2 |  | 0
5.12 | Gate Valve, double flange, 40 mm non-rising spindle type, with 2 No. flanged restraining adapters st. fl. to PE DN 40, complete with valve riser and valve box to suit | nr | 2 |  | 0
5.13 | Allow for internal plumbing from pipeline to ablution facilities. Prime Cost | sum | 1 |  | 0
Air valve assembly consisting of 1 No. compression tee with threaded male 1 1/2" branch vertically upwards, 1 No. female to male thr. spigot, 1 No. Stopcock, thr. dble. socket 1", and 1 No. Single air valve, thr. female 1". RATE ONLY
5.14.1 | Compression tee DN 50 x 50 x 1 1/2" male br., 1 No. female to male 1 1/2" to 1" thr. spigot | set | 0
5.14.2 | Compression tee DN 40 x 40 x 1 1/2" male br., 1 No. female to male 1 1/2" to 1" thr. Spigot | set | 0
| Carry forward |  |  |  | 0
| Brought forward |  |  |  | 0
Bill No. 6: Concrete Works to all Pipelines |  |  |  |  | 0
All unreinforced concrete works shall be in medium strength concrete unless otherwise indicated. Where bends less than 45o are obtained by bending the pipe, radius not less than 35 x pipe diameter, and provided there is no compression joint with 5 metres of either end of radius, no separate thrust block is required.
6.1 | Over excavate in trench bed at all gate valves, air valve assemblies and steel fittings and cast support slab to full width of trench with other dimensions being the length of the valve or the fitting between flanges or between the compression tightening nuts and depth below trench bed of 150 mm | nr | 2 |  | 0
6.2 | At all 45o and 90o bends, pipeline tees, and end caps, provide and subsequently remove shuttering and cast thrust blocks against undisturbed trench bed and trench wall, as shown on Standard Drawing | nr | 4 |  | 0
6.3 | Supply all materials and cast and complete air-valve chamber. RATE ONLY | nr | 1
| Sub-total Bill Nos 1 to 6 |  |  |  | 0
| Contingencies (10%) Bills No 1 to 6 |  |  |  | 0
| Taxes (VAT @16%) Bills Nos 1 to 6 |  |  |  | 0
| Total Bills Nos 1 to 6 |  |  |  | 0
Bill 7A | Electromechanical - OPTION A Solar Powered |  |  |  | 0
Bidder shall supply all the information and rates for both Alternatives for the offer to be considered. Final decision on the main power source (Option A ZESCO mains power from institutions incoming distribution board, or Option B from Solar Array will be confirmed during negotiation prior to award.
proposed submersible hybrid DC/AC pumpset manufacturer and agent:
proposed standby generator manufacturer and agent:
| confirm manufactures brochures included with bid |  | yes / no
No change from these manufacturers or agents shall be permitted without prior written approval from the Consultant
Submersible 48 VDC Borehole Pump
7.1 | Supply and install a hybrid DC/AC borehole submersible pump suitable for a borehole of ID 5" capable of being powered from either a 48 VDC or a nominal 230 VAC source c/w cabled connection to power sources located within 10 m of borehole head, pumping into an overhead tank with top water inlet 14 m above ground.. . |  | nr | 1
Information provided to guide Bidder
| Ground elevation at borehole (approximate) | masl | 958
| Yield | m3/hr | 0.45
| Pump installation level below ground surface | m | 48
| Riser pipe diameter | mm | DN 50
| Dynamic water level below ground surface | m | 38.53
| Top water level in overhead tank | masl | 973
Information to be provided by Bidder
| Manufacturers Pump reference No. | ref.
| Maximum flow at Installation indicated above | m3/hr
| Maximum pump head at installation indicated above | m3/hr
| Optimum flow at Installation indicated above | m3/hr
| Optimum head at Installation indicated above | m3/hr
| Pump efficiency at installation | %
| Input power required by pump | W
| Output power required by solar array | W
| No. of solar panels and arrays offered and guaranteed to meet requirement | nr
7.2 | Solar arrays to meet requirements c/w security fence and gate and lightning protection as per Drawing to be included in this Option
7.2.1 | Supply, install, erect and connect solar arrays to meet requirements c/w lightning protection as per Drawing and Specification | nr | 1 |  | 0
7.2.2 | Provide all materials and construct fenced and gated compound to contain solar array and associated chambers to Specification. | LS | 1 |  | 0
7.2.3 | Supply and install DN 25 water pipe take-off from rising mainand sgtandpipe for solar cleansing system | LS | 1 |  | 0
7.2.4 | Provide solar array cleansing step ladder and extendable washer to Specification | LS | 1 |  | 0
Supply and Installation of 220 VAC standby generator of rated power
7.3 | Supply, Install and connect by manually operated changeover switch standby generator capable of providing the VAC power required to operate the submersible borehole pump as specified above at half-load c/w roofed lockable waterproof steel protection cabinet. | nr | 1 |  | 0
Information to be provided by Bidder
Manufacturers Generator Set reference No.
| Output kVA at 1500rpm, 220V, single-phase, 50Hz, with power factor of 1.0 | kVA
| Fuel type (petrol/diesel) | type
| Fuel tank capacity | l
Air or water cooled
7.4 | External 230 VAC Power Source to be included in Option B
| Sub-total Bill No 7A |  |  |  | 0
| Contingencies (10%) Bill No 7A |  |  |  | 0
| Taxes (VAT @16%) Bill No 7A |  |  |  | 0
| Total Bill No 7A |  |  |  | 0
Bill 7B | Electromechanical - OPTION B Mains electric powered |  |  |  | 0
Bidder shall supply all the information and rates for both Alternatives for the offer to be considered. Final decision on the main power source (Option A ZESCO mains power from institutions incoming distribution board, or Option B from Solar Array will be confirmed during negotiation prior to award.
proposed submersible hybrid DC/AC pumpset manufacturer and agent:
proposed standby generator manufacturer and agent:
| confirm manufactures brochures included with bid |  | yes / no
No change from these manufacturers or agents shall be permitted without prior written approval from the Consultant
Submersible 48 VDC Borehole Pump
7.1 | Supply and install a hybrid DC/AC borehole submersible pump suitable for a borehole of ID 5" capable of being powered from either a 48 VDC or a nominal 230 VAC source c/w cabled connection to power sources located within 10 m of borehole head, pumping into an overhead tank with top water inlet 14 m above ground.. . |  | nr | 1
Information provided to guide Bidder
| Ground elevation at borehole (approximate) | masl | 958
| Yield | m3/hr | 0.45
| Pump installation level below ground surface | m | 48
| Riser pipe diameter | mm | DN 50
| Dynamic water level below ground surface | m | 38.53
| Top water level in overhead tank | masl | 973
Information to be provided by Bidder
| Manufacturers Pump reference No. | ref.
| Maximum flow at Installation indicated above | m3/hr
| Maximum pump head at installation indicated above | m3/hr
| Optimum flow at Installation indicated above | m3/hr
| Optimum head at Installation indicated above | m3/hr
| Pump efficiency at installation | %
| Input power required by pump | W
| Output power required by solar array | W
| No. of solar panels and arrays offered and guaranteed to meet requirement | nr
7.2 | Solar arrays to be included in Option A
Supply and Installation of 220 VAC standby generator of rated power
7.3 | Supply, Install and connect by manually operated changeover switch standby generator capable of providing the VAC power required to operate the submersible borehole pump as specified above at half-load c/w roofed lockable waterproof steel protection cabinet. | nr | 1 |  | 0
Information to be provided by Bidder
Manufacturers Generator Set reference No.
| Output kVA at 1500rpm, 220V, single-phase, 50Hz, with power factor of 1.0 | kVA
| Fuel type (petrol/diesel) | type
| Fuel tank capacity | l
Air or water cooled
External 230 VAC Power Source
7.4 | Underground armoured cable c/w all internal building works, and making good, outside excavation, backfilling and protective concrete cover slabs from Main Distribution Board |  | 0
7.4.1 | All ancilliary work excludng outside excavation, and backfilling, supply and installation of underground armoured cable and protective concrete cover slabs | nr | 1 |  | 0
7.4.2 | External excavation, and backfilling, supply and installation of underground armoured cable and protective concrete cover slabs, minimum cover to cable 600 mm.. Length subject to reconfirmation prior to award. | m | 50 |  | 0
| Sub-total Bill No 7B |  |  |  | 0
| Contingencies (10%) Bill No 7B |  |  |  | 0
| Taxes (VAT @16%) Bill No 7B |  |  |  | 0
| Total Bill No 7B |  |  |  | 0

## St Pauls Hosp Staff Houses
UNICEF
Solar Powered Borehole Schemes in institutions in Nchelenge (Mantapala) Refugee Camp & Host Communities
St Pauls Hospital Staff Houses
Bill No. HC5:
Item | Description | Unit | Qty | Rate (ZMW) | Amount (ZMW)
Bill No. out, Demolition and Site Clearance |  |  |  |  | 0
1.1 | In collaboration with the Inspector of Works, and based upon pipe lengths and alignment shown on layout plan, agree upon final alignment of pipelines, road crossings, location of all tees, bends, isolating valves, air valves, washouts, tapstands, and consumer connection offtakes. Set out pipeline centre-lines, survey, agree upon Starting Surfaces, and final lengths and produce final plans at horizontal scale of 1:200 for approval before proceeding further. | LS | 1 |  | 0
1.2 | General Clearance for urban land & rough grass land along pipeline wayleaves (trench width plus 0.5 m on either side) | ha | 0.1 |  | 0
1.4 | Removal of tree stumps within approved alignment. PROVISIONAL SUM | nr | 1 |  | 0
1.5 | Cut down and remove trees and tree stumps within approved alignment only if specifically directed to do so by Inspector of Works following agreement from the Host Community PROVISIONAL SUM | nr | 1 |  | 0
Bill No. 2: Excavation and backfilling of trenches - all pipelines |  |  |  |  | 0
2.1 | Excavate test pits along centre line of proposed pipeline to depth of 1m at least every 50 m | nr | 9 |  | 0
2.2 | Excavate and trim trench bed to depth not exceeding 1 m to ensure minimum cover provided to pipeline is not less than 600 mm | m | 367.2 |  | 0
2.3 | E. O. item 2.2 at road crossings. Excavate and trim trench to additional depth not exceeding 1.5 m to ensure minimum cover provided to the pipeline is 900 mm | m | 40.8 |  | 0
2.4 | Over excavate trench by a further depth of 150mm in areas identified by the Inspector of Works as requiring imported granular backfill RATE ONLY | m3 | 3.672 |  | 0
2.5 | Import, place and compact granular backfill in areas identified by the Inspector of Works as requiring imported granular backfill. RATE ONLY, | m3 | 3.672 |  | 0
2.6 | Place and compact sidefill and backfill using selected excavated material free of stones and tree roots to depth 300 mm above crown of pipe, and after compaction, other excavated material thereafter to final surface | m | 367.2 |  | 0
2.7 | Dispose of all surplus excavated material off-site as directed | LS | 1 |  | 0
Bill No. 3: Supply and Installation of rising main- borehole to elevated water tank |  |  |  |  | 0
All PE compression joints and fittings shall be supplied complete with suitable pipe joint stiffeners. All steel fittings shall be epoxy coated and all nuts and bolts galvanised. Rate shall include supply, lay, bed, joint , pressure test, sterilize and flushing of HDPE pipelines
3.1 | Raw water rising main from borehole to the Elevated Tank , HDPE DN50 (OD 63), SDR17, PN 10 | m | 12 |  | 0
3.2 | Gate Valve, double flange, handwheel operated 50 mm non-rising spindle type, with 1 No. flanged restraining adapters st. fl. to PE DN 50, installed above ground within tank inlet riser pipe | set | 1 |  | 0
3.3 | Supply and Installation of DN 40 parallel bulk water meter with magnetic transmission and dry recording head , metrological class B, minimum display 1 m3/hr to specification, suitable for vertical mounting, within water tank inlet riser pipe complete with strainer (metallic double flanged body c/w lockable meter box pipe surround). The meter assembly shall comprise: 1 No. DN50 to DN40 reducer, 1 DN40 500mm long straight pipe length, 1 DN 40 mm double flanged vertically mounted parallel bulk type meter, located approximately 1.5 m above ground level, 1 DN 40 250 mm straight pipe length, and one DN40 to DN50 reducer. | set | 1 |  | 0
| Carry forward |  |  |  | 0
| Brought forward |  |  |  | 0
Bill No. 4: Tanks, Tankstands and Tap Stands |  |  |  |  | 0
Bidder shall supply outline details of water tank stand and tank c/w, pipework and fittings.
water tank stand manufacturer:
HDPE cylindrical tank manufacturer:
HDPE cylindrical tank supplier (if different):
Contractor shall supply full set of structural calculations and drawings for water tank stand certified by a registered structural engineer for written approval prior to fabrication.
4.1 | Conduct geotechnical investigations and design foundation and tank stand for the elevated tank | LS | 1 |  | 0
4.2 | Tank reinforced concrete foundations 1 m x 1m x 1.5 m deep inc. excavation, shuttering, concreting, curing, backfilling and disposal of excess spoil material from site | nr | 4 |  | 0
Supply and install 1 No. HDPE cylindrical tank on Contractor designed mild steel tankstand c/w with inlet float valve, all inflow, outflow, overflow, and scour (washout) pipework, fittings, adaptors and 6m high steel stand c/w access ladder and lightning arrestor.
4.3 | Capacity 5m3. | nr | 1 |  | 0
4.4 | Supply and paint all mild steel in tank stand with two coats of zinc 82% rich paint in dry film | LS | 1 |  | 0
4.5 | Leak testing and disinfection of tank and pipework | nr | 1 |  | 0
4.6 | Provide & install float level indicator gauge on side of tank readable from ground level adjacent to tank | nr | 1 |  | 0
4.7 | Provide and install chlorine cartridge type inline doser in lockable chamber at start of tank outlet pipe c/w twelve months supply of chlorine cartridges. | LS | 1 |  | 0
4.8 | Provide materials for and construct tap stand and associated drainage | nr | 3 |  | 0
Bill No. 5: Supply and Install Water Distribution Network |  |  |  |  | 0
All PE compression joints and fittings shall be supplied complete with suitable pipe joint stiffeners. All steel fittings shall be epoxy coated and all nuts and bolts galvanised. Rate shall include supply, lay, bed, joint , pressure test, sterilize and flushing of HDPE pipelines
5.1 | Network reticulation pipework HDPE DN50 (OD 63), SDR17, PN 10 | m | 132 |  | 0
5.2 | Compression reducer coupling 50mm x 40mm | nr | 3 |  | 0
5.3 | Compression reducer coupling 40mm x 32mm | nr | 1 |  | 0
5.4 | Network reticulation pipework HDPE DN 40mm, SDR17, PN 10 | m | 264 |  | 0
5.5 | Compression fitting, elbow 45o DN 50mm | nr | 2 |  | 0
5.6 | Compression fitting, elbow 45o DN 40mm | nr | 2 |  | 0
5.7 | Compression fitting, elbow 90o DN 40mm | nr | 3 |  | 0
5.8 | End cap DN 32mm (compression type) | nr | 1 |  | 0
5.9 | Supply and install GI pipes 25mm dia c/w fittings to tap stands c/w isolating stop cock | nr | 3 |  | 0
5.1 | Supply and install heavy weight brass garden bib tap (non-lever arm type) | nr | 6 |  | 0
5.11 | Compression tee DN 40 x 40 x 1" male branch to connect to tap stand pipework | nr | 2 |  | 0
5.12 | Compression tee DN 32 x 32 x 1" male branch to connect to tap stand pipework | nr | 1 |  | 0
5.13 | Gate Valve, double flange, 40 mm non-rising spindle type, with 2 No. flanged restraining adapters st. fl. to PE DN 40, complete with valve riser and valve box to suit | nr | 1 |  | 0
Air valve assembly consisting of 1 No. compression tee with threaded male 1 1/2" branch vertically upwards, 1 No. female to male thr. spigot, 1 No. Stopcock, thr. dble. socket 1", and 1 No. Single air valve, thr. female 1". RATE ONLY
5.14.1 | Compression tee DN 50 x 50 x 1 1/2" male br., 1 No. female to male 1 1/2" to 1" thr. spigot | set | 0
5.14.2 | Compression tee DN 40 x 40 x 1 1/2" male br., 1 No. female to male 1 1/2" to 1" thr. Spigot | set | 0
| Carry forward |  |  |  | 0
| Brought forward |  |  |  | 0
Bill No. 6: Concrete Works to all Pipelines |  |  |  |  | 0
All unreinforced concrete works shall be in medium strength concrete unless otherwise indicated. Where bends less than 45o are obtained by bending the pipe, radius not less than 35 x pipe diameter, and provided there is no compression joint with 5 metres of either end of radius, no separate thrust block is required.
6.1 | Over excavate in trench bed at all gate valves, air valve assemblies and steel fittings and cast support slab to full width of trench with other dimensions being the length of the valve or the fitting between flanges or between the compression tightening nuts and depth below trench bed of 150 mm | nr | 1 |  | 0
6.2 | At all 45o and 90o bends, pipeline tees, and end caps, provide and subsequently remove shuttering and cast thrust blocks against undisturbed trench bed and trench wall | nr | 8 |  | 0
6.3 | Supply all materials and cast and complete air-valve chamber. RATE ONLY | nr | 1
| Sub-total Bill Nos 1 to 6 |  |  |  | 0
| Contingencies (10%) Bills No 1 to 6 |  |  |  | 0
| Taxes (VAT @16%) Bills Nos 1 to 6 |  |  |  | 0
| Total Bills Nos 1 to 6 |  |  |  | 0
Bill 7A | Electromechanical - OPTION A Solar Powered |  |  |  | 0
Bidder shall supply all the information and rates for both Alternatives for the offer to be considered. Final decision on the main power source (Option A ZESCO mains power from institutions incoming distribution board, or Option B from Solar Array will be confirmed during negotiation prior to award.
proposed submersible hybrid DC/AC pumpset manufacturer and agent:
proposed standby generator manufacturer and agent:
| confirm manufactures brochures included with bid |  | yes / no
No change from these manufacturers or agents shall be permitted without prior written approval from the Consultant
Submersible 48 VDC Borehole Pump
7.1 | Supply and install a hybrid DC/AC borehole submersible pump suitable for a borehole of ID 5" capable of being powered from either a 48 VDC or a nominal 230 VAC source c/w cabled connection to power sources located within 10 m of borehole head, pumping into an overhead tank with top water inlet 14 m above ground.. . |  | nr | 1
Information provided to guide Bidder
| Ground elevation at borehole (approximate) | masl | 963
| Yield | m3/hr | 5.1
| Pump installation level below ground surface | m | 48
| Riser pipe diameter | mm | DN 50
| Dynamic water level below ground surface | m | 32.48
| Top water level in overhead tank | masl | 977
Information to be provided by Bidder
| Manufacturers Pump reference No. | ref.
| Maximum flow at Installation indicated above | m3/hr
| Maximum pump head at installation indicated above | m3/hr
| Optimum flow at Installation indicated above | m3/hr
| Optimum head at Installation indicated above | m3/hr
| Pump efficiency at installation | %
| Input power required by pump | W
| Output power required by solar array | W
| No. of solar panels and arrays offered and guaranteed to meet requirement | nr
7.2 | Solar arrays to be included in Option A
7.2.1 | Supply, install, erect and connect solar arrays to meet requirements c/w lightning protection as per Drawing and Specification | nr | 1 |  | 0
7.2.2 | Provide all materials and construct fenced and gated compound to contain solar array and associated chambers to Specification. | LS | 1 |  | 0
7.2.3 | Supply and install DN 25 water pipe take-off from rising mainand sgtandpipe for solar cleansing system | LS | 1 |  | 0
7.2.4 | Provide solar array cleansing step ladder and extendable washer to Specification | LS | 1 |  | 0
Supply and Installation of 220 VAC standby generator of rated power
7.3 | Supply, Install and connect by manually operated changeover switch standby generator capable of providing the VAC power required to operate the submersible borehole pump as specified above at half-load c/w roofed lockable waterproof steel protection cabinet. | nr | 1 |  | 0
Information to be provided by Bidder
Manufacturers Generator Set reference No.
| Output kVA at 1500rpm, 220V, single-phase, 50Hz, with power factor of 1.0 | kVA
| Fuel type (petrol/diesel) | type
| Fuel tank capacity | l
Air or water cooled
7.4 | External 230 VAC Power Source to be included in Option B
| Sub-total Bill No 7A |  |  |  | 0
| Contingencies (10%) Bill No 7A |  |  |  | 0
| Taxes (VAT @16%) Bill No 7A |  |  |  | 0
| Total Bill No 7A |  |  |  | 0
Bill 7B | Electromechanical - OPTION B Mains electric powered |  |  |  | 0
Bidder shall supply all the information and rates for both Alternatives for the offer to be considered. Final decision on the main power source (Option A ZESCO mains power from institutions incoming distribution board, or Option B from Solar Array will be confirmed during negotiation prior to award.
proposed submersible hybrid DC/AC pumpset manufacturer and agent:
proposed standby generator manufacturer and agent:
| confirm manufactures brochures included with bid |  | yes / no
No change from these manufacturers or agents shall be permitted without prior written approval from the Consultant
Submersible 48 VDC Borehole Pump
7.1 | Supply and install a hybrid DC/AC borehole submersible pump suitable for a borehole of ID 5" capable of being powered from either a 48 VDC or a nominal 230 VAC source c/w cabled connection to power sources located within 10 m of borehole head, pumping into an overhead tank with top water inlet 14 m above ground.. . |  | nr | 1
Information provided to guide Bidder
| Ground elevation at borehole (approximate) | masl | 963
| Yield | m3/hr | 5.1
| Pump installation level below ground surface | m | 48
| Riser pipe diameter | mm | DN 50
| Dynamic water level below ground surface | m | 32.48
| Top water level in overhead tank | masl | 977
Information to be provided by Bidder
| Manufacturers Pump reference No. | ref.
| Maximum flow at Installation indicated above | m3/hr
| Maximum pump head at installation indicated above | m3/hr
| Optimum flow at Installation indicated above | m3/hr
| Optimum head at Installation indicated above | m3/hr
| Pump efficiency at installation | %
| Input power required by pump | W
| Output power required by solar array | W
| No. of solar panels and arrays offered and guaranteed to meet requirement | nr
7.2 | Solar arrays to be included in Option A
Supply and Installation of 220 VAC standby generator of rated power
7.3 | Supply, Install and connect by manually operated changeover switch standby generator capable of providing the VAC power required to operate the submersible borehole pump as specified above at half-load c/w roofed lockable waterproof steel protection cabinet. | nr | 1 |  | 0
Information to be provided by Bidder
Manufacturers Generator Set reference No.
| Output kVA at 1500rpm, 220V, single-phase, 50Hz, with power factor of 1.0 | kVA
| Fuel type (petrol/diesel) | type
| Fuel tank capacity | l
Air or water cooled
External 230 VAC Power Source
7.4 | Underground armoured cable c/w all internal building works, and making good, outside excavation, backfilling and protective concrete cover slabs from Main Distribution Board |  | 0
7.4.1 | All ancilliary work excludng outside excavation, and backfilling, supply and installation of underground armoured cable and protective concrete cover slabs | nr | 1 |  | 0
7.4.2 | External excavation, and backfilling, supply and installation of underground armoured cable and protective concrete cover slabs, minimum cover to cable 600 mm. Length subject to reconfirmation prior to award. | m | 205 |  | 0
| Sub-total Bill No 7B |  |  |  | 0
| Contingencies (10%) Bill No 7B |  |  |  | 0
| Taxes (VAT @16%) Bill No 7B |  |  |  | 0
| Total Bill No 7B |  |  |  | 0

## Kapambwe RHC
UNICEF
Solar Powered Borehole Schemes in institutions in Nchelenge (Mantapala) Refugee Camp & Host Communities
Kapambwe RHC
Bill No. HC6:
Item | Description | Unit | Qty | Rate (ZMW) | Amount (ZMW)
Bill No. out, Demolition and Site Clearance |  |  |  |  | 0
1.1 | In collaboration with the Inspector of Works, and based upon pipe lengths and alignment shown on layout plan, agree upon final alignment of pipelines, road crossings, location of all tees, bends, isolating valves, air valves, washouts, tapstands, and consumer connection offtakes. Set out pipeline centre-lines, survey, agree upon Starting Surfaces, and final lengths and produce final plans at horizontal scale of 1:200 for approval before proceeding further. | LS | 1 |  | 0
1.2 | General Clearance for urban land & rough grass land along pipeline wayleaves (trench width plus 0.5 m on either side) | ha | 0.1 |  | 0
1.3 | Removal of tree stumps within approved alignment. PROVISIONAL SUM | nr | 1 |  | 0
1.4 | Cut down and remove trees and tree stumps within approved alignment only if specifically directed to do so by Inspector of Works following agreement from the Host Community PROVISIONAL SUM | nr | 1 |  | 0
Bill No. 2: Excavation and backfilling of trenches - all pipelines |  |  |  |  | 0
2.1 | Excavate test pits along centre line of proposed pipeline to depth of 1m at least every 50 m | nr | 4 |  | 0
2.2 | Excavate and trim trench bed to depth not exceeding 1 m to ensure minimum cover provided to pipeline is not less than 600 mm | m | 170.1 |  | 0
2.3 | E. O. item 2.2 at road crossings. Excavate and trim trench to additional depth not exceeding 1.5 m to ensure minimum cover provided to the pipeline is 900 mm | m | 18.9 |  | 0
2.4 | Over excavate trench by a further depth of 150mm in areas identified by the Inspector of Works as requiring imported granular backfill RATE ONLY | m3 | 1.701 |  | 0
2.5 | Import, place and compact granular backfill in areas identified by the Inspector of Works as requiring imported granular backfill. RATE ONLY, | m3 | 1.701 |  | 0
2.6 | Place and compact sidefill and backfill using selected excavated material free of stones and tree roots to depth 300 mm above crown of pipe, and after compaction, other excavated material thereafter to final surface | m | 170.1 |  | 0
2.7 | Dispose of all surplus excavated material off-site as directed | LS | 1 |  | 0
Bill No. 3: Supply and Installation of rising main- borehole to elevated water tank |  |  |  |  | 0
All PE compression joints and fittings shall be supplied complete with suitable pipe joint stiffeners. All steel fittings shall be epoxy coated and all nuts and bolts galvanised. Rate shall include supply, lay, bed, joint , pressure test, sterilize and flushing of HDPE pipelines
3.1 | Raw water rising main from borehole to the Elevated Tank , HDPE DN50 (OD 63), SDR17, PN 10 | m | 28 |  | 0
3.2 | Gate Valve, double flange, handwheel operated 50 mm non-rising spindle type, with 1 No. flanged restraining adapters st. fl. to PE DN 50, installed above ground within tank inlet riser pipe | set | 1 |  | 0
3.3 | Supply and Installation of DN 40 parallel bulk water meter with magnetic transmission and dry recording head , metrological class B, minimum display 1 m3/hr to specification, suitable for vertical mounting, within water tank inlet riser pipe complete with strainer (metallic double flanged body c/w lockable meter box pipe surround). The meter assembly shall comprise: 1 No. DN50 to DN40 reducer, 1 DN40 500mm long straight pipe length, 1 DN 40 mm double flanged vertically mounted parallel bulk type meter, located approximately 1.5 m above ground level, 1 DN 40 250 mm straight pipe length, and one DN40 to DN50 reducer. | set | 1 |  | 0
3.4 | Provide all materials and construct fenced and gated compound to contain solar array and associated chambers to Specification. | LS | 1 |  | 0
3.5 | Supply and install DN 25 water pipe take-off from rising mainand standpipe for solar cleansing system | LS | 1 |  | 0
3.6 | Provide solar array cleansing step ladder and extendable washer to Specification | LS | 1 |  | 0
| Carry forward |  |  |  | 0
| Brought forward |  |  |  | 0
Bill No. 4: Tanks, Tankstands and Tap Stands |  |  |  |  | 0
Bidder shall supply outline details of water tank stand and tank c/w, pipework and fittings.
water tank stand manufacturer:
HDPE cylindrical tank manufacturer:
HDPE cylindrical tank supplier (if different):
Contractor shall supply full set of structural calculations and drawings for water tank stand certified by a registered structural engineer for written approval prior to fabrication.
4.1 | Conduct geotechnical investigations and design foundation and tank stand for the elevated tank | LS | 1 |  | 0
4.2 | Tank reinforced concrete foundations 1 m x 1m x 1.5 m deep inc. excavation, shuttering, concreting, curing, backfilling and disposal of excess spoil material from site | nr | 4 |  | 0
Supply and install 1 No. HDPE cylindrical tank on Contractor designed mild steel tankstand c/w with inlet float valve, all inflow, outflow, overflow, and scour (washout) pipework, fittings, adaptors and 6m high steel stand c/w access ladder and lightning arrestor.
4.3 | Capacity 5m3. | nr | 1 |  | 0
4.4 | Supply and paint all mild steel in tank stand with two coats of zinc 82% rich paint in dry film | LS | 1 |  | 0
4.5 | Leak testing and disinfection of tank and pipework | nr | 1 |  | 0
4.6 | Provide & install float level indicator gauge on side of tank readable from ground level adjacent to tank | nr | 1 |  | 0
4.7 | Provide and install chlorine cartridge type inline doser in lockable chamber at start of tank outlet pipe c/w twelve months supply of chlorine cartridges. | LS | 1 |  | 0
4.8 | Provide materials for and construct tap stand and associated drainage | nr | 4 |  | 0
Bill No. 5: Supply and Install Water Distribution Network |  |  |  |  | 0
All PE compression joints and fittings shall be supplied complete with suitable pipe joint stiffeners. All steel fittings shall be epoxy coated and all nuts and bolts galvanised. Rate shall include supply, lay, bed, joint , pressure test, sterilize and flushing of HDPE pipelines
5.1 | Equal tee compression fitting DN 32 x 32 x 32 mm | nr | 3 |  | 0
5.2 | Network reticulation pipework HDPE DN 32mm, SDR17, PN 10 | m | 161 |  | 0
5.3 | End cap DN 32mm (compression type) | nr | 4 |  | 0
5.4 | Saddle clamp 32mm x 3/4" to supply individual consumer connection | nr | 0 |  | 0
5.5 | Supply and install GI pipes 25mm dia c/w fittings to tap stands c/w isolating stop cock | nr | 4 |  | 0
5.6 | Supply and install heavy weight brass garden bib tap (non-lever arm type) | nr | 8 |  | 0
5.7 | Compression tee DN 32 x 32 x 1" male branch to connect to tap stand pipework | nr | 4 |  | 0
5.8 | Gate Valve, double flange, 40 mm non-rising spindle type, with 2 No. flanged restraining adapters st. fl. to PE DN 40, complete with valve riser and valve box to suit | nr | 1 |  | 0
Air valve assembly consisting of 1 No. compression tee with threaded male 1 1/2" branch vertically upwards, 1 No. female to male thr. spigot, 1 No. Stopcock, thr. dble. socket 1", and 1 No. Single air valve, thr. female 1". RATE ONLY
5.9 | Compression tee DN 32 x 32 x 1" male br, 1 No. female to male 1" to 1" thr. spigot | set | 0
| Carry forward |  |  |  | 0
| Brought forward |  |  |  | 0
Bill No. 6: Concrete Works to all Pipelines |  |  |  |  | 0
All unreinforced concrete works shall be in medium strength concrete unless otherwise indicated. Where bends less than 45o are obtained by bending the pipe, radius not less than 35 x pipe diameter, and provided there is no compression joint with 5 metres of either end of radius, no separate thrust block is required.
8.1 | Over excavate in trench bed at all gate valves, air valve assemblies and steel fittings and cast support slab to full width of trench with other dimensions being the length of the valve or the fitting between flanges or between the compression tightening nuts and depth below trench bed of 150 mm | nr | 1 |  | 0
6.2 | At all 45o and 90o bends, pipeline tees, and end caps, provide and subsequently remove shuttering and cast thrust blocks against undisturbed trench bed and trench wall | nr | 7 |  | 0
6.3 | Supply all materials and cast and complete air-valve chamber. RATE ONLY | nr | 1
Bill No. 7: Water Distribution Network | Electromechanical |  |  |  | 0
Bidder shall supply details of proposed pumpset c/w shroud, and standby generator for which there shall be a local agent
proposed submersible hybrid DC/AC pumpset manufacturer and agent:
proposed standby generator manufacturer and agent:
| confirm manufactures brochures included with bid |  | yes / no
No change from these manufacturers or agents shall be permitted without prior written approval from the Consultant
Submersible 48 VDC Borehole Pump
7.1 | Supply and install a hybrid DC/AC borehole submersible pump suitable for a borehole of ID 5" capable of being powered from either a 48 VDC or a nominal 230 VAC source c/w cabled connection to power sources located within 10 m of borehole head, pumping into an overhead tank with top water inlet 14 m above ground.. . |  | nr | 1
Information provided to guide Bidder
| Ground elevation at borehole (approximate) | masl | 819
| Yield | m3/hr | tbc
| Pump installation level below ground surface | m | tbc
| Riser pipe diameter | mm | DN 50
| Dynamic water level below ground surface | m | tbc
| Top water level in overhead tank | masl | 834
Information to be provided by Bidder
| Manufacturers Pump reference No. | ref.
| Maximum flow at Installation indicated above | m3/hr
| Maximum pump head at installation indicated above | m3/hr
| Optimum flow at Installation indicated above | m3/hr
| Optimum head at Installation indicated above | m3/hr
| Pump efficiency at installation | %
| Input power required by pump | W
| Output power required by solar array | W
| No. of solar panels and arrays offered and guaranteed to meet requirement | nr
7.2 | Supply, install, erect and connect solar arrays to meet requirements c/w lightning protection as per Drawing | LS | 1 |  | 0
Supply and Installation of 220 VAC standby generator of rated power
7.3 | Supply, Install and connect by manually operated changeover switch standby generator capable of providing the VAC power required to operate the submersible borehole pump as specified above at half-load c/w roofed lockable waterproof steel protection cabinet. | nr | 1 |  | 0
Information to be provided by Bidder
Manufacturers Generator Set reference No.
| Output kVA at 1500rpm, 220V, single-phase, 50Hz, with power factor of 1.0 | kVA
| Fuel type (petrol/diesel) | type
| Fuel tank capacity | l
Air or water cooled
External 230 VAC Power Source
7.4.1 | By underground armoured cable c/w all excavation, backfilling and protective concrete cover slabs from LV side of ZESCO step down transformer | m | 0
7.4.2 | By underground armoured cable c/w all internal building works, and making good, outside excavation, backfilling and protective concrete cover slabs from Main Distribution Board | m | 80 |  | 0
7.5 | By overhead single phase 230 VAC power line from LV side of ZESCO step-down transformer, c/w all necessary intermediate power poles | m | 0
| Sub-total |  |  |  | 0
| Contingencies (10%) |  |  |  | 0
| Taxes (VAT @16%) |  |  |  | 0
| Total |  |  |  | 0
Note on C26: Baker: parallel or vertical Woltman meter?

## Kashikishi Market
UNICEF
Solar Powered Borehole Schemes in institutions in Nchelenge (Mantapala) Refugee Camp & Host Communities
Kashikishi Market
Bill No. MKT1:
Item | Description | Unit | Qty | Rate (ZMW) | Amount (ZMW)
Bill No. out, Demolition and Site Clearance |  |  |  |  | 0
1.1 | In collaboration with the Inspector of Works, and based upon pipe lengths and alignment shown on layout plan, agree upon final alignment of pipelines, road crossings, location of all tees, bends, isolating valves, air valves, washouts, tapstands, and consumer connection offtakes. Set out pipeline centre-lines, survey, agree upon Starting Surfaces, and final lengths and produce final plans at horizontal scale of 1:200 for approval before proceeding further. | LS | 1 |  | 0
1.2 | General Clearance for urban land & rough grass land along pipeline wayleaves (trench width plus 0.5 m on either side) | ha | 0.1 |  | 0
1.3 | Removal of tree stumps within approved alignment. PROVISIONAL SUM | nr | 1 |  | 0
1.4 | Cut down and remove trees and tree stumps within approved alignment only if specifically directed to do so by Inspector of Works following agreement from the Host Community PROVISIONAL SUM | nr | 1 |  | 0
Bill No. 2: Excavation and backfilling of trenches - all pipelines |  |  |  |  | 0
2.1 | Excavate test pits along centre line of proposed pipeline to depth of 1m at least every 50 m | nr | 5 |  | 0
2.2 | Excavate and trim trench bed to depth not exceeding 1 m to ensure minimum cover provided to pipeline is not less than 600 mm | m | 213.3 |  | 0
2.3 | E. O. item 2.2 at road crossings. Excavate and trim trench to additional depth not exceeding 1.5 m to ensure minimum cover provided to the pipeline is 900 mm | m | 23.7 |  | 0
2.4 | Over excavate trench by a further depth of 150mm in areas identified by the Inspector of Works as requiring imported granular backfill RATE ONLY | m3 | 2.133 |  | 0
2.5 | Import, place and compact granular backfill in areas identified by the Inspector of Works as requiring imported granular backfill. RATE ONLY, | m3 | 2.133 |  | 0
2.6 | Place and compact sidefill and backfill using selected excavated material free of stones and tree roots to depth 300 mm above crown of pipe, and after compaction, other excavated material thereafter to final surface | m | 213.3 |  | 0
2.7 | Dispose of all surplus excavated material off-site as directed | LS | 1 |  | 0
Bill No. 3: Supply and Installation of rising main- borehole to elevated water tank |  |  |  |  | 0
All PE compression joints and fittings shall be supplied complete with suitable pipe joint stiffeners. All steel fittings shall be epoxy coated and all nuts and bolts galvanised. Rate shall include supply, lay, bed, joint , pressure test, sterilize and flushing of HDPE pipelines
3.1 | Raw water rising main from borehole to the Elevated Tank , HDPE DN50 (OD 63), SDR17, PN 10 | m | 58 |  | 0
3.2 | Compression fitting, elbow 90o DN 50mm | nr | 1
3.3 | Gate Valve, double flange, handwheel operated 50 mm non-rising spindle type, with 1 No. flanged restraining adapters st. fl. to PE DN 50, installed above ground within tank inlet riser pipe | set | 1 |  | 0
3.4 | Supply and Installation of DN 40 parallel bulk water meter with magnetic transmission and dry recording head , metrological class B, minimum display 1 m3/hr to specification, suitable for vertical mounting, within water tank inlet riser pipe complete with strainer (metallic double flanged body c/w lockable meter box pipe surround). The meter assembly shall comprise: 1 No. DN50 to DN40 reducer, 1 DN40 500mm long straight pipe length, 1 DN 40 mm double flanged vertically mounted parallel bulk type meter, located approximately 1.5 m above ground level, 1 DN 40 250 mm straight pipe length, and one DN40 to DN50 reducer. | set | 1 |  | 0
| Carry forward |  |  |  | 0
| Brought forward |  |  |  | 0
Bill No. 4: Tanks, Tankstands and Tap Stands |  |  |  |  | 0
Bidder shall supply outline details of water tank stand and tank c/w, pipework and fittings.
water tank stand manufacturer:
HDPE cylindrical tank manufacturer:
HDPE cylindrical tank supplier (if different):
Contractor shall supply full set of structural calculations and drawings for water tank stand certified by a registered structural engineer for written approval prior to fabrication.
4.1 | Conduct geotechnical investigations and design foundation and tank stand for the elevated tank | LS | 1 |  | 0
4.2 | Tank reinforced concrete foundations 1 m x 1m x 1.5 m deep inc. excavation, shuttering, concreting, curing, backfilling and disposal of excess spoil material from site | nr | 6 |  | 0
Supply and install 2 No. HDPE cylindrical tank on Contractor designed six vertical members) mild steel tankstand c/w with inlet float valves, all inflow, valved connecting, outflow, overflow, and scour (washout) pipework, fittings, adaptors and 6m high steel stand c/w access ladder and lightning arrestor.
4.3 | Capacity 10m3.(2 no. 5m3 tanks) | nr | 1 |  | 0
4.4 | Supply and paint all mild steel in tank stand with two coats of zinc 82% rich paint in dry film | LS | 1 |  | 0
4.5 | Leak testing and disinfection of tank and pipework | nr | 1 |  | 0
4.6 | Provide & install float level indicator gauge on side of tank readable from ground level adjacent to tank | nr | 1 |  | 0
4.7 | Provide and install chlorine cartridge type inline doser in lockable chamber at start of tank outlet pipe c/w twelve months supply of chlorine cartridges. | LS | 1 |  | 0
4.8 | Provide materials for and construct tap stand and associated drainage | nr | 3 |  | 0
Bill No. 5: Supply and Install Water Distribution Network |  |  |  |  | 0
All PE compression joints and fittings shall be supplied complete with suitable pipe joint stiffeners. All steel fittings shall be epoxy coated and all nuts and bolts galvanised. Rate shall include supply, lay, bed, joint , pressure test, sterilize and flushing of HDPE pipelines
5.1 | Network reticulation pipework HDPE DN50 (OD 63), SDR17, PN 10 | m | 43 |  | 0
5.2 | Equal tee compression fitting DN 50 x 50 x 50 mm | nr | 1 |  | 0
5.3 | Unequal reducing tee compression fitting DN 50 x 50 x 40 mm | nr | 1 |  | 0
5.4 | Compression reducer coupling 50mm x 40mm | nr | 2 |  | 0
5.5 | Compression reducer coupling 50mm x 32mm | nr | 1 |  | 0
5.6 | Compression reducer coupling 40mm x 32mm | nr | 2 |  | 0
5.7 | Network reticulation pipework HDPE DN 40mm, SDR17, PN 10 | m | 125 |  | 0
5.8 | Network reticulation pipework HDPE DN 32mm, SDR17, PN 10 | m | 11 |  | 0
5.9 | Compression fitting, elbow 90o DN 50mm | nr | 2 |  | 0
5.1 | End cap DN 32mm (compression type) | nr | 4 |  | 0
5.11 | Saddle clamp 50mm x 3/4" to supply individual consumer connection to Clinic | nr | 1 |  | 0
5.12 | Supply and install GI pipes 25mm dia c/w fittings to tap stands c/w isolating stop cock | nr | 3 |  | 0
5.13 | Supply and install heavy weight brass garden bib tap (non-lever arm type) | nr | 6 |  | 0
5.14 | Compression tee DN 40 x 40 x 1" male branch to connect to tap stand pipework | nr | 3 |  | 0
5.15 | Gate Valve, double flange, 40 mm non-rising spindle type, with 2 No. flanged restraining adapters st. fl. to PE DN 40, complete with valve riser and valve box to suit | nr | 1 |  | 0
5.16 | Allow for internal plumbing from pipeline to ablution facilities. Prime Cost | sum | 1 | 20000 | 20000
Air valve assembly consisting of 1 No. compression tee with threaded male 1 1/2" branch vertically upwards, 1 No. female to male thr. spigot, 1 No. Stopcock, thr. dble. socket 1", and 1 No. Single air valve, thr. female 1". RATE ONLY
5.17 | Compression tee DN 40 x 40 x 1 1/2" male br., 1 No. female to male 1 1/2" to 1" thr. Spigot | set | 0
| Carry forward |  |  |  | 0
| Brought forward |  |  |  | 0
Bill No. 6: Concrete Works to all Pipelines |  |  |  |  | 0
All unreinforced concrete works shall be in medium strength concrete unless otherwise indicated. Where bends less than 45o are obtained by bending the pipe, radius not less than 35 x pipe diameter, and provided there is no compression joint with 5 metres of either end of radius, no separate thrust block is required.
6.1 | Over excavate in trench bed at all gate valves, air valve assemblies and steel fittings and cast support slab to full width of trench with other dimensions being the length of the valve or the fitting between flanges or between the compression tightening nuts and depth below trench bed of 150 mm | nr | 1 |  | 0
6.2 | At all 45o and 90o bends, pipeline tees, and end caps, provide and subsequently remove shuttering and cast thrust blocks against undisturbed trench bed and trench wall | nr | 7 |  | 0
6.3 | Supply all materials and cast and complete air-valve chamber. RATE ONLY | nr | 1
| Sub-total Bill Nos 1 to 6 |  |  |  | 0
| Contingencies (10%) Bills No 1 to 6 |  |  |  | 0
| Taxes (VAT @16%) Bills Nos 1 to 6 |  |  |  | 0
| Total Bills Nos 1 to 6 |  |  |  | 0
Bill 7A | Electromechanical - OPTION A Solar Powered |  |  |  | 0
Bidder shall supply all the information and rates for both Alternatives for the offer to be considered. Final decision on the main power source (Option A ZESCO mains power from institutions incoming distribution board, or Option B from Solar Array will be confirmed during negotiation prior to award.
proposed submersible hybrid DC/AC pumpset manufacturer and agent:
proposed standby generator manufacturer and agent:
| confirm manufactures brochures included with bid |  | yes / no
No change from these manufacturers or agents shall be permitted without prior written approval from the Consultant
Submersible 48 VDC Borehole Pump
7.1 | Supply and install a hybrid DC/AC borehole submersible pump suitable for a borehole of ID 5" capable of being powered from either a 48 VDC or a nominal 230 VAC source c/w cabled connection to power sources located within 10 m of borehole head, pumping into an overhead tank with top water inlet 14 m above ground.. . |  | nr | 1
Information provided to guide Bidder
| Ground elevation at borehole (approximate) | masl | 973
| Yield | m3/hr | 1
| Pump installation level below ground surface | m | tbc
| Riser pipe diameter | mm | DN 50
| Dynamic water level below ground surface | m | tbc
| Top water level in overhead tank | masl | 988
Information to be provided by Bidder
| Manufacturers Pump reference No. | ref.
| Maximum flow at Installation indicated above | m3/hr
| Maximum pump head at installation indicated above | m3/hr
| Optimum flow at Installation indicated above | m3/hr
| Optimum head at Installation indicated above | m3/hr
| Pump efficiency at installation | %
| Input power required by pump | W
| Output power required by solar array | W
| No. of solar panels and arrays offered and guaranteed to meet requirement | nr
7.2 | Solar arrays to meet requirements c/w security fence and gate and lightning protection as per Drawing to be included in this Option
7.2.1 | Supply, install, erect and connect solar arrays to meet requirements c/w lightning protection as per Drawing and Specification | nr | 1 |  | 0
7.2.2 | Provide all materials and construct fenced and gated compound to contain solar array and associated chambers to Specification. | LS | 1 |  | 0
7.2.3 | Supply and install DN 25 water pipe take-off from rising mainand sgtandpipe for solar cleansing system | LS | 1 |  | 0
7.2.4 | Provide solar array cleansing step ladder and extendable washer to Specification | LS | 1 |  | 0
Supply and Installation of 220 VAC standby generator of rated power
7.3 | Supply, Install and connect by manually operated changeover switch standby generator capable of providing the VAC power required to operate the submersible borehole pump as specified above at half-load c/w roofed lockable waterproof steel protection cabinet. | nr | 1 |  | 0
Information to be provided by Bidder
Manufacturers Generator Set reference No.
| Output kVA at 1500rpm, 220V, single-phase, 50Hz, with power factor of 1.0 | kVA
| Fuel type (petrol/diesel) | type
| Fuel tank capacity | l
Air or water cooled
7.4 | External 230 VAC Power Source to be included in Option B
| Sub-total Bill No 7A |  |  |  | 0
| Contingencies (10%) Bill No 7A |  |  |  | 0
| Taxes (VAT @16%) Bill No 7A |  |  |  | 0
| Total Bill No 7A |  |  |  | 0
Bill 7B | Electromechanical - OPTION B Mains electric powered |  |  |  | 0
Bidder shall supply all the information and rates for both Alternatives for the offer to be considered. Final decision on the main power source (Option A ZESCO mains power from institutions incoming distribution board, or Option B from Solar Array will be confirmed during negotiation prior to award.
proposed submersible hybrid DC/AC pumpset manufacturer and agent:
proposed standby generator manufacturer and agent:
| confirm manufactures brochures included with bid |  | yes / no
No change from these manufacturers or agents shall be permitted without prior written approval from the Consultant
Submersible 48 VDC Borehole Pump
7.1 | Supply and install a hybrid DC/AC borehole submersible pump suitable for a borehole of ID 5" capable of being powered from either a 48 VDC or a nominal 230 VAC source c/w cabled connection to power sources located within 10 m of borehole head, pumping into an overhead tank with top water inlet 14 m above ground.. . |  | nr | 1
Information provided to guide Bidder
| Ground elevation at borehole (approximate) | masl | 973
| Yield | m3/hr | 1
| Pump installation level below ground surface | m | tbc
| Riser pipe diameter | mm | DN 50
| Dynamic water level below ground surface | m | tbc
| Top water level in overhead tank | masl | 988
Information to be provided by Bidder
| Manufacturers Pump reference No. | ref.
| Maximum flow at Installation indicated above | m3/hr
| Maximum pump head at installation indicated above | m3/hr
| Optimum flow at Installation indicated above | m3/hr
| Optimum head at Installation indicated above | m3/hr
| Pump efficiency at installation | %
| Input power required by pump | W
| Output power required by solar array | W
| No. of solar panels and arrays offered and guaranteed to meet requirement | nr
7.2 | Solar arrays to be included in Option A
Supply and Installation of 220 VAC standby generator of rated power
7.3 | Supply, Install and connect by manually operated changeover switch standby generator capable of providing the VAC power required to operate the submersible borehole pump as specified above at half-load c/w roofed lockable waterproof steel protection cabinet. | nr | 1 |  | 0
Information to be provided by Bidder
Manufacturers Generator Set reference No.
| Output kVA at 1500rpm, 220V, single-phase, 50Hz, with power factor of 1.0 | kVA
| Fuel type (petrol/diesel) | type
| Fuel tank capacity | l
Air or water cooled
External 230 VAC Power Source
7.4 | Underground armoured cable c/w all internal building works, and making good, outside excavation, backfilling and protective concrete cover slabs from Main Distribution Board |  | 0
7.4.1 | All ancilliary work excludng outside excavation, and backfilling, supply and installation of underground armoured cable and protective concrete cover slabs | nr | 1 |  | 0
7.4.2 | External excavation, and backfilling, supply and installation of underground armoured cable and protective concrete cover slabs, minimum cover to cable 600 mm. Length subject to reconfirmation prior to award. | m | 90 |  | 0
| Sub-total Bill No 7B |  |  |  | 0
| Contingencies (10%) Bill No 7B |  |  |  | 0
| Taxes (VAT @16%) Bill No 7B |  |  |  | 0
| Total Bill No 7B |  |  |  | 0

## Kaputa R. Centre
UNICEF
Solar Powered Borehole Schemes in institutions in Nchelenge (Mantapala) Refugee Camp & Host Communities
Kaputa Reception Centre
Bill No. TC1:
Item | Description | Unit | Qty | Rate (ZMW) | Amount (ZMW)
Bill No. out, Demolition and Site Clearance |  |  |  |  | 0
1.1 | In collaboration with the Inspector of Works, and based upon pipe lengths and alignment shown on layout plan, agree upon final alignment of pipelines, road crossings, location of all tees, bends, isolating valves, air valves, washouts, tapstands, and consumer connection offtakes. Set out pipeline centre-lines, survey, agree upon Starting Surfaces, and final lengths and produce final plans at horizontal scale of 1:200 for approval before proceeding further. | LS | 1 |  | 0
1.2 | General Clearance for urban land & rough grass land along pipeline wayleaves (trench width plus 0.5 m on either side) | ha | 0.1 |  | 0
1.3 | Removal of tree stumps within approved alignment. PROVISIONAL SUM | nr | 1 |  | 0
1.4 | Cut down and remove trees and tree stumps within approved alignment only if specifically directed to do so by Inspector of Works following agreement from the Host Community PROVISIONAL SUM | nr | 1 |  | 0
Bill No. 2: Excavation and backfilling of trenches - all pipelines |  |  |  |  | 0
2.1 | Excavate test pits along centre line of proposed pipeline to depth of 1m at least every 50 m | nr | 4 |  | 0
2.2 | Excavate and trim trench bed to depth not exceeding 1 m to ensure minimum cover provided to pipeline is not less than 600 mm | m | 155.7 |  | 0
2.3 | E. O. item 2.2 at road crossings. Excavate and trim trench to additional depth not exceeding 1.5 m to ensure minimum cover provided to the pipeline is 900 mm | m | 17.3 |  | 0
2.4 | Over excavate trench by a further depth of 150mm in areas identified by the Inspector of Works as requiring imported granular backfill RATE ONLY | m3 | 1.557 |  | 0
2.5 | Import, place and compact granular backfill in areas identified by the Inspector of Works as requiring imported granular backfill. RATE ONLY, | m3 | 1.557 |  | 0
2.6 | Place and compact sidefill and backfill using selected excavated material free of stones and tree roots to depth 300 mm above crown of pipe, and after compaction, other excavated material thereafter to final surface | m | 155.7 |  | 0
2.7 | Dispose of all surplus excavated material off-site as directed | LS | 1 |  | 0
Bill No. 3: Supply and Installation of rising main- borehole to elevated water tank |  |  |  |  | 0
All PE compression joints and fittings shall be supplied complete with suitable pipe joint stiffeners. All steel fittings shall be epoxy coated and all nuts and bolts galvanised. Rate shall include supply, lay, bed, joint , pressure test, sterilize and flushing of HDPE pipelines
3.1 | Raw water rising main from borehole to the Elevated Tank , HDPE DN50 (OD 63), SDR17, PN 10 | m | 13 |  | 0
3.2 | Gate Valve, double flange, handwheel operated 50 mm non-rising spindle type, with 1 No. flanged restraining adapters st. fl. to PE DN 50, installed above ground within tank inlet riser pipe | set | 1 |  | 0
3.3 | Supply and Installation of DN 40 parallel bulk water meter with magnetic transmission and dry recording head , metrological class B, minimum display 1 m3/hr to specification, suitable for vertical mounting, within water tank inlet riser pipe complete with strainer (metallic double flanged body c/w lockable meter box pipe surround). The meter assembly shall comprise: 1 No. DN50 to DN40 reducer, 1 DN40 500mm long straight pipe length, 1 DN 40 mm double flanged vertically mounted parallel bulk type meter, located approximately 1.5 m above ground level, 1 DN 40 250 mm straight pipe length, and one DN40 to DN50 reducer. | set | 1 |  | 0
3.4 | Provide all materials and construct fenced and gated compound to contain solar array and associated chambers to Specification. | LS | 1 |  | 0
3.5 | Supply and install DN 25 water pipe take-off from rising mainand sgtandpipe for solar cleansing system | LS | 1 |  | 0
3.6 | Provide solar array cleansing step ladder and extendable washer to Specification | LS | 1 |  | 0
| Carry forward |  |  |  | 0
| Brought forward |  |  |  | 0
Bill No. 4: Tanks, Tankstands and Tap Stands |  |  |  |  | 0
Bidder shall supply outline details of water tank stand and tank c/w, pipework and fittings.
water tank stand manufacturer:
HDPE cylindrical tank manufacturer:
HDPE cylindrical tank supplier (if different):
Contractor shall supply full set of structural calculations and drawings for water tank stand certified by a registered structural engineer for written approval prior to fabrication.
4.1 | Conduct geotechnical investigations and design foundation and tank stand for the elevated tank | LS | 1 |  | 0
4.2 | Tank reinforced concrete foundations 1 m x 1m x 1.5 m deep inc. excavation, shuttering, concreting, curing, backfilling and disposal of excess spoil material from site | nr | 4 |  | 0
Supply and install 1 No. HDPE cylindrical tank on Contractor designed mild steel tankstand c/w with inlet float valve, all inflow, outflow, overflow, and scour (washout) pipework, fittings, adaptors and 6m high steel stand c/w access ladder and lightning arrestor.
4.3 | Capacity 5m3. | nr | 1 |  | 0
4.4 | Supply and paint all mild steel in tank stand with two coats of zinc 82% rich paint in dry film | LS | 1 |  | 0
4.5 | Leak testing and disinfection of tank and pipework | nr | 1 |  | 0
4.6 | Provide & install float level indicator gauge on side of tank readable from ground level adjacent to tank | nr | 1 |  | 0
4.7 | Provide and install chlorine cartridge type inline doser in lockable chamber at start of tank outlet pipe c/w twelve months supply of chlorine cartridges. | LS | 1 |  | 0
4.8 | Provide materials for and construct tap stand and associated drainage | nr | 3 |  | 0
Bill No. 5: Supply and Install Water Distribution Network |  |  |  |  | 0
All PE compression joints and fittings shall be supplied complete with suitable pipe joint stiffeners. All steel fittings shall be epoxy coated and all nuts and bolts galvanised. Rate shall include supply, lay, bed, joint , pressure test, sterilize and flushing of HDPE pipelines
5.1 | Network reticulation pipework HDPE DN 32mm, SDR17, PN 10 | m | 160 |  | 0
5.2 | Compression fitting, elbow 45o DN 32mm | nr | 1 |  | 0
5.3 | Compression fitting, elbow 90o DN 50mm | nr | 3 |  | 0
5.4 | End cap DN 32mm (compression type) | nr | 2 |  | 0
5.5 | Supply and install GI pipes 25mm dia c/w fittings to tap stands c/w isolating stop cock | nr | 3 |  | 0
5.6 | Supply and install heavy weight brass garden bib tap (non-lever arm type) | nr | 6 |  | 0
5.7 | Compression tee DN 32 x 32 x 1" male branch to connect to tap stand pipework | nr | 3 |  | 0
5.8 | Gate Valve, double flange, 40 mm non-rising spindle type, with 2 No. flanged restraining adapters st. fl. to PE DN 40, complete with valve riser and valve box to suit | nr | 1 |  | 0
Air valve assembly consisting of 1 No. compression tee with threaded male 1 1/2" branch vertically upwards, 1 No. female to male thr. spigot, 1 No. Stopcock, thr. dble. socket 1", and 1 No. Single air valve, thr. female 1". RATE ONLY
5.9 | Compression tee DN 32 x 32 x 1" male br, 1 No. female to male 1" to 1" thr. spigot | set | 1
| Carry forward |  |  |  | 0
| Brought forward |  |  |  | 0
Bill No. 6: Concrete Works to all Pipelines |  |  |  |  | 0
All unreinforced concrete works shall be in medium strength concrete unless otherwise indicated. Where bends less than 45o are obtained by bending the pipe, radius not less than 35 x pipe diameter, and provided there is no compression joint with 5 metres of either end of radius, no separate thrust block is required.
6.1 | Over excavate in trench bed at all gate valves, air valve assemblies and steel fittings and cast support slab to full width of trench with other dimensions being the length of the valve or the fitting between flanges or between the compression tightening nuts and depth below trench bed of 150 mm | nr | 1 |  | 0
6.2 | At all 45o and 90o bends, pipeline tees, and end caps, provide and subsequently remove shuttering and cast thrust blocks against undisturbed trench bed and trench wall | nr | 6 |  | 0
6.3 | Supply all materials and cast and complete air-valve chamber. RATE ONLY | nr | 1
Bill No. 7: Water Distribution Network | Electromechanical |  |  |  | 0
Bidder shall supply details of proposed pumpset c/w shroud, and standby generator for which there shall be a local agent
proposed submersible hybrid DC/AC pumpset manufacturer and agent:
proposed standby generator manufacturer and agent:
| confirm manufactures brochures included with bid |  | yes / no
No change from these manufacturers or agents shall be permitted without prior written approval from the Consultant
Submersible 48 VDC Borehole Pump
7.1 | Supply and install a hybrid DC/AC borehole submersible pump suitable for a borehole of ID 5" capable of being powered from either a 48 VDC or a nominal 230 VAC source c/w cabled connection to power sources located within 10 m of borehole head, pumping into an overhead tank with top water inlet 14 m above ground.. . |  | nr | 1
Information provided to guide Bidder
| Ground elevation at borehole (approximate) | masl | 969
| Yield | m3/hr | 0.5
| Pump installation level below ground surface | m | 75
| Riser pipe diameter | mm | DN 50
| Dynamic water level below ground surface | m | 69.5
| Top water level in overhead tank | masl | 983
Information to be provided by Bidder
| Manufacturers Pump reference No. | ref.
| Maximum flow at Installation indicated above | m3/hr
| Maximum pump head at installation indicated above | m3/hr
| Optimum flow at Installation indicated above | m3/hr
| Optimum head at Installation indicated above | m3/hr
| Pump efficiency at installation | %
| Input power required by pump | W
| Output power required by solar array | W
| No. of solar panels and arrays offered and guaranteed to meet requirement | nr
7.2 | Supply, install, erect and connect solar arrays to meet requirements c/w lightning protection as per Drawing | LS | 1 |  | 0
Supply and Installation of 220 VAC standby generator of rated power
7.3 | Supply, Install and connect by manually operated changeover switch standby generator capable of providing the VAC power required to operate the submersible borehole pump as specified above at half-load c/w roofed lockable waterproof steel protection cabinet. | nr | 1 |  | 0
Information to be provided by Bidder
Manufacturers Generator Set reference No.
| Output kVA at 1500rpm, 220V, single-phase, 50Hz, with power factor of 1.0 | kVA
| Fuel type (petrol/diesel) | type
| Fuel tank capacity | l
Air or water cooled
| Sub-total |  |  |  | 0
| Contingencies (10%) |  |  |  | 0
| Taxes (VAT @16%) |  |  |  | 0
| Total |  |  |  | 0
Note on C26: Baker: parallel or vertical Woltman meter?

## Lambwe Chomba RC
UNICEF
Solar Powered Borehole Schemes in institutions in Nchelenge (Mantapala) Refugee Camp & Host Communities
Lambwe Chomba Reception Centre
Bill No. TC2
Item | Description | Unit | Qty | Rate (ZMW) | Amount (ZMW)
Bill No. out, Demolition and Site Clearance |  |  |  |  | 0
1.1 | In collaboration with the Inspector of Works, and based upon pipe lengths and alignment shown on layout plan, agree upon final alignment of pipelines, road crossings, location of all tees, bends, isolating valves, air valves, washouts, tapstands, and consumer connection offtakes. Set out pipeline centre-lines, survey, agree upon Starting Surfaces, and final lengths and produce final plans at horizontal scale of 1:200 for approval before proceeding further. | LS | 1 |  | 0
1.2 | General Clearance for urban land & rough grass land along pipeline wayleaves (trench width plus 0.5 m on either side) | ha | 0.1 |  | 0
1.3 | Removal of tree stumps within approved alignment. PROVISIONAL SUM | nr | 1 |  | 0
1.4 | Cut down and remove trees and tree stumps within approved alignment only if specifically directed to do so by Inspector of Works following agreement from the Host Community PROVISIONAL SUM | nr | 1 |  | 0
Bill No. 2: Excavation and backfilling of trenches - all pipelines |  |  |  |  | 0
2.1 | Excavate test pits along centre line of proposed pipeline to depth of 1m at least every 50 m | nr | 5 |  | 0
2.2 | Excavate and trim trench bed to depth not exceeding 1 m to ensure minimum cover provided to pipeline is not less than 600 mm | m | 213.3 |  | 0
2.3 | E. O. item 2.2 at road crossings. Excavate and trim trench to additional depth not exceeding 1.5 m to ensure minimum cover provided to the pipeline is 900 mm | m | 23.7 |  | 0
2.4 | Over excavate trench by a further depth of 150mm in areas identified by the Inspector of Works as requiring imported granular backfill RATE ONLY | m3 | 2.133 |  | 0
2.5 | Import, place and compact granular backfill in areas identified by the Inspector of Works as requiring imported granular backfill. RATE ONLY, | m3 | 2.133 |  | 0
2.6 | Place and compact sidefill and backfill using selected excavated material free of stones and tree roots to depth 300 mm above crown of pipe, and after compaction, other excavated material thereafter to final surface | m | 213.3 |  | 0
2.7 | Dispose of all surplus excavated material off-site as directed | LS | 1 |  | 0
Bill No. 3: Supply and Installation of rising main- borehole to elevated water tank |  |  |  |  | 0
All PE compression joints and fittings shall be supplied complete with suitable pipe joint stiffeners. All steel fittings shall be epoxy coated and all nuts and bolts galvanised. Rate shall include supply, lay, bed, joint , pressure test, sterilize and flushing of HDPE pipelines
3.1 | Raw water rising main from borehole to the Elevated Tank , HDPE DN50 (OD 63), SDR17, PN 10 | m | 21 |  | 0
3.2 | Gate Valve, double flange, handwheel operated 50 mm non-rising spindle type, with 1 No. flanged restraining adapters st. fl. to PE DN 50, installed above ground within tank inlet riser pipe | set | 1 |  | 0
3.3 | Supply and Installation of DN 40 parallel bulk water meter with magnetic transmission and dry recording head , metrological class B, minimum display 1 m3/hr to specification, suitable for vertical mounting, within water tank inlet riser pipe complete with strainer (metallic double flanged body c/w lockable meter box pipe surround). The meter assembly shall comprise: 1 No. DN50 to DN40 reducer, 1 DN40 500mm long straight pipe length, 1 DN 40 mm double flanged vertically mounted parallel bulk type meter, located approximately 1.5 m above ground level, 1 DN 40 250 mm straight pipe length, and one DN40 to DN50 reducer. | set | 1 |  | 0
3.4 | Provide all materials and construct fenced and gated compound to contain solar array and associated chambers to Specification. | LS | 1 |  | 0
3.5 | Supply and install DN 25 water pipe take-off from rising mainand sgtandpipe for solar cleansing system | LS | 1 |  | 0
3.6 | Provide solar array cleansing step ladder and extendable washer to Specification | LS | 1 |  | 0
| Carry forward |  |  |  | 0
| Brought forward |  |  |  | 0
Bill No. 4: Tanks, Tankstands and Tap Stands |  |  |  |  | 0
Bidder shall supply outline details of water tank stand and tank c/w, pipework and fittings.
water tank stand manufacturer:
HDPE cylindrical tank manufacturer:
HDPE cylindrical tank supplier (if different):
Contractor shall supply full set of structural calculations and drawings for water tank stand certified by a registered structural engineer for written approval prior to fabrication.
4.1 | Conduct geotechnical investigations and design foundation and tank stand for the elevated tank | LS | 1 |  | 0
4.2 | Tank reinforced concrete foundations 1 m x 1m x 1.5 m deep inc. excavation, shuttering, concreting, curing, backfilling and disposal of excess spoil material from site | nr | 4 |  | 0
Supply and install 1 No. HDPE cylindrical tank on Contractor designed mild steel tankstand c/w with inlet float valve, all inflow, outflow, overflow, and scour (washout) pipework, fittings, adaptors and 6m high steel stand c/w access ladder and lightning arrestor.
4.3 | Capacity 5m3. | nr | 1 |  | 0
4.4 | Supply and paint all mild steel in tank stand with two coats of zinc 82% rich paint in dry film | LS | 1 |  | 0
4.5 | Leak testing and disinfection of tank and pipework | nr | 1 |  | 0
4.6 | Provide & install float level indicator gauge on side of tank readable from ground level adjacent to tank | nr | 1 |  | 0
4.7 | Provide and install chlorine cartridge type inline doser in lockable chamber at start of tank outlet pipe c/w twelve months supply of chlorine cartridges. | LS | 1 |  | 0
4.8 | Provide materials for and construct tap stand and associated drainage | nr | 4 |  | 0
Bill No. 5: Supply and Install Water Distribution Network |  |  |  |  | 0
All PE compression joints and fittings shall be supplied complete with suitable pipe joint stiffeners. All steel fittings shall be epoxy coated and all nuts and bolts galvanised. Rate shall include supply, lay, bed, joint , pressure test, sterilize and flushing of HDPE pipelines
5.1 | Equal tee compression fitting DN 32 x 32 x 32 mm | nr | 1 |  | 0
5.2 | Network reticulation pipework HDPE DN 32mm, SDR17, PN 10 | m | 216 |  | 0
5.3 | Compression fitting, elbow 90o DN 32mm | nr | 3 |  | 0
5.4 | End cap DN 32mm (compression type) | nr | 2 |  | 0
5.5 | Supply and install GI pipes 25mm dia c/w fittings to tap stands c/w isolating stop cock | nr | 4 |  | 0
5.6 | Supply and install heavy weight brass garden bib tap (non-lever arm type) | nr | 8 |  | 0
5.7 | Compression tee DN 32 x 32 x 1" male branch to connect to tap stand pipework | nr | 4 |  | 0
5.8 | Gate Valve, double flange, 40 mm non-rising spindle type, with 2 No. flanged restraining adapters st. fl. to PE DN 40, complete with valve riser and valve box to suit | nr | 1 |  | 0
Air valve assembly consisting of 1 No. compression tee with threaded male 1 1/2" branch vertically upwards, 1 No. female to male thr. spigot, 1 No. Stopcock, thr. dble. socket 1", and 1 No. Single air valve, thr. female 1". RATE ONLY
5.9 | Compression tee DN 32 x 32 x 1" male br, 1 No. female to male 1" to 1" thr. spigot | set | 1
| Carry forward |  |  |  | 0
| Brought forward |  |  |  | 0
Bill No. 6: Concrete Works to all Pipelines |  |  |  |  | 0
All unreinforced concrete works shall be in medium strength concrete unless otherwise indicated. Where bends less than 45o are obtained by bending the pipe, radius not less than 35 x pipe diameter, and provided there is no compression joint with 5 metres of either end of radius, no separate thrust block is required.
6.1 | Over excavate in trench bed at all gate valves, air valve assemblies and steel fittings and cast support slab to full width of trench with other dimensions being the length of the valve or the fitting between flanges or between the compression tightening nuts and depth below trench bed of 150 mm | nr | 1 |  | 0
6.2 | At all 45o and 90o bends, pipeline tees, and end caps, provide and subsequently remove shuttering and cast thrust blocks against undisturbed trench bed and trench wall, as shown on Standard Drawing | nr | 6 |  | 0
6.3 | Supply all materials and cast and complete air-valve chamber. RATE ONLY | nr | 1
Bill No. 7: Water Distribution Network | Electromechanical |  |  |  | 0
Bidder shall supply details of proposed pumpset c/w shroud, and standby generator for which there shall be a local agent
proposed submersible hybrid DC/AC pumpset manufacturer and agent:
proposed standby generator manufacturer and agent:
| confirm manufactures brochures included with bid |  | yes / no
No change from these manufacturers or agents shall be permitted without prior written approval from the Consultant
Submersible 48 VDC Borehole Pump
7.1 | Supply and install a hybrid DC/AC borehole submersible pump suitable for a borehole of ID 5" capable of being powered from either a 48 VDC or a nominal 230 VAC source c/w cabled connection to power sources located within 10 m of borehole head, pumping into an overhead tank with top water inlet 14 m above ground.. . |  | nr | 1
Information provided to guide Bidder
| Ground elevation at borehole (approximate) | masl | 993
| Yield | m3/hr | tbc
| Pump installation level below ground surface | m | tbc
| Riser pipe diameter | mm | DN 50
| Dynamic water level below ground surface | m | tbc
| Top water level in overhead tank | masl | 1009
Information to be provided by Bidder
| Manufacturers Pump reference No. | ref.
| Maximum flow at Installation indicated above | m3/hr
| Maximum pump head at installation indicated above | m3/hr
| Optimum flow at Installation indicated above | m3/hr
| Optimum head at Installation indicated above | m3/hr
| Pump efficiency at installation | %
| Input power required by pump | W
| Output power required by solar array | W
| No. of solar panels and arrays offered and guaranteed to meet requirement | nr
7.2 | Supply, install, erect and connect solar arrays to meet requirements c/w lightning protection as per Drawing | LS | 1 |  | 0
Supply and Installation of 220 VAC standby generator of rated power
7.3 | Supply, Install and connect by manually operated changeover switch standby generator capable of providing the VAC power required to operate the submersible borehole pump as specified above at half-load c/w roofed lockable waterproof steel protection cabinet. | nr | 1 |  | 0
Information to be provided by Bidder
Manufacturers Generator Set reference No.
| Output kVA at 1500rpm, 220V, single-phase, 50Hz, with power factor of 1.0 | kVA
| Fuel type (petrol/diesel) | type
| Fuel tank capacity | l
Air or water cooled
External 230 VAC Power Source
7.4.1 | By underground armoured cable c/w all excavation, backfilling and protective concrete cover slabs from LV side of ZESCO step down transformer | m | 0
7.4.2 | By underground armoured cable c/w all internal building works, and making good, outside excavation, backfilling and protective concrete cover slabs from Main Distribution Board | m | 100 |  | 0
7.5 | By overhead single phase 230 VAC power line from LV side of ZESCO step-down transformer, c/w all necessary intermediate power poles | m | 0
| Sub-total |  |  |  | 0
| Contingencies (10%) |  |  |  | 0
| Taxes (VAT @16%) |  |  |  | 0
| Total |  |  |  | 0
Note on C26: Baker: parallel or vertical Woltman meter?

## Lupiya R Centre
UNICEF
Solar Powered Borehole Schemes in institutions in Nchelenge (Mantapala) Refugee Camp & Host Communities
Lupiya Reception Centre
Bill No. TC3:
| Item | Description | Unit | Qty | Rate (ZMW) | Amount (ZMW)
| Bill No. out, Demolition and Site Clearance |  |  |  |  | 0
| 1.1 | In collaboration with the Inspector of Works, and based upon pipe lengths and alignment shown on layout plan, agree upon final alignment of pipelines, road crossings, location of all tees, bends, isolating valves, air valves, washouts, tapstands, and consumer connection offtakes. Set out pipeline centre-lines, survey, agree upon Starting Surfaces, and final lengths and produce final plans at horizontal scale of 1:200 for approval before proceeding further. | LS | 1 |  | 0
| 1.2 | General Clearance for urban land & rough grass land along pipeline wayleaves (trench width plus 0.5 m on either side) | ha | 0.1 |  | 0
| 1.3 | Removal of tree stumps within approved alignment. PROVISIONAL SUM | nr | 1 |  | 0
| 1.4 | Cut down and remove trees and tree stumps within approved alignment only if specifically directed to do so by Inspector of Works following agreement from the Host Community PROVISIONAL SUM | nr | 1 |  | 0
| Bill No. 2: Excavation and backfilling of trenches - all pipelines |  |  |  |  | 0
| 2.1 | Excavate test pits along centre line of proposed pipeline to depth of 1m at least every 50 m | nr | 9 |  | 0
| 2.2 | Excavate and trim trench bed to depth not exceeding 1 m to ensure minimum cover provided to pipeline is not less than 600 mm | m | 378 |  | 0
| 2.3 | E. O. item 2.2 at road crossings. Excavate and trim trench to additional depth not exceeding 1.5 m to ensure minimum cover provided to the pipeline is 900 mm | m | 42 |  | 0
| 2.4 | Over excavate trench by a further depth of 150mm in areas identified by the Inspector of Works as requiring imported granular backfill RATE ONLY | m3 | 3.78 |  | 0
| 2.5 | Import, place and compact granular backfill in areas identified by the Inspector of Works as requiring imported granular backfill. RATE ONLY, | m3 | 3.78 |  | 0
| 2.6 | Place and compact sidefill and backfill using selected excavated material free of stones and tree roots to depth 300 mm above crown of pipe, and after compaction, other excavated material thereafter to final surface | m | 378 |  | 0
| 2.7 | Dispose of all surplus excavated material off-site as directed | LS | 1 |  | 0
| Bill No. 3: Supply and Installation of rising main- borehole to elevated water tank |  |  |  |  | 0
All PE compression joints and fittings shall be supplied complete with suitable pipe joint stiffeners. All steel fittings shall be epoxy coated and all nuts and bolts galvanised. Rate shall include supply, lay, bed, joint , pressure test, sterilize and flushing of HDPE pipelines
| 3.1 | Raw water rising main from borehole to the Elevated Tank , HDPE DN50 (OD 63), SDR17, PN 10 | m | 133 |  | 0
| 3.2 | Compression fitting, elbow 90o DN 50mm | nr | 1
| 3.3 | Gate Valve, double flange, handwheel operated 50 mm non-rising spindle type, with 1 No. flanged restraining adapters st. fl. to PE DN 50, installed above ground within tank inlet riser pipe | set | 1 |  | 0
| 3.4 | Supply and Installation of DN 40 parallel bulk water meter with magnetic transmission and dry recording head , metrological class B, minimum display 1 m3/hr to specification, suitable for vertical mounting, within water tank inlet riser pipe complete with strainer (metallic double flanged body c/w lockable meter box pipe surround). The meter assembly shall comprise: 1 No. DN50 to DN40 reducer, 1 DN40 500mm long straight pipe length, 1 DN 40 mm double flanged vertically mounted parallel bulk type meter, located approximately 1.5 m above ground level, 1 DN 40 250 mm straight pipe length, and one DN40 to DN50 reducer. | set | 1 |  | 0
| 3.5 | Provide all materials and construct fenced and gated compound to contain solar array and associated chambers to Specification. | LS | 1 |  | 0
| 3.6 | Supply and install DN 25 water pipe take-off from rising mainand sgtandpipe for solar cleansing system | LS | 1 |  | 0
| 3.7 | Provide solar array cleansing step ladder and extendable washer to Specification | LS | 1 |  | 0
|  | Carry forward |  |  |  | 0
|  | Brought forward |  |  |  | 0
| Bill No. 4: Tanks, Tankstands and Tap Stands |  |  |  |  | 0
Bidder shall supply outline details of water tank stand and tank c/w, pipework and fittings.
water tank stand manufacturer:
HDPE cylindrical tank manufacturer:
HDPE cylindrical tank supplier (if different):
Contractor shall supply full set of structural calculations and drawings for water tank stand certified by a registered structural engineer for written approval prior to fabrication.
| 4.1 | Conduct geotechnical investigations and design foundation and tank stand for the elevated tank | LS | 1 |  | 0
| 4.2 | Tank reinforced concrete foundations 1 m x 1m x 1.5 m deep inc. excavation, shuttering, concreting, curing, backfilling and disposal of excess spoil material from site | nr | 6 |  | 0
Supply and install 2 No. HDPE cylindrical tank on Contractor designed six vertical members) mild steel tankstand c/w with inlet float valves, all inflow, valved connecting, outflow, overflow, and scour (washout) pipework, fittings, adaptors and 6m high steel stand c/w access ladder and lightning arrestor.
| 4.3 | Capacity 10m3. (2no. 5m3 tanks) | nr | 1 |  | 0
| 4.4 | Supply and paint all mild steel in tank stand with two coats of zinc 82% rich paint in dry film | LS | 1 |  | 0
| 4.5 | Leak testing and disinfection of tank and pipework | nr | 1 |  | 0
| 4.6 | Provide & install float level indicator gauge on side of tank readable from ground level adjacent to tank | nr | 1 |  | 0
| 4.7 | Provide and install chlorine cartridge type inline doser in lockable chamber at start of tank outlet pipe c/w twelve months supply of chlorine cartridges. | LS | 1 |  | 0
| 4.8 | Provide materials for and construct tap stand and associated drainage | nr | 4 |  | 0
| Bill No. 5: Supply and Install Water Distribution Network |  |  |  |  | 0
All PE compression joints and fittings shall be supplied complete with suitable pipe joint stiffeners. All steel fittings shall be epoxy coated and all nuts and bolts galvanised. Rate shall include supply, lay, bed, joint , pressure test, sterilize and flushing of HDPE pipelines
| 5.1 | Equal tee compression fitting DN 32 x 32 x 32 mm | nr | 2 |  | 0
| 5.2 | Network reticulation pipework HDPE DN 32mm, SDR17, PN 10 | m | 287 |  | 0
| 5.3 | Compression fitting, elbow 45o DN 32mm | nr | 3 |  | 0
| 5.4 | Compression fitting, elbow 90o DN 32mm | nr | 3 |  | 0
| 5.5 | End cap DN 32mm (compression type) | nr | 4 |  | 0
| 5.6 | Supply and install GI pipes 25mm dia c/w fittings to tap stands c/w isolating stop cock | nr | 4 |  | 0
| 5.7 | Supply and install heavy weight brass garden bib tap (non-lever arm type) | nr | 8 |  | 0
| 5.8 | Compression tee DN 32 x 32 x 1" male branch to connect to tap stand pipework | nr | 4 |  | 0
| 5.9 | Gate Valve, double flange, 40 mm non-rising spindle type, with 2 No. flanged restraining adapters st. fl. to PE DN 40, complete with valve riser and valve box to suit | nr | 1 |  | 0
Air valve assembly consisting of 1 No. compression tee with threaded male 1 1/2" branch vertically upwards, 1 No. female to male thr. spigot, 1 No. Stopcock, thr. dble. socket 1", and 1 No. Single air valve, thr. female 1". RATE ONLY
| 5.1 | Compression tee DN 32 x 32 x 1" male br, 1 No. female to male 1" to 1" thr. spigot | set | 0
|  | Carry forward |  |  |  | 0
|  | Brought forward |  |  |  | 0
| Bill No. 6: Concrete Works to all Pipelines |  |  |  |  | 0
All unreinforced concrete works shall be in medium strength concrete unless otherwise indicated. Where bends less than 45o are obtained by bending the pipe, radius not less than 35 x pipe diameter, and provided there is no compression joint with 5 metres of either end of radius, no separate thrust block is required.
6.1 | 6.1 | Over excavate in trench bed at all gate valves, air valve assemblies and steel fittings and cast support slab to full width of trench with other dimensions being the length of the valve or the fitting between flanges or between the compression tightening nuts and depth below trench bed of 150 mm | nr | 1 |  | 0
| 6.2 | At all 45o and 90o bends, pipeline tees, and end caps, provide and subsequently remove shuttering and cast thrust blocks against undisturbed trench bed and trench wall | nr | 8 |  | 0
| 6.3 | Supply all materials and cast and complete air-valve chamber. RATE ONLY | nr | 1
| Bill No. 7: Water Distribution Network | Electromechanical |  |  |  | 0
Bidder shall supply details of proposed pumpset c/w shroud, and standby generator for which there shall be a local agent
proposed submersible hybrid DC/AC pumpset manufacturer and agent:
proposed standby generator manufacturer and agent:
|  | confirm manufactures brochures included with bid |  | yes / no
No change from these manufacturers or agents shall be permitted without prior written approval from the Consultant
Submersible 48 VDC Borehole Pump
| 7.1 | Supply and install a hybrid DC/AC borehole submersible pump suitable for a borehole of ID 5" capable of being powered from either a 48 VDC or a nominal 230 VAC source c/w cabled connection to power sources located within 10 m of borehole head, pumping into an overhead tank with top water inlet 14 m above ground.. . |  | nr | 1
Information provided to guide Bidder
|  | Ground elevation at borehole (approximate) | masl | 943
|  | Yield | m3/hr | 0.5
|  | Pump installation level below ground surface | m | 41
|  | Riser pipe diameter | mm | DN 50
|  | Dynamic water level below ground surface | m | 18.93
|  | Top water level in overhead tank | masl | 958
Information to be provided by Bidder
|  | Manufacturers Pump reference No. | ref.
|  | Maximum flow at Installation indicated above | m3/hr
|  | Maximum pump head at installation indicated above | m3/hr
|  | Optimum flow at Installation indicated above | m3/hr
|  | Optimum head at Installation indicated above | m3/hr
|  | Pump efficiency at installation | %
|  | Input power required by pump | W
|  | Output power required by solar array | W
|  | No. of solar panels and arrays offered and guaranteed to meet requirement | nr
| 7.2 | Supply, install, erect and connect solar arrays to meet requirements c/w lightning protection as per Drawing | LS | 1 |  | 0
Supply and Installation of 220 VAC standby generator of rated power
| 7.3 | Supply, Install and connect by manually operated changeover switch standby generator capable of providing the VAC power required to operate the submersible borehole pump as specified above at half-load c/w roofed lockable waterproof steel protection cabinet. | nr | 1 |  | 0
Information to be provided by Bidder
Manufacturers Generator Set reference No.
|  | Output kVA at 1500rpm, 220V, single-phase, 50Hz, with power factor of 1.0 | kVA
|  | Fuel type (petrol/diesel) | type
|  | Fuel tank capacity | l
Air or water cooled
External 230 VAC Power Source
| 7.4.1 | By underground armoured cable c/w all excavation, backfilling and protective concrete cover slabs from LV side of ZESCO step down transformer | m | 0
| 7.4.2 | By underground armoured cable c/w all internal building works, and making good, outside excavation, backfilling and protective concrete cover slabs from Main Distribution Board | m | 80 |  | 0
| 7.5 | By overhead single phase 230 VAC power line from LV side of ZESCO step-down transformer, c/w all necessary intermediate power poles | m | 0
|  | Sub-total |  |  |  | 0
|  | Contingencies (10%) |  |  |  | 0
|  | Taxes (VAT @16%) |  |  |  | 0
|  | Total |  |  |  | 0
Note on C27: Baker: parallel or vertical Woltman meter?

## Mpulungu R. Centre
UNICEF
Solar Powered Borehole Schemes in institutions in Nchelenge (Mantapala) Refugee Camp & Host Communities
Mpulungu Reception Centre
Bill No. TC4:
Item | Description | Unit | Qty | Rate (ZMW) | Amount (ZMW)
Bill No. out, Demolition and Site Clearance |  |  |  |  | 0
1.1 | In collaboration with the Inspector of Works, and based upon pipe lengths and alignment shown on layout plan, agree upon final alignment of pipelines, road crossings, location of all tees, bends, isolating valves, air valves, washouts, tapstands, and consumer connection offtakes. Set out pipeline centre-lines, survey, agree upon Starting Surfaces, and final lengths and produce final plans at horizontal scale of 1:200 for approval before proceeding further. | LS | 1 |  | 0
1.2 | General Clearance for urban land & rough grass land along pipeline wayleaves (trench width plus 0.5 m on either side) | ha | 0.1 |  | 0
1.3 | Removal of tree stumps within approved alignment. PROVISIONAL SUM | nr | 1 |  | 0
1.4 | Cut down and remove trees and tree stumps within approved alignment only if specifically directed to do so by Inspector of Works following agreement from the Host Community PROVISIONAL SUM | nr | 1 |  | 0
Bill No. 2: Excavation and backfilling of trenches - all pipelines |  |  |  |  | 0
2.1 | Excavate test pits along centre line of proposed pipeline to depth of 1m at least every 50 m | nr | 6 |  | 0
2.2 | Excavate and trim trench bed to depth not exceeding 1 m to ensure minimum cover provided to pipeline is not less than 600 mm | m | 236.7 |  | 0
2.3 | E. O. item 2.2 at road crossings. Excavate and trim trench to additional depth not exceeding 1.5 m to ensure minimum cover provided to the pipeline is 900 mm | m | 26.3 |  | 0
2.4 | Over excavate trench by a further depth of 150mm in areas identified by the Inspector of Works as requiring imported granular backfill RATE ONLY | m3 | 2.367 |  | 0
2.5 | Import, place and compact granular backfill in areas identified by the Inspector of Works as requiring imported granular backfill. RATE ONLY, | m3 | 2.367 |  | 0
2.6 | Place and compact sidefill and backfill using selected excavated material free of stones and tree roots to depth 300 mm above crown of pipe, and after compaction, other excavated material thereafter to final surface | m | 236.7 |  | 0
2.7 | Dispose of all surplus excavated material off-site as directed | LS | 1 |  | 0
Bill No. 3: Supply and Installation of rising main- borehole to elevated water tank |  |  |  |  | 0
All PE compression joints and fittings shall be supplied complete with suitable pipe joint stiffeners. All steel fittings shall be epoxy coated and all nuts and bolts galvanised. Rate shall include supply, lay, bed, joint , pressure test, sterilize and flushing of HDPE pipelines
3.1 | Raw water rising main from borehole to the Elevated Tank , HDPE DN50 (OD 63), SDR17, PN 10 | m | 59 |  | 0
3.2 | Gate Valve, double flange, handwheel operated 50 mm non-rising spindle type, with 1 No. flanged restraining adapters st. fl. to PE DN 50, installed above ground within tank inlet riser pipe | set | 1 |  | 0
3.3 | Supply and Installation of DN 40 parallel bulk water meter with magnetic transmission and dry recording head , metrological class B, minimum display 1 m3/hr to specification, suitable for vertical mounting, within water tank inlet riser pipe complete with strainer (metallic double flanged body c/w lockable meter box pipe surround). The meter assembly shall comprise: 1 No. DN50 to DN40 reducer, 1 DN40 500mm long straight pipe length, 1 DN 40 mm double flanged vertically mounted parallel bulk type meter, located approximately 1.5 m above ground level, 1 DN 40 250 mm straight pipe length, and one DN40 to DN50 reducer. | set | 1 |  | 0
3.4 | Provide all materials and construct fenced and gated compound to contain solar array and associated chambers to Specification. | LS | 1 |  | 0
3.5 | Supply and install DN 25 water pipe take-off from rising mainand sgtandpipe for solar cleansing system | LS | 1 |  | 0
3.6 | Provide solar array cleansing step ladder and extendable washer to Specification | LS | 1 |  | 0
| Carry forward |  |  |  | 0
| Brought forward |  |  |  | 0
Bill No. 4: Tanks, Tankstands and Tap Stands |  |  |  |  | 0
Bidder shall supply outline details of water tank stand and tank c/w, pipework and fittings.
water tank stand manufacturer:
HDPE cylindrical tank manufacturer:
HDPE cylindrical tank supplier (if different):
Contractor shall supply full set of structural calculations and drawings for water tank stand certified by a registered structural engineer for written approval prior to fabrication.
4.1 | Conduct geotechnical investigations and design foundation and tank stand for the elevated tank | LS | 1 |  | 0
4.2 | Tank reinforced concrete foundations 1 m x 1m x 1.5 m deep inc. excavation, shuttering, concreting, curing, backfilling and disposal of excess spoil material from site | nr | 4 |  | 0
Supply and install 1 No. HDPE cylindrical tank on Contractor designed mild steel tankstand c/w with inlet float valve, all inflow, outflow, overflow, and scour (washout) pipework, fittings, adaptors and 6m high steel stand c/w access ladder and lightning arrestor.
4.3 | Capacity 5m3. | nr | 1 |  | 0
4.4 | Supply and paint all mild steel in tank stand with two coats of zinc 82% rich paint in dry film | LS | 1 |  | 0
4.5 | Leak testing and disinfection of tank and pipework | nr | 1 |  | 0
4.6 | Provide & install float level indicator gauge on side of tank readable from ground level adjacent to tank | nr | 1 |  | 0
4.7 | Provide and install chlorine cartridge type inline doser in lockable chamber at start of tank outlet pipe c/w twelve months supply of chlorine cartridges. | LS | 1 |  | 0
4.8 | Provide materials for and construct tap stand and associated drainage | nr | 4 |  | 0
Bill No. 5: Supply and Install Water Distribution Network |  |  |  |  | 0
All PE compression joints and fittings shall be supplied complete with suitable pipe joint stiffeners. All steel fittings shall be epoxy coated and all nuts and bolts galvanised. Rate shall include supply, lay, bed, joint , pressure test, sterilize and flushing of HDPE pipelines
5.1 | Equal tee compression fitting DN 32 x 32 x 32 mm | nr | 2 |  | 0
5.2 | Network reticulation pipework HDPE DN 32mm, SDR17, PN 10 | m | 204 |  | 0
5.3 | Compression fitting, elbow 90o DN 32mm | nr | 2 |  | 0
5.4 | End cap DN 32mm (compression type) | nr | 3 |  | 0
5.5 | Compression tee DN 32 x 32 x 1" male branch to connect to tap stand pipework | nr | 4 |  | 0
5.6 | Gate Valve, double flange, 40 mm non-rising spindle type, with 2 No. flanged restraining adapters st. fl. to PE DN 40, complete with valve riser and valve box to suit | nr | 1 |  | 0
Air valve assembly consisting of 1 No. compression tee with threaded male 1 1/2" branch vertically upwards, 1 No. female to male thr. spigot, 1 No. Stopcock, thr. dble. socket 1", and 1 No. Single air valve, thr. female 1". RATE ONLY
5.7 | Compression tee DN 32 x 32 x 1" male br, 1 No. female to male 1" to 1" thr. spigot | set | 1
| Carry forward |  |  |  | 0
| Brought forward |  |  |  | 0
Bill No. 6: Concrete Works to all Pipelines |  |  |  |  | 0
All unreinforced concrete works shall be in medium strength concrete unless otherwise indicated. Where bends less than 45o are obtained by bending the pipe, radius not less than 35 x pipe diameter, and provided there is no compression joint with 5 metres of either end of radius, no separate thrust block is required.
6.1 | Over excavate in trench bed at all gate valves, air valve assemblies and steel fittings and cast support slab to full width of trench with other dimensions being the length of the valve or the fitting between flanges or between the compression tightening nuts and depth below trench bed of 150 mm | nr | 1 |  | 0
6.2 | At all 45o and 90o bends, pipeline tees, and end caps, provide and subsequently remove shuttering and cast thrust blocks against undisturbed trench bed and trench wall | nr | 7 |  | 0
6.3 | Supply all materials and cast and complete air-valve chamber. RATE ONLY | nr | 1
Bill No. 7: Water Distribution Network | Electromechanical |  |  |  | 0
Bidder shall supply details of proposed pumpset c/w shroud, and standby generator for which there shall be a local agent
proposed submersible hybrid DC/AC pumpset manufacturer and agent:
proposed standby generator manufacturer and agent:
| confirm manufactures brochures included with bid |  | yes / no
No change from these manufacturers or agents shall be permitted without prior written approval from the Consultant
Submersible 48 VDC Borehole Pump
7.1 | Supply and install a hybrid DC/AC borehole submersible pump suitable for a borehole of ID 5" capable of being powered from either a 48 VDC or a nominal 230 VAC source c/w cabled connection to power sources located within 10 m of borehole head, pumping into an overhead tank with top water inlet 14 m above ground.. . |  | nr | 1
Information provided to guide Bidder
| Ground elevation at borehole (approximate) | masl | 839
| Yield | m3/hr | 0.33
| Pump installation level below ground surface | m | 90
| Riser pipe diameter | mm | DN 50
| Dynamic water level below ground surface | m | 87.98
| Top water level in overhead tank | masl | 853
Information to be provided by Bidder
| Manufacturers Pump reference No. | ref.
| Maximum flow at Installation indicated above | m3/hr
| Maximum pump head at installation indicated above | m3/hr
| Optimum flow at Installation indicated above | m3/hr
| Optimum head at Installation indicated above | m3/hr
| Pump efficiency at installation | %
| Input power required by pump | W
| Output power required by solar array | W
| No. of solar panels and arrays offered and guaranteed to meet requirement | nr
7.2 | Supply, install, erect and connect solar arrays to meet requirements c/w lightning protection as per Drawing | LS | 1 |  | 0
Supply and Installation of 220 VAC standby generator of rated power
7.3 | Supply, Install and connect by manually operated changeover switch standby generator capable of providing the VAC power required to operate the submersible borehole pump as specified above at half-load c/w roofed lockable waterproof steel protection cabinet. | nr | 1 |  | 0
Information to be provided by Bidder
Manufacturers Generator Set reference No.
| Output kVA at 1500rpm, 220V, single-phase, 50Hz, with power factor of 1.0 | kVA
| Fuel type (petrol/diesel) | type
| Fuel tank capacity | l
Air or water cooled
| Sub-total |  |  |  | 0
| Contingencies (10%) |  |  |  | 0
| Taxes (VAT @16%) |  |  |  | 0
| Total |  |  |  | 0
Note on C26: Baker: parallel or vertical Woltman meter?