## Grand Total Summary
| TITLE: LOT 3 SOLAR SCHEMES IN KALUMBILA DISTRICT | Bill AMOUNT
ITEM No. | D E S C R I P T I O N | AMOUNT
(ZMW)
BILL COLLECTION SHEET
SUB-BILL
Bill No.P&G: | PRELIMINARY & GENERAL ITEMS | 220000
Bill No. SCH1 | Meheba B International School | 0
Bill No. SCH2 | Meheba A Secondary Boarding School | 0
Bill No. SCH3 | Manyama Primary School | 0
Bill No. SCH4 | Kananga Primary School & RHC | 0
Bill No. SCH5 | Kambazhi Primary School and RHC | 0
Bill No. SCH6 | Shilenda Primary School | 0
Bill No. RHC1: | Meheba B RHC | 0
Bill No. RHC2: | Meheba A RHC with extension to Primary School | 0
| Meheba A Primary School Transfer Pipeline from Meheba A Rural Health Clinic | 0
| Meheba A Primary School Storage and Distribution System | 0
Bill No. RHC3: | Kakaindu RHC with Primary School extension | 0
Bill No. RHC4: | Meheba Block G RHC and Primary School | 0
Bill No. RHC5: | Meheba Block D RHC with extension to Primary School | 0
| Meheba D Primary School Transfer Pipeline from Meheba D Rural Health Clinic | 0
| Meheba D Primary School Storage and Distribution System | 0
Bill No. RHC6: | Lumwana Hospital | 0
Bill No. TC1 | Block D Transit Center 36 | 0
| BILL OF QUANTITIES TOTAL | 220000
| 10% Contingencies | 22000
| TOTAL WORKS | 242000

## P&Gs
UNICEF
Solar Powered Borehole Schemes in institutions in Kalumbila District Meheba Host Communities
Bill No.P&G:
Item | Description | Unit | Qty | Rate (ZMW) | Amount (ZMW)
Bill No. 1: Preliminary and general |  |  |  |  | 220000
1.1 | Allow for all sureties and insurance cover; site establishment (Including time-related costs); offices; workshops; storage sheds; living accommodation; compliance with labour regulations; ablution facilities; water supplies, power and communication; site notice boards etc. | LS | 1 |  | 0
1.2 | Provisional sum for material testing | PS | 1 | 20000 | 20000
1.3 | Compliance with Environmental and Social Safeguards (EP) | LS | 1 |  | 0
1.4 | Compliance with Health and Safety Safeguards (HS) | LS | 1 |  | 0
1.5 | Repair of existing water supplies (solar related systems) | PS | 1 | 200000 | 200000
1.6 | Supply and install 2 x Solar Powered Light Poles with batteries (as per standard drawing) | no. | 14 |  | 0
| Sub-total |  |  |  | 220000
Contingencies (10%)
Taxes (VAT @16%)
| Total |  |  |  | 220000

## Meheba B Int Sch
UNICEF
Solar Powered Borehole Schemes in institutions in Meheba Refugee Camp & Host Communities
Meheba B International School
Bill No. SCH1
| Item | Description | Unit | Qty | Rate (ZMW) | Amount (ZMW)
| Bill No. out, Demolition and Site Clearance |  |  |  |  | 0
| 1.1 | In collaboration with the Inspector of Works, and based upon pipe lengths and alignment shown on layout plan, agree upon final alignment of pipelines, road crossings, location of all tees, bends, isolating valves, air valves, washouts, tapstands, and consumer connection offtakes. Set out pipeline centre-lines, survey, agree upon Starting Surfaces, and final lengths and produce final plans at horizontal scale of 1:200 for approval before proceeding further. | LS | 1 |  | 0
| 1.2 | General Clearance for urban land & rough grass land along pipeline wayleaves (trench width plus 0.5 m on either side) | ha | 0.2 |  | 0
| 1.3 | Removal of tree stumps within approved alignment. PROVISIONAL SUM | nr | 1 |  | 0
| 1.4 | Cut down and remove trees and tree stumps within approved alignment only if specifically directed to do so by Inspector of Works following agreement from the Host Community PROVISIONAL SUM | nr | 1 |  | 0
| Bill No. 2: Excavation and backfilling of trenches - all pipelines |  |  |  |  | 0
| 2.1 | Excavate test pits along centre line of proposed pipeline to depth of 1m at least every 50 m | nr | 16 |  | 0
| 2.2 | Excavate and trim trench bed to depth not exceeding 1 m to ensure minimum cover to pipeline of 600 mm | m | 677.7 |  | 0
| 2.3 | Excavate and trim trench to depth not exceeding 1.5 m to ensure minimum cover to pipeline of 900 mm | m | 75.3 |  | 0
| 2.4 | Over excavate trench by a further depth of 150mm in areas identified by the Inspector of Works as requiring imported granular backfill RATE ONLY | m3 | 6.777 |  | 0
| 2.5 | Import, place and compact granular backfill in areas identified by the Inspector of Works as requiring imported granular backfill. RATE ONLY, | m3 | 6.777 |  | 0
| 2.6 | Place and compact sidefill and backfill using selected excavated material free of stones and tree roots to depth 300 mm above crown of pipe, and after compaction, other excavated material thereafter to final surface | m | 677.7 |  | 0
| 2.7 | Dispose of all surplus excavated material off-site | LS | 1 |  | 0
| Bill No. 3: Supply and Installation of rising main- borehole to elevated water tank |  |  |  |  | 0
All PE compression joints and fittings shall be supplied complete with suitable pipe joint stiffeners. All steel fittings shall be epoxy coated and all nuts and bolts galvanised. Rate shall include supply, lay, bed, joint , pressure test, sterilize and flushing of HDPE pipelines
| 3.1 | Raw water rising main from borehole to the Elevated Tank , HDPE DN50 (OD 63), SDR17, PN 10 | m | 54 |  | 0
| 3.2 | Compression fitting, elbow 90o DN 50mm | nr | 1
| 3.3 | Supply and Installation of DN 40 parallel Woltman type bulk water meter, metrological class B, minimum display 1 m3/hr, suitable for vertical mounting, within water tank inlet riser pipe complete with strainer (metallic double flanged body c/w lockable meter box pipe surround). The meter assembly shall comprise: 1 No. DN50 to DN40 reducer, 1 DN40 500mm long straight pipe length, 1 DN 40 mm double flanged vertically mounted parallel Woltman type meter, located approximately 1.5 m above ground level, 1 DN 40 250 mm straight pipe length, and one DN40 to DN50 reducer. | set | 1 |  | 0
| 3.4 | Gate Valve, double flange, 50 mm non-rising spindle type, with 2 No. flanged restraining adapters st. fl. to PE DN 50, complete with valve riser and valve box to suit | set | 1 |  | 0
| 3.5 | Supply and install DN 25 water pipe take-off from rising mainand standpipe for solar cleansing system | LS | 1 |  | 0
| 3.6 | Provide solar array cleansing step ladder and extendable washer to Specification | LS | 1 |  | 0
|  | Carry forward |  |  |  | 0
|  | Brought forward |  |  |  | 0
| Bill No. 4: Tanks, Tankstands and Tap Stands |  |  |  |  | 0
Bidder shall supply outline details of water tank stand and tank c/w, pipework and fittings.
water tank stand manufacturer:
HDPE cylindrical tank manufacturer:
HDPE cylindrical tank supplier (if different):
Contractor shall supply full set of structural calculations and drawings for water tank stand certified by a registered structural engineer for written approval prior to fabrication.
| 4.1 | Conduct geotechnical investigations and design foundation and tank stand for the elevated tank | LS | 1 |  | 0
| 4.2 | Tank reinforced concrete foundations 1 m x 1m x 1.5 m deep inc. excavation, shuttering, concreting, curing, backfilling and disposal of excess spoil material from site | nr | 6 |  | 0
Supply and install 2 No. HDPE cylindrical tank on Contractor designed six vertical members) mild steel tankstand c/w with inlet float valves, all inflow, valved connecting, outflow, overflow, and scour (washout) pipework, fittings, adaptors and 6m high steel stand c/w access ladder and lightning arrestor.
4.3 | 4.3 | Capacity 10m3.(two no. of 5m3) | nr | 10 |  | 0
| 4.4 | Supply and paint all mild steel in tank stand with two coats of zinc 82% rich paint in dry film | LS | 1 |  | 0
| 4.5 | Leak testing and disinfection of tank and pipework | nr | 1 |  | 0
| 4.6 | Provide & install float level indicator gauge on side of tank readable from ground level adjacent to tank | nr | 1 |  | 0
| 4.7 | Provide and install chlorine cartridge type inline doser in lockable chamber at start of tank outlet pipe c/w twelve months supply of chlorine cartridges. | LS | 1 |  | 0
| 4.8 | Provide materials for and construct tap stand and associated drainage | nr | 8 |  | 0
| Bill No. 5: Supply and Install Water Distribution Network |  |  |  |  | 0
All PE compression joints and fittings shall be supplied complete with suitable pipe joint stiffeners. All steel fittings shall be epoxy coated and all nuts and bolts galvanised. Rate shall include supply, lay, bed, joint , pressure test, sterilize and flushing of HDPE pipelines
| 5.1 | Network reticulation pipework HDPE DN50 (OD 63), SDR17, PN 10 | m | 432 |  | 0
| 5.2 | Equal tee compression fitting DN 50 x 50 x 50 mm | nr | 1 |  | 0
| 5.3 | Unequal reducing tee compression fitting DN 50 x 50 x 40 mm | nr | 1 |  | 0
| 5.4 | Unequal reducing tee compression fitting DN 50 x 50 x 32 mm | nr | 2 |  | 0
| 5.5 | Compression reducer coupling 50mm x 40mm | nr | 5 |  | 0
| 5.6 | Compression reducer coupling 50mm x 32mm | nr | 0 |  | 0
| 5.7 | Compression reducer coupling 40mm x 32mm | nr | 3 |  | 0
| 5.8 | Network reticulation pipework HDPE DN 40mm, SDR17, PN 10 | m | 205 |  | 0
| 5.9 | Network reticulation pipework HDPE DN 32mm, SDR17, PN 10 | m | 62 |  | 0
| 5.1 | Compression fitting, elbow 90o DN 50mm | nr | 2 |  | 0
| 5.11 | Compression fitting, elbow 90o DN 40mm | nr | 2 |  | 0
| 5.12 | End cap DN 32mm (compression type) | nr | 4 |  | 0
| 5.13 | Supply and install GI pipes 25mm dia c/w fittings to tap stands c/w isolating stop cock | nr | 8 |  | 0
| 5.14 | Supply and install heavy weight brass garden bib tap (non-lever arm type) | nr | 16 |  | 0
| 5.15 | Compression tee DN 50 x 50 x 1 1/2" male br., 1 No. female to male 1 1/2" to 1" thr. spigot to connect to tap stand pipework | nr | 4 |  | 0
| 5.16 | Gate Valve, double flange, 40 mm non-rising spindle type, with 2 No. flanged restraining adapters st. fl. to PE DN 40, complete with valve riser and valve box to suit | nr | 2 |  | 0
Air valve assembly consisting of 1 No. compression tee with threaded male 1 1/2" branch vertically upwards, 1 No. female to male thr. spigot, 1 No. Stopcock, thr. dble. socket 1", and 1 No. Single air valve, thr. female 1". RATE ONLY
| 5.18.1 | Compression tee DN 50 x 50 x 1 1/2" male br., 1 No. female to male 1 1/2" to 1" thr. spigot | set | 1
| 5.18.2 | Compression tee DN 40 x 40 x 1 1/2" male br., 1 No. female to male 1 1/2" to 1" thr. Spigot | set | 1
| 5.18.3 | Compression tee DN 32 x 32 x 1" male br, 1 No. female to male 1" to 1" thr. spigot | set | 1
|  | Carry forward |  |  |  | 0
|  | Brought forward |  |  |  | 0
| Bill No. 6: Concrete Works to all Pipelines |  |  |  |  | 0
All unreinforced concrete works shall be in medium strength concrete unless otherwise indicated. Where bends less than 45o are obtained by bending the pipe, radius not less than 35 x pipe diameter, and provided there is no compression joint with 5 metres of either end of radius, no separate thrust block is required.
| 6.1 | Over excavate in trench bed at all gate valves, air valve assemblies and steel fittings and cast support slab to full width of trench with other dimensions being the length of the valve or the fitting between flanges or between the compression tightening nuts and depth below trench bed of 150 mm | nr | 3 |  | 0
| 6.2 | At all 45o and 90o bends, pipeline tees, and end caps, provide and subsequently remove shuttering and cast thrust blocks against undisturbed trench bed and trench wall | nr | 12 |  | 0
| 6.3 | Supply all materials and cast and complete air-valve chamber. RATE ONLY | nr | 1
| Bill No. 7: Water Distribution Network | Electromechanical |  |  |  | 0
Bidder shall supply details of proposed pumpset c/w shroud, and standby generator for which there shall be a local agent
proposed submersible hybrid DC/AC pumpset manufacturer and agent:
proposed standby generator manufacturer and agent:
|  | confirm manufactures brochures included with bid |  | yes / no
No change from these manufacturers or agents shall be permitted without prior written approval from the Consultant
Submersible 48 VDC Borehole Pump
| 7.1 | Supply and install a hybrid DC/AC borehole submersible pump suitable for a borehole of ID 5" capable of being powered from either a 48 VDC or a nominal 230 VAC source c/w cabled connection to power sources located within 10 m of borehole head, pumping into an overhead tank with top water inlet 14 m above ground.. . |  | nr | 1
Information provided to guide Bidder
|  | Ground elevation at borehole (approximate) | masl | 1319
|  | Yield | m3/hr | 2 | tbc
|  | Pump installation level below ground surface | m | 37 | tbc
|  | Riser pipe diameter | mm | DN 50
|  | Dynamic water level below ground surface | m | 29 | tbc
|  | Top water level in overhead tank | masl | 1333
Information to be provided by Bidder
|  | Manufacturers Pump reference No. | ref.
|  | Maximum flow at Installation indicated above | m3/hr
|  | Maximum pump head at installation indicated above | m3/hr
|  | Optimum flow at Installation indicated above | m3/hr
|  | Optimum head at Installation indicated above | m3/hr
|  | Pump efficiency at installation | %
|  | Input power required by pump | W
|  | Output power required by solar array | W
|  | No. of solar panels and arrays offered and guaranteed to meet requirement | nr
| 7.2 | Solar arrays to meet requirements c/w security fence and gate and lightning protection as per Drawing to be included in this Option
| 7.2.1 | Supply, install, erect and connect solar arrays to meet requirements c/w lightning protection as per Drawing and Specification | nr | 1 |  | 0
| 7.2.2 | Provide all materials and construct fenced and gated compound to contain solar array and associated chambers to Specification | LS | 1 |  | 0
| 7.2.3 | Supply and install DN 25 water pipe take-off from rising main and standpipe for solar cleansing system | LS | 1 |  | 0
| 7.2.4 | Provide solar array cleansing step ladder and extendable washer to Specification | LS | 1 |  | 0
Supply and Installation of 220 VAC standby generator of rated power
| 7.3 | Supply, Install and connect by manually operated changeover switch standby generator capable of providing the VAC power required to operate the submersible borehole pump as specified above at half-load c/w roofed lockable waterproof steel protection cabinet. | nr | 1 |  | 0
Information to be provided by Bidder
Manufacturers Generator Set reference No.
|  | Output kVA at 1500rpm, 220V, single-phase, 50Hz, with power factor of 1.0 | kVA
|  | Fuel type (petrol/diesel) | type
|  | Fuel tank capacity | l
Air or water cooled
|  | Sub-total |  |  |  | 0
|  | Contingencies (10%) |  |  |  | 0
|  | Taxes (VAT @16%) |  |  |  | 0
|  | Total |  |  |  | 0

## Meheba A Sc Brd Sch
UNICEF
Solar Powered Borehole Schemes in institutions in Meheba Refugee Camp & Host Communities
Meheba A Secondary Boarding School
Bill No. SCH2
| Item | Description | Unit | Qty | Rate (ZMW) | Amount (ZMW)
| Bill No. out, Demolition and Site Clearance |  |  |  |  | 0
| 1.1 | In collaboration with the Inspector of Works, and based upon pipe lengths and alignment shown on layout plan, agree upon final alignment of pipelines, road crossings, location of all tees, bends, isolating valves, air valves, washouts, tapstands, and consumer connection offtakes. Set out pipeline centre-lines, survey, agree upon Starting Surfaces, and final lengths and produce final plans at horizontal scale of 1:200 for approval before proceeding further. | LS | 1 |  | 0
| 1.2 | General Clearance for urban land & rough grass land along pipeline wayleaves (trench width plus 0.5 m on either side) | ha | 0.3 |  | 0
| 1.3 | Removal of tree stumps within approved alignment. PROVISIONAL SUM | nr | 1 |  | 0
| 1.4 | Cut down and remove trees and tree stumps within approved alignment only if specifically directed to do so by Inspector of Works following agreement from the Host Community PROVISIONAL SUM | nr | 1 |  | 0
| Bill No. 2: Excavation and backfilling of trenches - all pipelines |  |  |  |  | 0
| 2.1 | Excavate test pits along centre line of proposed pipeline to depth of 1m at least every 50 m | nr | 27 |  | 0
| 2.2 | Excavate and trim trench bed to depth not exceeding 1 m to ensure minimum cover to pipeline of 600 mm | m | 1215 |  | 0
| 2.3 | Excavate and trim trench to depth not exceeding 1.5 m to ensure minimum cover to pipeline of 900 mm | m | 135 |  | 0
| 2.4 | Over excavate trench by a further depth of 150mm in areas identified by the Inspector of Works as requiring imported granular backfill RATE ONLY | m3 | 12.15 |  | 0
| 2.5 | Import, place and compact granular backfill in areas identified by the Inspector of Works as requiring imported granular backfill. RATE ONLY, | m3 | 12.15 |  | 0
| 2.6 | Place and compact sidefill and backfill using selected excavated material free of stones and tree roots to depth 300 mm above crown of pipe, and after compaction, other excavated material thereafter to final surface | m | 1215 |  | 0
| 2.7 | Dispose of all surplus excavated material off-site | LS | 1 |  | 0
| Bill No. 3: Supply and Installation of rising main- borehole to elevated water tank |  |  |  |  | 0
All PE compression joints and fittings shall be supplied complete with suitable pipe joint stiffeners. All steel fittings shall be epoxy coated and all nuts and bolts galvanised. Rate shall include supply, lay, bed, joint , pressure test, sterilize and flushing of HDPE pipelines
| 3.1 | Raw water rising main from borehole to the Elevated Tank , HDPE DN50 (OD 63), SDR17, PN 10 | m | 135 |  | 0
| 3.2 | Compression fitting, elbow 45o DN 50mm | nr | 0 |  | 0
| 3.3 | Compression fitting, elbow 90o DN 50mm | nr | 1
| 3.4 | Supply and Installation of DN 40 parallel Woltman type bulk water meter, metrological class B, minimum display 1 m3/hr, suitable for vertical mounting, within water tank inlet riser pipe complete with strainer (metallic double flanged body c/w lockable meter box pipe surround). The meter assembly shall comprise: 1 No. DN50 to DN40 reducer, 1 DN40 500mm long straight pipe length, 1 DN 40 mm double flanged vertically mounted parallel Woltman type meter, located approximately 1.5 m above ground level, 1 DN 40 250 mm straight pipe length, and one DN40 to DN50 reducer. | set | 1 |  | 0
| 3.5 | Gate Valve, double flange, 50 mm non-rising spindle type, with 2 No. flanged restraining adapters st. fl. to PE DN 50, complete with valve riser and valve box to suit | set | 1 |  | 0
| 3.6 | Supply and install DN 25 water pipe take-off from rising mainand standpipe for solar cleansing system | LS | 1 |  | 0
| 3.7 | Provide solar array cleansing step ladder and extendable washer to Specification | LS | 1 |  | 0
|  | Carry forward |  |  |  | 0
|  | Brought forward |  |  |  | 0
| Bill No. 4: Tanks, Tankstands and Tap Stands |  |  |  |  | 0
Bidder shall supply outline details of water tank stand and tank c/w, pipework and fittings.
water tank stand manufacturer:
HDPE cylindrical tank manufacturer:
HDPE cylindrical tank supplier (if different):
Contractor shall supply full set of structural calculations and drawings for water tank stand certified by a registered structural engineer for written approval prior to fabrication.
| 4.1 | Conduct geotechnical investigations and design foundation and tank stand for the elevated tank | LS | 1 |  | 0
| 4.2 | Tank reinforced concrete foundations 1 m x 1m x 1.5 m deep inc. excavation, shuttering, concreting, curing, backfilling and disposal of excess spoil material from site | nr | 6 |  | 0
Supply and install 2 No. HDPE cylindrical tank on Contractor designed six vertical members) mild steel tankstand c/w with inlet float valves, all inflow, valved connecting, outflow, overflow, and scour (washout) pipework, fittings, adaptors and 6m high steel stand c/w access ladder and lightning arrestor.
| 4.3 | Capacity 12m3.(two no. of 6m3) | nr | 1 |  | 0
| 4.4 | Supply and paint all mild steel in tank stand with two coats of zinc 82% rich paint in dry film | LS | 1 |  | 0
| 4.5 | Leak testing and disinfection of tank and pipework | nr | 1 |  | 0
| 4.6 | Provide & install float level indicator gauge on side of tank readable from ground level adjacent to tank | nr | 1 |  | 0
| 4.7 | Provide and install chlorine cartridge type inline doser in lockable chamber at start of tank outlet pipe c/w twelve months supply of chlorine cartridges. | LS | 1 |  | 0
| 4.8 | Provide materials for and construct tap stand and associated drainage | nr | 5 |  | 0
| Bill No. 5: Supply and Install Water Distribution Network |  |  |  |  | 0
All PE compression joints and fittings shall be supplied complete with suitable pipe joint stiffeners. All steel fittings shall be epoxy coated and all nuts and bolts galvanised. Rate shall include supply, lay, bed, joint , pressure test, sterilize and flushing of HDPE pipelines
| 5.1 | Network reticulation pipework HDPE DN50 (OD 63), SDR17, PN 10 | m | 1078 |  | 0
| 5.2 | Equal tee compression fitting DN 50 x 50 x 50 mm | nr | 5 |  | 0
| 5.3 | Unequal reducing tee compression fitting DN 50 x 50 x 40 mm | nr | 18 |  | 0
| 5.4 | Compression reducer coupling 50mm x 40mm | nr | 10 |  | 0
| 5.5 | Compression reducer coupling 50mm x 32mm | nr | 1 |  | 0
131 | 5.6 | Network reticulation pipework HDPE DN 40mm, SDR17, PN 10 | m | 131 |  | 0
| 5.7 | Network reticulation pipework HDPE DN 32mm, SDR17, PN 10 | m | 6 |  | 0
| 5.8 | Compression fitting, elbow 45o DN 50mm | nr | 2 |  | 0
| 5.9 | Compression fitting, elbow 90o DN 50mm | nr | 9 |  | 0
| 5.1 | End cap DN 32mm (compression type) | nr | 22 |  | 0
| 5.11 | Saddle clamp 32mm x 3/4" to supply individual consumer connection | nr | 20 |  | 0
| 5.12 | Supply and install GI pipes 25mm dia c/w fittings to tap stands c/w isolating stop cock | nr | 5 |  | 0
| 5.13 | Supply and install heavy weight brass garden bib tap (non-lever arm type) | nr | 10 |  | 0
| 5.14 | Compression tee DN 50 x 50 x 1 1/2" male br., 1 No. female to male 1 1/2" to 1" thr. spigot to connect to tap stand pipework | nr | 5 |  | 0
| 5.15 | Gate Valve, double flange, 40 mm non-rising spindle type, with 2 No. flanged restraining adapters st. fl. to PE DN 40, complete with valve riser and valve box to suit | nr | 5 |  | 0
Air valve assembly consisting of 1 No. compression tee with threaded male 1 1/2" branch vertically upwards, 1 No. female to male thr. spigot, 1 No. Stopcock, thr. dble. socket 1", and 1 No. Single air valve, thr. female 1". RATE ONLY
| 5.16.1 | Compression tee DN 50 x 50 x 1 1/2" male br., 1 No. female to male 1 1/2" to 1" thr. spigot | set | 1
| 5.16.2 | Compression tee DN 40 x 40 x 1 1/2" male br., 1 No. female to male 1 1/2" to 1" thr. Spigot | set | 1
|  | Carry forward |  |  |  | 0
|  | Brought forward |  |  |  | 0
| Bill No. 6: Concrete Works to all Pipelines |  |  |  |  | 0
All unreinforced concrete works shall be in medium strength concrete unless otherwise indicated. Where bends less than 45o are obtained by bending the pipe, radius not less than 35 x pipe diameter, and provided there is no compression joint with 5 metres of either end of radius, no separate thrust block is required.
| 6.1 | Over excavate in trench bed at all gate valves, air valve assemblies and steel fittings and cast support slab to full width of trench with other dimensions being the length of the valve or the fitting between flanges or between the compression tightening nuts and depth below trench bed of 150 mm | nr | 6 |  | 0
| 6.2 | At all 45o and 90o bends, pipeline tees, and end caps, provide and subsequently remove shuttering and cast thrust blocks against undisturbed trench bed and trench wall | nr | 57 |  | 0
| 6.3 | Supply all materials and cast and complete air-valve chamber. RATE ONLY | nr | 1
| Bill No. 7: Water Distribution Network | Electromechanical |  |  |  | 0
Bidder shall supply details of proposed pumpset c/w shroud, and standby generator for which there shall be a local agent
proposed submersible hybrid DC/AC pumpset manufacturer and agent:
proposed standby generator manufacturer and agent:
|  | confirm manufactures brochures included with bid |  | yes / no
No change from these manufacturers or agents shall be permitted without prior written approval from the Consultant
Submersible 48 VDC Borehole Pump
| 7.1 | Supply and install a hybrid DC/AC borehole submersible pump suitable for a borehole of ID 5" capable of being powered from either a 48 VDC or a nominal 230 VAC source c/w cabled connection to power sources located within 10 m of borehole head, pumping into an overhead tank with top water inlet 14 m above ground.. . |  | nr | 1
Information provided to guide Bidder
|  | Ground elevation at borehole (approximate) | masl | 1362
|  | Yield | m3/hr | 1.2 | tbc
|  | Pump installation level below ground surface | m | 35 | tbc
|  | Riser pipe diameter | mm | DN 50
|  | Dynamic water level below ground surface | m | 24 | tbc
|  | Top water level in overhead tank | masl | 1376
Information to be provided by Bidder
|  | Manufacturers Pump reference No. | ref.
|  | Maximum flow at Installation indicated above | m3/hr
|  | Maximum pump head at installation indicated above | m3/hr
|  | Optimum flow at Installation indicated above | m3/hr
|  | Optimum head at Installation indicated above | m3/hr
|  | Pump efficiency at installation | %
|  | Input power required by pump | W
|  | Output power required by solar array | W
|  | No. of solar panels and arrays offered and guaranteed to meet requirement | nr
| 7.2 | Solar arrays to meet requirements c/w security fence and gate and lightning protection as per Drawing to be included in this Option
| 7.2.1 | Supply, install, erect and connect solar arrays to meet requirements c/w lightning protection as per Drawing and Specification | nr | 1 |  | 0
| 7.2.2 | Provide all materials and construct fenced and gated compound to contain solar array and associated chambers to Specification | LS | 1 |  | 0
| 7.2.3 | Supply and install DN 25 water pipe take-off from rising main and standpipe for solar cleansing system | LS | 1 |  | 0
| 7.2.4 | Provide solar array cleansing step ladder and extendable washer to Specification | LS | 1 |  | 0
Supply and Installation of 220 VAC standby generator of rated power
| 7.3 | Supply, Install and connect by manually operated changeover switch standby generator capable of providing the VAC power required to operate the submersible borehole pump as specified above at half-load c/w roofed lockable waterproof steel protection cabinet. | nr | 1 |  | 0
Information to be provided by Bidder
Manufacturers Generator Set reference No.
|  | Output kVA at 1500rpm, 220V, single-phase, 50Hz, with power factor of 1.0 | kVA
|  | Fuel type (petrol/diesel) | type
|  | Fuel tank capacity | l
Air or water cooled
|  | Sub-total |  |  |  | 0
|  | Contingencies (10%) |  |  |  | 0
|  | Taxes (VAT @16%) |  |  |  | 0
|  | Total |  |  |  | 0

## Manyama Pr Sch
UNICEF
Solar Powered Borehole Schemes in institutions in Meheba Refugee Camp & Host Communities
Manyama Primary School
Bill No. SCH3
| Item | Description | Unit | Qty | Rate (ZMW) | Amount (ZMW)
| Bill No. out, Demolition and Site Clearance |  |  |  |  | 0
| 1.1 | In collaboration with the Inspector of Works, and based upon pipe lengths and alignment shown on layout plan, agree upon final alignment of pipelines, road crossings, location of all tees, bends, isolating valves, air valves, washouts, tapstands, and consumer connection offtakes. Set out pipeline centre-lines, survey, agree upon Starting Surfaces, and final lengths and produce final plans at horizontal scale of 1:200 for approval before proceeding further. | LS | 1 |  | 0
| 1.2 | General Clearance for urban land & rough grass land along pipeline wayleaves (trench width plus 0.5 m on either side) | ha | 0.3 |  | 0
| 1.3 | Removal of tree stumps within approved alignment. PROVISIONAL SUM | nr | 1 |  | 0
| 1.4 | Cut down and remove trees and tree stumps within approved alignment only if specifically directed to do so by Inspector of Works following agreement from the Host Community PROVISIONAL SUM | nr | 1 |  | 0
| Bill No. 2: Excavation and backfilling of trenches - all pipelines |  |  |  |  | 0
| 2.1 | Excavate test pits along centre line of proposed pipeline to depth of 1m at least every 50 m | nr | 27 |  | 0
| 2.2 | Excavate and trim trench bed to depth not exceeding 1 m to ensure minimum cover to pipeline of 600 mm | m | 1215 |  | 0
| 2.3 | Excavate and trim trench to depth not exceeding 1.5 m to ensure minimum cover to pipeline of 900 mm | m | 135 |  | 0
| 2.4 | Over excavate trench by a further depth of 150mm in areas identified by the Inspector of Works as requiring imported granular backfill RATE ONLY | m3 | 12.15 |  | 0
| 2.5 | Import, place and compact granular backfill in areas identified by the Inspector of Works as requiring imported granular backfill. RATE ONLY, | m3 | 12.15 |  | 0
| 2.6 | Place and compact sidefill and backfill using selected excavated material free of stones and tree roots to depth 300 mm above crown of pipe, and after compaction, other excavated material thereafter to final surface | m | 1215 |  | 0
| 2.7 | Dispose of all surplus excavated material off-site | LS | 1 |  | 0
| Bill No. 3: Supply and Installation of rising main- borehole to elevated water tank |  |  |  |  | 0
All PE compression joints and fittings shall be supplied complete with suitable pipe joint stiffeners. All steel fittings shall be epoxy coated and all nuts and bolts galvanised. Rate shall include supply, lay, bed, joint , pressure test, sterilize and flushing of HDPE pipelines
| 3.1 | Raw water rising main from borehole to the Elevated Tank , HDPE DN50 (OD 63), SDR17, PN 10 | m | 135 |  | 0
| 3.2 | Compression fitting, elbow 45o DN 50mm | nr | 0 |  | 0
| 3.3 | Compression fitting, elbow 90o DN 50mm | nr | 1
| 3.4 | Supply and Installation of DN 40 parallel Woltman type bulk water meter, metrological class B, minimum display 1 m3/hr, suitable for vertical mounting, within water tank inlet riser pipe complete with strainer (metallic double flanged body c/w lockable meter box pipe surround). The meter assembly shall comprise: 1 No. DN50 to DN40 reducer, 1 DN40 500mm long straight pipe length, 1 DN 40 mm double flanged vertically mounted parallel Woltman type meter, located approximately 1.5 m above ground level, 1 DN 40 250 mm straight pipe length, and one DN40 to DN50 reducer. | set | 1 |  | 0
| 3.5 | Gate Valve, double flange, 50 mm non-rising spindle type, with 2 No. flanged restraining adapters st. fl. to PE DN 50, complete with valve riser and valve box to suit | set | 1 |  | 0
| 3.6 | Supply and install DN 25 water pipe take-off from rising mainand standpipe for solar cleansing system | LS | 1 |  | 0
| 3.7 | Provide solar array cleansing step ladder and extendable washer to Specification | LS | 1 |  | 0
|  | Carry forward |  |  |  | 0
|  | Brought forward |  |  |  | 0
| Bill No. 4: Tanks, Tankstands and Tap Stands |  |  |  |  | 0
Bidder shall supply outline details of water tank stand and tank c/w, pipework and fittings.
water tank stand manufacturer:
HDPE cylindrical tank manufacturer:
HDPE cylindrical tank supplier (if different):
Contractor shall supply full set of structural calculations and drawings for water tank stand certified by a registered structural engineer for written approval prior to fabrication.
| 4.1 | Conduct geotechnical investigations and design foundation and tank stand for the elevated tank | LS | 1 |  | 0
| 4.2 | Tank reinforced concrete foundations 1 m x 1m x 1.5 m deep inc. excavation, shuttering, concreting, curing, backfilling and disposal of excess spoil material from site | nr | 6 |  | 0
Supply and install 2 No. HDPE cylindrical tank on Contractor designed six vertical members) mild steel tankstand c/w with inlet float valves, all inflow, valved connecting, outflow, overflow, and scour (washout) pipework, fittings, adaptors and 6m high steel stand c/w access ladder and lightning arrestor.
| 4.3 | Capacity 20m3.(two no. of 10m3) | nr | 1 |  | 0
| 4.4 | Supply and paint all mild steel in tank stand with two coats of zinc 82% rich paint in dry film | LS | 1 |  | 0
| 4.5 | Leak testing and disinfection of tank and pipework | nr | 1 |  | 0
| 4.6 | Provide & install float level indicator gauge on side of tank readable from ground level adjacent to tank | nr | 1 |  | 0
| 4.7 | Provide and install chlorine cartridge type inline doser in lockable chamber at start of tank outlet pipe c/w twelve months supply of chlorine cartridges. | LS | 1 |  | 0
| 4.8 | Provide materials for and construct tap stand and associated drainage | nr | 5 |  | 0
| Bill No. 5: Supply and Install Water Distribution Network |  |  |  |  | 0
All PE compression joints and fittings shall be supplied complete with suitable pipe joint stiffeners. All steel fittings shall be epoxy coated and all nuts and bolts galvanised. Rate shall include supply, lay, bed, joint , pressure test, sterilize and flushing of HDPE pipelines
| 5.1 | Network reticulation pipework HDPE DN50 (OD 63), SDR17, PN 10 | m | 1078 |  | 0
| 5.2 | Equal tee compression fitting DN 50 x 50 x 50 mm | nr | 5 |  | 0
| 5.3 | Unequal reducing tee compression fitting DN 50 x 50 x 40 mm | nr | 18 |  | 0
| 5.4 | Compression reducer coupling 50mm x 40mm | nr | 10 |  | 0
| 5.5 | Compression reducer coupling 50mm x 32mm | nr | 1 |  | 0
131 | 5.6 | Network reticulation pipework HDPE DN 40mm, SDR17, PN 10 | m | 131 |  | 0
| 5.7 | Network reticulation pipework HDPE DN 32mm, SDR17, PN 10 | m | 6 |  | 0
| 5.8 | Compression fitting, elbow 45o DN 50mm | nr | 2 |  | 0
| 5.9 | Compression fitting, elbow 90o DN 50mm | nr | 9 |  | 0
| 5.1 | End cap DN 32mm (compression type) | nr | 22 |  | 0
| 5.11 | Saddle clamp 32mm x 3/4" to supply individual consumer connection | nr | 20 |  | 0
| 5.12 | Supply and install GI pipes 25mm dia c/w fittings to tap stands c/w isolating stop cock | nr | 5 |  | 0
| 5.13 | Supply and install heavy weight brass garden bib tap (non-lever arm type) | nr | 10 |  | 0
| 5.14 | Compression tee DN 50 x 50 x 1 1/2" male br., 1 No. female to male 1 1/2" to 1" thr. spigot to connect to tap stand pipework | nr | 5 |  | 0
| 5.15 | Gate Valve, double flange, 40 mm non-rising spindle type, with 2 No. flanged restraining adapters st. fl. to PE DN 40, complete with valve riser and valve box to suit | nr | 5 |  | 0
Air valve assembly consisting of 1 No. compression tee with threaded male 1 1/2" branch vertically upwards, 1 No. female to male thr. spigot, 1 No. Stopcock, thr. dble. socket 1", and 1 No. Single air valve, thr. female 1". RATE ONLY
| 5.16.1 | Compression tee DN 50 x 50 x 1 1/2" male br., 1 No. female to male 1 1/2" to 1" thr. spigot | set | 1
| 5.16.2 | Compression tee DN 40 x 40 x 1 1/2" male br., 1 No. female to male 1 1/2" to 1" thr. Spigot | set | 1
|  | Carry forward |  |  |  | 0
|  | Brought forward |  |  |  | 0
| Bill No. 6: Concrete Works to all Pipelines |  |  |  |  | 0
All unreinforced concrete works shall be in medium strength concrete unless otherwise indicated. Where bends less than 45o are obtained by bending the pipe, radius not less than 35 x pipe diameter, and provided there is no compression joint with 5 metres of either end of radius, no separate thrust block is required.
| 6.1 | Over excavate in trench bed at all gate valves, air valve assemblies and steel fittings and cast support slab to full width of trench with other dimensions being the length of the valve or the fitting between flanges or between the compression tightening nuts and depth below trench bed of 150 mm | nr | 6 |  | 0
| 6.2 | At all 45o and 90o bends, pipeline tees, and end caps, provide and subsequently remove shuttering and cast thrust blocks against undisturbed trench bed and trench wall | nr | 57 |  | 0
| 6.3 | Supply all materials and cast and complete air-valve chamber. RATE ONLY | nr | 1
| Bill No. 7: Water Distribution Network | Electromechanical |  |  |  | 0
Bidder shall supply details of proposed pumpset c/w shroud, and standby generator for which there shall be a local agent
proposed submersible hybrid DC/AC pumpset manufacturer and agent:
proposed standby generator manufacturer and agent:
|  | confirm manufactures brochures included with bid |  | yes / no
No change from these manufacturers or agents shall be permitted without prior written approval from the Consultant
Submersible 48 VDC Borehole Pump
| 7.1 | Supply and install a hybrid DC/AC borehole submersible pump suitable for a borehole of ID 5" capable of being powered from either a 48 VDC or a nominal 230 VAC source c/w cabled connection to power sources located within 10 m of borehole head, pumping into an overhead tank with top water inlet 14 m above ground.. . |  | nr | 1
Information provided to guide Bidder
|  | Ground elevation at borehole (approximate) | masl | 1404
|  | Yield | m3/hr | 2.1 | tbc
|  | Pump installation level below ground surface | m | 44 | tbc
|  | Riser pipe diameter | mm | DN 50
|  | Dynamic water level below ground surface | m | 38 | tbc
|  | Top water level in overhead tank | masl | 1420
Information to be provided by Bidder
|  | Manufacturers Pump reference No. | ref.
|  | Maximum flow at Installation indicated above | m3/hr
|  | Maximum pump head at installation indicated above | m3/hr
|  | Optimum flow at Installation indicated above | m3/hr
|  | Optimum head at Installation indicated above | m3/hr
|  | Pump efficiency at installation | %
|  | Input power required by pump | W
|  | Output power required by solar array | W
|  | No. of solar panels and arrays offered and guaranteed to meet requirement | nr
| 7.2 | Solar arrays to meet requirements c/w security fence and gate and lightning protection as per Drawing to be included in this Option
| 7.2.1 | Supply, install, erect and connect solar arrays to meet requirements c/w lightning protection as per Drawing and Specification | nr | 1 |  | 0
| 7.2.2 | Provide all materials and construct fenced and gated compound to contain solar array and associated chambers to Specification | LS | 1 |  | 0
| 7.2.3 | Supply and install DN 25 water pipe take-off from rising main and standpipe for solar cleansing system | LS | 1 |  | 0
| 7.2.4 | Provide solar array cleansing step ladder and extendable washer to Specification | LS | 1 |  | 0
Supply and Installation of 220 VAC standby generator of rated power
| 7.3 | Supply, Install and connect by manually operated changeover switch standby generator capable of providing the VAC power required to operate the submersible borehole pump as specified above at half-load c/w roofed lockable waterproof steel protection cabinet. | nr | 1 |  | 0
Information to be provided by Bidder
Manufacturers Generator Set reference No.
|  | Output kVA at 1500rpm, 220V, single-phase, 50Hz, with power factor of 1.0 | kVA
|  | Fuel type (petrol/diesel) | type
|  | Fuel tank capacity | l
Air or water cooled
|  | Sub-total |  |  |  | 0
|  | Contingencies (10%) |  |  |  | 0
|  | Taxes (VAT @16%) |  |  |  | 0
|  | Total |  |  |  | 0

## Kananga Pr Sch & RHC
UNICEF
Solar Powered Borehole Schemes in institutions in Meheba Refugee Camp & Host Communities
Kananga Primary School & RHC
Bill No. SCH4
| Item | Description | Unit | Qty | Rate (ZMW) | Amount (ZMW)
| Bill No. out, Demolition and Site Clearance |  |  |  |  | 0
| 1.1 | In collaboration with the Inspector of Works, and based upon pipe lengths and alignment shown on layout plan, agree upon final alignment of pipelines, road crossings, location of all tees, bends, isolating valves, air valves, washouts, tapstands, and consumer connection offtakes. Set out pipeline centre-lines, survey, agree upon Starting Surfaces, and final lengths and produce final plans at horizontal scale of 1:200 for approval before proceeding further. | LS | 1 |  | 0
| 1.2 | General Clearance for urban land & rough grass land along pipeline wayleaves (trench width plus 0.5 m on either side) | ha | 0.3 |  | 0
| 1.3 | Removal of tree stumps within approved alignment. PROVISIONAL SUM | nr | 1 |  | 0
| 1.4 | Cut down and remove trees and tree stumps within approved alignment only if specifically directed to do so by Inspector of Works following agreement from the Host Community PROVISIONAL SUM | nr | 1 |  | 0
| Bill No. 2: Excavation and backfilling of trenches - all pipelines |  |  |  |  | 0
| 2.1 | Excavate test pits along centre line of proposed pipeline to depth of 1m at least every 50 m | nr | 27 |  | 0
| 2.2 | Excavate and trim trench bed to depth not exceeding 1 m to ensure minimum cover to pipeline of 600 mm | m | 1215 |  | 0
| 2.3 | Excavate and trim trench to depth not exceeding 1.5 m to ensure minimum cover to pipeline of 900 mm | m | 135 |  | 0
| 2.4 | Over excavate trench by a further depth of 150mm in areas identified by the Inspector of Works as requiring imported granular backfill RATE ONLY | m3 | 12.15 |  | 0
| 2.5 | Import, place and compact granular backfill in areas identified by the Inspector of Works as requiring imported granular backfill. RATE ONLY, | m3 | 12.15 |  | 0
| 2.6 | Place and compact sidefill and backfill using selected excavated material free of stones and tree roots to depth 300 mm above crown of pipe, and after compaction, other excavated material thereafter to final surface | m | 1215 |  | 0
| 2.7 | Dispose of all surplus excavated material off-site | LS | 1 |  | 0
| Bill No. 3: Supply and Installation of rising main- borehole to elevated water tank |  |  |  |  | 0
All PE compression joints and fittings shall be supplied complete with suitable pipe joint stiffeners. All steel fittings shall be epoxy coated and all nuts and bolts galvanised. Rate shall include supply, lay, bed, joint , pressure test, sterilize and flushing of HDPE pipelines
| 3.1 | Raw water rising main from borehole to the Elevated Tank , HDPE DN50 (OD 63), SDR17, PN 10 | m | 135 |  | 0
| 3.2 | Compression fitting, elbow 45o DN 50mm | nr | 0 |  | 0
| 3.3 | Compression fitting, elbow 90o DN 50mm | nr | 1
| 3.4 | Supply and Installation of DN 40 parallel Woltman type bulk water meter, metrological class B, minimum display 1 m3/hr, suitable for vertical mounting, within water tank inlet riser pipe complete with strainer (metallic double flanged body c/w lockable meter box pipe surround). The meter assembly shall comprise: 1 No. DN50 to DN40 reducer, 1 DN40 500mm long straight pipe length, 1 DN 40 mm double flanged vertically mounted parallel Woltman type meter, located approximately 1.5 m above ground level, 1 DN 40 250 mm straight pipe length, and one DN40 to DN50 reducer. | set | 1 |  | 0
| 3.5 | Gate Valve, double flange, 50 mm non-rising spindle type, with 2 No. flanged restraining adapters st. fl. to PE DN 50, complete with valve riser and valve box to suit | set | 1 |  | 0
| 3.6 | Supply and install DN 25 water pipe take-off from rising mainand standpipe for solar cleansing system | LS | 1 |  | 0
| 3.7 | Provide solar array cleansing step ladder and extendable washer to Specification | LS | 1 |  | 0
|  | Carry forward |  |  |  | 0
|  | Brought forward |  |  |  | 0
| Bill No. 4: Tanks, Tankstands and Tap Stands |  |  |  |  | 0
Bidder shall supply outline details of water tank stand and tank c/w, pipework and fittings.
water tank stand manufacturer:
HDPE cylindrical tank manufacturer:
HDPE cylindrical tank supplier (if different):
Contractor shall supply full set of structural calculations and drawings for water tank stand certified by a registered structural engineer for written approval prior to fabrication.
| 4.1 | Conduct geotechnical investigations and design foundation and tank stand for the elevated tank | LS | 1 |  | 0
| 4.2 | Tank reinforced concrete foundations 1 m x 1m x 1.5 m deep inc. excavation, shuttering, concreting, curing, backfilling and disposal of excess spoil material from site | nr | 6 |  | 0
Supply and install 2 No. HDPE cylindrical tank on Contractor designed six vertical members) mild steel tankstand c/w with inlet float valves, all inflow, valved connecting, outflow, overflow, and scour (washout) pipework, fittings, adaptors and 6m high steel stand c/w access ladder and lightning arrestor.
| 4.3 | Capacity 15m3.(two no. of 7.5 m3) | nr | 1 |  | 0
| 4.4 | Supply and paint all mild steel in tank stand with two coats of zinc 82% rich paint in dry film | LS | 1 |  | 0
| 4.5 | Leak testing and disinfection of tank and pipework | nr | 1 |  | 0
| 4.6 | Provide & install float level indicator gauge on side of tank readable from ground level adjacent to tank | nr | 1 |  | 0
| 4.7 | Provide and install chlorine cartridge type inline doser in lockable chamber at start of tank outlet pipe c/w twelve months supply of chlorine cartridges. | LS | 1 |  | 0
| 4.8 | Provide materials for and construct tap stand and associated drainage | nr | 5 |  | 0
| Bill No. 5: Supply and Install Water Distribution Network |  |  |  |  | 0
All PE compression joints and fittings shall be supplied complete with suitable pipe joint stiffeners. All steel fittings shall be epoxy coated and all nuts and bolts galvanised. Rate shall include supply, lay, bed, joint , pressure test, sterilize and flushing of HDPE pipelines
| 5.1 | Network reticulation pipework HDPE DN50 (OD 63), SDR17, PN 10 | m | 1078 |  | 0
| 5.2 | Equal tee compression fitting DN 50 x 50 x 50 mm | nr | 5 |  | 0
| 5.3 | Unequal reducing tee compression fitting DN 50 x 50 x 40 mm | nr | 18 |  | 0
| 5.4 | Compression reducer coupling 50mm x 40mm | nr | 10 |  | 0
| 5.5 | Compression reducer coupling 50mm x 32mm | nr | 1 |  | 0
131 | 5.6 | Network reticulation pipework HDPE DN 40mm, SDR17, PN 10 | m | 131 |  | 0
| 5.7 | Network reticulation pipework HDPE DN 32mm, SDR17, PN 10 | m | 6 |  | 0
| 5.8 | Compression fitting, elbow 45o DN 50mm | nr | 2 |  | 0
| 5.9 | Compression fitting, elbow 90o DN 50mm | nr | 9 |  | 0
| 5.1 | End cap DN 32mm (compression type) | nr | 22 |  | 0
| 5.11 | Saddle clamp 32mm x 3/4" to supply individual consumer connection | nr | 20 |  | 0
| 5.12 | Supply and install GI pipes 25mm dia c/w fittings to tap stands c/w isolating stop cock | nr | 5 |  | 0
| 5.13 | Supply and install heavy weight brass garden bib tap (non-lever arm type) | nr | 10 |  | 0
| 5.14 | Compression tee DN 50 x 50 x 1 1/2" male br., 1 No. female to male 1 1/2" to 1" thr. spigot to connect to tap stand pipework | nr | 5 |  | 0
| 5.15 | Gate Valve, double flange, 40 mm non-rising spindle type, with 2 No. flanged restraining adapters st. fl. to PE DN 40, complete with valve riser and valve box to suit | nr | 5 |  | 0
Air valve assembly consisting of 1 No. compression tee with threaded male 1 1/2" branch vertically upwards, 1 No. female to male thr. spigot, 1 No. Stopcock, thr. dble. socket 1", and 1 No. Single air valve, thr. female 1". RATE ONLY
| 5.16.1 | Compression tee DN 50 x 50 x 1 1/2" male br., 1 No. female to male 1 1/2" to 1" thr. spigot | set | 1
| 5.16.2 | Compression tee DN 40 x 40 x 1 1/2" male br., 1 No. female to male 1 1/2" to 1" thr. Spigot | set | 1
|  | Carry forward |  |  |  | 0
|  | Brought forward |  |  |  | 0
| Bill No. 6: Concrete Works to all Pipelines |  |  |  |  | 0
All unreinforced concrete works shall be in medium strength concrete unless otherwise indicated. Where bends less than 45o are obtained by bending the pipe, radius not less than 35 x pipe diameter, and provided there is no compression joint with 5 metres of either end of radius, no separate thrust block is required.
| 6.1 | Over excavate in trench bed at all gate valves, air valve assemblies and steel fittings and cast support slab to full width of trench with other dimensions being the length of the valve or the fitting between flanges or between the compression tightening nuts and depth below trench bed of 150 mm | nr | 6 |  | 0
| 6.2 | At all 45o and 90o bends, pipeline tees, and end caps, provide and subsequently remove shuttering and cast thrust blocks against undisturbed trench bed and trench wall | nr | 57 |  | 0
| 6.3 | Supply all materials and cast and complete air-valve chamber. RATE ONLY | nr | 1
| Bill No. 7: Water Distribution Network | Electromechanical |  |  |  | 0
Bidder shall supply details of proposed pumpset c/w shroud, and standby generator for which there shall be a local agent
proposed submersible hybrid DC/AC pumpset manufacturer and agent:
proposed standby generator manufacturer and agent:
|  | confirm manufactures brochures included with bid |  | yes / no
No change from these manufacturers or agents shall be permitted without prior written approval from the Consultant
Submersible 48 VDC Borehole Pump
| 7.1 | Supply and install a hybrid DC/AC borehole submersible pump suitable for a borehole of ID 5" capable of being powered from either a 48 VDC or a nominal 230 VAC source c/w cabled connection to power sources located within 10 m of borehole head, pumping into an overhead tank with top water inlet 14 m above ground.. . |  | nr | 1
Information provided to guide Bidder
|  | Ground elevation at borehole (approximate) | masl | 1372
|  | Yield | m3/hr |  | tbc
|  | Pump installation level below ground surface | m |  | tbc
|  | Riser pipe diameter | mm | DN 50
|  | Dynamic water level below ground surface | m |  | tbc
|  | Top water level in overhead tank | masl | 1387
Information to be provided by Bidder
|  | Manufacturers Pump reference No. | ref.
|  | Maximum flow at Installation indicated above | m3/hr
|  | Maximum pump head at installation indicated above | m3/hr
|  | Optimum flow at Installation indicated above | m3/hr
|  | Optimum head at Installation indicated above | m3/hr
|  | Pump efficiency at installation | %
|  | Input power required by pump | W
|  | Output power required by solar array | W
|  | No. of solar panels and arrays offered and guaranteed to meet requirement | nr
| 7.2 | Solar arrays to meet requirements c/w security fence and gate and lightning protection as per Drawing to be included in this Option
| 7.2.1 | Supply, install, erect and connect solar arrays to meet requirements c/w lightning protection as per Drawing and Specification | nr | 1 |  | 0
| 7.2.2 | Provide all materials and construct fenced and gated compound to contain solar array and associated chambers to Specification | LS | 1 |  | 0
| 7.2.3 | Supply and install DN 25 water pipe take-off from rising main and standpipe for solar cleansing system | LS | 1 |  | 0
| 7.2.4 | Provide solar array cleansing step ladder and extendable washer to Specification | LS | 1 |  | 0
Supply and Installation of 220 VAC standby generator of rated power
| 7.3 | Supply, Install and connect by manually operated changeover switch standby generator capable of providing the VAC power required to operate the submersible borehole pump as specified above at half-load c/w roofed lockable waterproof steel protection cabinet. | nr | 1 |  | 0
Information to be provided by Bidder
Manufacturers Generator Set reference No.
|  | Output kVA at 1500rpm, 220V, single-phase, 50Hz, with power factor of 1.0 | kVA
|  | Fuel type (petrol/diesel) | type
|  | Fuel tank capacity | l
Air or water cooled
|  | Sub-total |  |  |  | 0
|  | Contingencies (10%) |  |  |  | 0
|  | Taxes (VAT @16%) |  |  |  | 0
|  | Total |  |  |  | 0

## Kambazhi Pr Sch & RHC
UNICEF
Solar Powered Borehole Schemes in institutions in Meheba Refugee Camp & Host Communities
Kambazhi Primary School and RHC
Bill No. SCH5
| Item | Description | Unit | Qty | Rate (ZMW) | Amount (ZMW)
| Bill No. out, Demolition and Site Clearance |  |  |  |  | 0
| 1.1 | In collaboration with the Inspector of Works, and based upon pipe lengths and alignment shown on layout plan, agree upon final alignment of pipelines, road crossings, location of all tees, bends, isolating valves, air valves, washouts, tapstands, and consumer connection offtakes. Set out pipeline centre-lines, survey, agree upon Starting Surfaces, and final lengths and produce final plans at horizontal scale of 1:200 for approval before proceeding further. | LS | 1 |  | 0
| 1.2 | General Clearance for urban land & rough grass land along pipeline wayleaves (trench width plus 0.5 m on either side) | ha | 0.2 |  | 0
| 1.3 | Removal of tree stumps within approved alignment. PROVISIONAL SUM | nr | 1 |  | 0
| 1.4 | Cut down and remove trees and tree stumps within approved alignment only if specifically directed to do so by Inspector of Works following agreement from the Host Community PROVISIONAL SUM | nr | 1 |  | 0
| Bill No. 2: Excavation and backfilling of trenches - all pipelines |  |  |  |  | 0
| 2.1 | Excavate test pits along centre line of proposed pipeline to depth of 1m at least every 50 m | nr | 11 |  | 0
| 2.2 | Excavate and trim trench bed to depth not exceeding 1 m to ensure minimum cover to pipeline of 600 mm | m | 484.2 |  | 0
| 2.3 | Excavate and trim trench to depth not exceeding 1.5 m to ensure minimum cover to pipeline of 900 mm | m | 53.8 |  | 0
| 2.4 | Over excavate trench by a further depth of 150mm in areas identified by the Inspector of Works as requiring imported granular backfill RATE ONLY | m3 | 4.842 |  | 0
| 2.5 | Import, place and compact granular backfill in areas identified by the Inspector of Works as requiring imported granular backfill. RATE ONLY, | m3 | 4.842 |  | 0
| 2.6 | Place and compact sidefill and backfill using selected excavated material free of stones and tree roots to depth 300 mm above crown of pipe, and after compaction, other excavated material thereafter to final surface | m | 484.2 |  | 0
| 2.7 | Dispose of all surplus excavated material off-site | LS | 1 |  | 0
| Bill No. 3: Supply and Installation of rising main- borehole to elevated water tank |  |  |  |  | 0
All PE compression joints and fittings shall be supplied complete with suitable pipe joint stiffeners. All steel fittings shall be epoxy coated and all nuts and bolts galvanised. Rate shall include supply, lay, bed, joint , pressure test, sterilize and flushing of HDPE pipelines
| 3.1 | Raw water rising main from borehole to the Elevated Tank , HDPE DN50 (OD 63), SDR17, PN 10 | m | 6 |  | 0
| 3.2 | Supply and Installation of DN 40 parallel Woltman type bulk water meter, metrological class B, minimum display 1 m3/hr, suitable for vertical mounting, within water tank inlet riser pipe complete with strainer (metallic double flanged body c/w lockable meter box pipe surround). The meter assembly shall comprise: 1 No. DN50 to DN40 reducer, 1 DN40 500mm long straight pipe length, 1 DN 40 mm double flanged vertically mounted parallel Woltman type meter, located approximately 1.5 m above ground level, 1 DN 40 250 mm straight pipe length, and one DN40 to DN50 reducer. | set | 1 |  | 0
| 3.3 | Gate Valve, double flange, 50 mm non-rising spindle type, with 2 No. flanged restraining adapters st. fl. to PE DN 50, complete with valve riser and valve box to suit | set | 1 |  | 0
| 3.4 | Supply and install DN 25 water pipe take-off from rising mainand standpipe for solar cleansing system | LS | 1 |  | 0
| 3.5 | Provide solar array cleansing step ladder and extendable washer to Specification | LS | 1 |  | 0
|  | Carry forward |  |  |  | 0
|  | Brought forward |  |  |  | 0
| Bill No. 4: Tanks, Tankstands and Tap Stands |  |  |  |  | 0
Bidder shall supply outline details of water tank stand and tank c/w, pipework and fittings.
water tank stand manufacturer:
HDPE cylindrical tank manufacturer:
HDPE cylindrical tank supplier (if different):
Contractor shall supply full set of structural calculations and drawings for water tank stand certified by a registered structural engineer for written approval prior to fabrication.
| 4.1 | Conduct geotechnical investigations and design foundation and tank stand for the elevated tank | LS | 1 |  | 0
| 4.2 | Tank reinforced concrete foundations 1 m x 1m x 1.5 m deep inc. excavation, shuttering, concreting, curing, backfilling and disposal of excess spoil material from site | nr | 6 |  | 0
Supply and install 2 No. HDPE cylindrical tank on Contractor designed six vertical members) mild steel tankstand c/w with inlet float valves, all inflow, valved connecting, outflow, overflow, and scour (washout) pipework, fittings, adaptors and 6m high steel stand c/w access ladder and lightning arrestor.
4.3 | 4,3 | Capacity 10m3.(two no. of 5.0 m3) | nr | 1 |  | 0
| 4.4 | Supply and paint all mild steel in tank stand with two coats of zinc 82% rich paint in dry film | LS | 1 |  | 0
| 4.5 | Leak testing and disinfection of tank and pipework | nr | 1 |  | 0
| 4.6 | Provide & install float level indicator gauge on side of tank readable from ground level adjacent to tank | nr | 1 |  | 0
| 4.7 | Provide and install chlorine cartridge type inline doser in lockable chamber at start of tank outlet pipe c/w twelve months supply of chlorine cartridges. | LS | 1 |  | 0
| 4.8 | Provide materials for and construct tap stand and associated drainage | nr | 8 |  | 0
| Bill No. 5: Supply and Install Water Distribution Network |  |  |  |  | 0
All PE compression joints and fittings shall be supplied complete with suitable pipe joint stiffeners. All steel fittings shall be epoxy coated and all nuts and bolts galvanised. Rate shall include supply, lay, bed, joint , pressure test, sterilize and flushing of HDPE pipelines
| 5.1 | Network reticulation pipework HDPE DN50 (OD 63), SDR17, PN 10 | m | 386 |  | 0
| 5.2 | Equal tee compression fitting DN 50 x 50 x 50 mm | nr | 2 |  | 0
| 5.3 | Equal tee compression fitting DN 40 x 40 x 40 mm | nr | 1 |  | 0
| 5.4 | Compression reducer coupling 50mm x 40mm | nr | 6 |  | 0
| 5.5 | Compression reducer coupling 40mm x 32mm | nr | 2 |  | 0
| 5.6 | Network reticulation pipework HDPE DN 40mm, SDR17, PN 10 | m | 62 |  | 0
| 5.7 | Network reticulation pipework HDPE DN 32mm, SDR17, PN 10 | m | 84 |  | 0
| 5.8 | Compression fitting, elbow 90o DN 50mm | nr | 3 |  | 0
| 5.9 | End cap DN 32mm (compression type) | nr | 2 |  | 0
| 5.1 | Supply and install GI pipes 25mm dia c/w fittings to tap stands c/w isolating stop cock | nr | 8 |  | 0
| 5.11 | Supply and install heavy weight brass garden bib tap (non-lever arm type) | nr | 16 |  | 0
| 5.12 | Compression tee DN 40 x 40 x 1" male branch to connect to tap stand pipework | nr | 6 |  | 0
| 5.13 | Compression tee DN 32 x 32 x 1" male branch to connect to tap stand pipework | nr | 2 |  | 0
| 5.14 | Compression tee DN 50 x 50 x 1 1/2" male br., 1 No. female to male 1 1/2" to 1" thr. spigot to connect to tap stand pipework | nr | 5 |  | 0
| 5.15 | Gate Valve, double flange, 40 mm non-rising spindle type, with 2 No. flanged restraining adapters st. fl. to PE DN 40, complete with valve riser and valve box to suit | nr | 4 |  | 0
Air valve assembly consisting of 1 No. compression tee with threaded male 1 1/2" branch vertically upwards, 1 No. female to male thr. spigot, 1 No. Stopcock, thr. dble. socket 1", and 1 No. Single air valve, thr. female 1". RATE ONLY
| 5.16.1 | Compression tee DN 50 x 50 x 1 1/2" male br., 1 No. female to male 1 1/2" to 1" thr. spigot | set | 1
| 5.16.2 | Compression tee DN 40 x 40 x 1 1/2" male br., 1 No. female to male 1 1/2" to 1" thr. Spigot | set | 1
| 5.16.3 | Compression tee DN 32 x 32 x 1" male br, 1 No. female to male 1" to 1" thr. spigot | set | 1
|  | Carry forward |  |  |  | 0
|  | Brought forward |  |  |  | 0
| Bill No. 6: Concrete Works to all Pipelines |  |  |  |  | 0
All unreinforced concrete works shall be in medium strength concrete unless otherwise indicated. Where bends less than 45o are obtained by bending the pipe, radius not less than 35 x pipe diameter, and provided there is no compression joint with 5 metres of either end of radius, no separate thrust block is required.
| 6.1 | Over excavate in trench bed at all gate valves, air valve assemblies and steel fittings and cast support slab to full width of trench with other dimensions being the length of the valve or the fitting between flanges or between the compression tightening nuts and depth below trench bed of 150 mm | nr | 5 |  | 0
| 6.2 | At all 45o and 90o bends, pipeline tees, and end caps, provide and subsequently remove shuttering and cast thrust blocks against undisturbed trench bed and trench wall | nr | 8 |  | 0
| 6.3 | Supply all materials and cast and complete air-valve chamber. RATE ONLY | nr | 1
| Bill No. 7: Water Distribution Network | Electromechanical |  |  |  | 0
Bidder shall supply details of proposed pumpset c/w shroud, and standby generator for which there shall be a local agent
proposed submersible hybrid DC/AC pumpset manufacturer and agent:
proposed standby generator manufacturer and agent:
|  | confirm manufactures brochures included with bid |  | yes / no
No change from these manufacturers or agents shall be permitted without prior written approval from the Consultant
Submersible 48 VDC Borehole Pump
| 7.1 | Supply and install a hybrid DC/AC borehole submersible pump suitable for a borehole of ID 5" capable of being powered from either a 48 VDC or a nominal 230 VAC source c/w cabled connection to power sources located within 10 m of borehole head, pumping into an overhead tank with top water inlet 14 m above ground.. . |  | nr | 1
Information provided to guide Bidder
|  | Ground elevation at borehole (approximate) | masl | 1372
|  | Yield | m3/hr | 1.5 | tbc
|  | Pump installation level below ground surface | m | 40 | tbc
|  | Riser pipe diameter | mm | DN 50
|  | Dynamic water level below ground surface | m | 30 | tbc
|  | Top water level in overhead tank | masl | 1386
Information to be provided by Bidder
|  | Manufacturers Pump reference No. | ref.
|  | Maximum flow at Installation indicated above | m3/hr
|  | Maximum pump head at installation indicated above | m3/hr
|  | Optimum flow at Installation indicated above | m3/hr
|  | Optimum head at Installation indicated above | m3/hr
|  | Pump efficiency at installation | %
|  | Input power required by pump | W
|  | Output power required by solar array | W
|  | No. of solar panels and arrays offered and guaranteed to meet requirement | nr
| 7.2 | Solar arrays to meet requirements c/w security fence and gate and lightning protection as per Drawing to be included in this Option
| 7.2.1 | Supply, install, erect and connect solar arrays to meet requirements c/w lightning protection as per Drawing and Specification | nr | 1 |  | 0
| 7.2.2 | Provide all materials and construct fenced and gated compound to contain solar array and associated chambers to Specification | LS | 1 |  | 0
| 7.2.3 | Supply and install DN 25 water pipe take-off from rising main and standpipe for solar cleansing system | LS | 1 |  | 0
| 7.2.4 | Provide solar array cleansing step ladder and extendable washer to Specification | LS | 1 |  | 0
Supply and Installation of 220 VAC standby generator of rated power
| 7.3 | Supply, Install and connect by manually operated changeover switch standby generator capable of providing the VAC power required to operate the submersible borehole pump as specified above at half-load c/w roofed lockable waterproof steel protection cabinet. | nr | 1 |  | 0
Information to be provided by Bidder
Manufacturers Generator Set reference No.
|  | Output kVA at 1500rpm, 220V, single-phase, 50Hz, with power factor of 1.0 | kVA
|  | Fuel type (petrol/diesel) | type
|  | Fuel tank capacity | l
Air or water cooled
|  | Sub-total |  |  |  | 0
|  | Contingencies (10%) |  |  |  | 0
|  | Taxes (VAT @16%) |  |  |  | 0
|  | Total |  |  |  | 0

## Shilenda Pr Sch
UNICEF
Solar Powered Borehole Schemes in institutions in Meheba Refugee Camp & Host Communities
Shilenda Primary School
Bill No. SCH6
| Item | Description | Unit | Qty | Rate (ZMW) | Amount (ZMW)
| Bill No. out, Demolition and Site Clearance |  |  |  |  | 0
| 1.1 | In collaboration with the Inspector of Works, and based upon pipe lengths and alignment shown on layout plan, agree upon final alignment of pipelines, road crossings, location of all tees, bends, isolating valves, air valves, washouts, tapstands, and consumer connection offtakes. Set out pipeline centre-lines, survey, agree upon Starting Surfaces, and final lengths and produce final plans at horizontal scale of 1:200 for approval before proceeding further. | LS | 1 |  | 0
| 1.2 | General Clearance for urban land & rough grass land along pipeline wayleaves (trench width plus 0.5 m on either side) | ha | 0.2 |  | 0
| 1.3 | Removal of tree stumps within approved alignment. PROVISIONAL SUM | nr | 1 |  | 0
| 1.4 | Cut down and remove trees and tree stumps within approved alignment only if specifically directed to do so by Inspector of Works following agreement from the Host Community PROVISIONAL SUM | nr | 1 |  | 0
| Bill No. 2: Excavation and backfilling of trenches - all pipelines |  |  |  |  | 0
| 2.1 | Excavate test pits along centre line of proposed pipeline to depth of 1m at least every 50 m | nr | 11 |  | 0
| 2.2 | Excavate and trim trench bed to depth not exceeding 1 m to ensure minimum cover to pipeline of 600 mm | m | 484.2 |  | 0
| 2.3 | Excavate and trim trench to depth not exceeding 1.5 m to ensure minimum cover to pipeline of 900 mm | m | 53.8 |  | 0
| 2.4 | Over excavate trench by a further depth of 150mm in areas identified by the Inspector of Works as requiring imported granular backfill RATE ONLY | m3 | 4.842 |  | 0
| 2.5 | Import, place and compact granular backfill in areas identified by the Inspector of Works as requiring imported granular backfill. RATE ONLY, | m3 | 4.842 |  | 0
| 2.6 | Place and compact sidefill and backfill using selected excavated material free of stones and tree roots to depth 300 mm above crown of pipe, and after compaction, other excavated material thereafter to final surface | m | 484.2 |  | 0
| 2.7 | Dispose of all surplus excavated material off-site | LS | 1 |  | 0
| Bill No. 3: Supply and Installation of rising main- borehole to elevated water tank |  |  |  |  | 0
All PE compression joints and fittings shall be supplied complete with suitable pipe joint stiffeners. All steel fittings shall be epoxy coated and all nuts and bolts galvanised. Rate shall include supply, lay, bed, joint , pressure test, sterilize and flushing of HDPE pipelines
| 3.1 | Raw water rising main from borehole to the Elevated Tank , HDPE DN50 (OD 63), SDR17, PN 10 | m | 6 |  | 0
| 3.2 | Supply and Installation of DN 40 parallel Woltman type bulk water meter, metrological class B, minimum display 1 m3/hr, suitable for vertical mounting, within water tank inlet riser pipe complete with strainer (metallic double flanged body c/w lockable meter box pipe surround). The meter assembly shall comprise: 1 No. DN50 to DN40 reducer, 1 DN40 500mm long straight pipe length, 1 DN 40 mm double flanged vertically mounted parallel Woltman type meter, located approximately 1.5 m above ground level, 1 DN 40 250 mm straight pipe length, and one DN40 to DN50 reducer. | set | 1 |  | 0
| 3.3 | Gate Valve, double flange, 50 mm non-rising spindle type, with 2 No. flanged restraining adapters st. fl. to PE DN 50, complete with valve riser and valve box to suit | set | 1 |  | 0
| 3.4 | Supply and install DN 25 water pipe take-off from rising mainand standpipe for solar cleansing system | LS | 1 |  | 0
| 3.5 | Provide solar array cleansing step ladder and extendable washer to Specification | LS | 1 |  | 0
|  | Carry forward |  |  |  | 0
|  | Brought forward |  |  |  | 0
| Bill No. 4: Tanks, Tankstands and Tap Stands |  |  |  |  | 0
Bidder shall supply outline details of water tank stand and tank c/w, pipework and fittings.
water tank stand manufacturer:
HDPE cylindrical tank manufacturer:
HDPE cylindrical tank supplier (if different):
Contractor shall supply full set of structural calculations and drawings for water tank stand certified by a registered structural engineer for written approval prior to fabrication.
| 4.1 | Conduct geotechnical investigations and design foundation and tank stand for the elevated tank | LS | 1 |  | 0
| 4.2 | Tank reinforced concrete foundations 1 m x 1m x 1.5 m deep inc. excavation, shuttering, concreting, curing, backfilling and disposal of excess spoil material from site | nr | 6 |  | 0
Supply and install 2 No. HDPE cylindrical tank on Contractor designed six vertical members) mild steel tankstand c/w with inlet float valves, all inflow, valved connecting, outflow, overflow, and scour (washout) pipework, fittings, adaptors and 6m high steel stand c/w access ladder and lightning arrestor.
4.3 | 4,3 | Capacity 10m3.(two no. of 5.0 m3) | nr | 1 |  | 0
| 4.4 | Supply and paint all mild steel in tank stand with two coats of zinc 82% rich paint in dry film | LS | 1 |  | 0
| 4.5 | Leak testing and disinfection of tank and pipework | nr | 1 |  | 0
| 4.6 | Provide & install float level indicator gauge on side of tank readable from ground level adjacent to tank | nr | 1 |  | 0
| 4.7 | Provide and install chlorine cartridge type inline doser in lockable chamber at start of tank outlet pipe c/w twelve months supply of chlorine cartridges. | LS | 1 |  | 0
| 4.8 | Provide materials for and construct tap stand and associated drainage | nr | 8 |  | 0
| Bill No. 5: Supply and Install Water Distribution Network |  |  |  |  | 0
All PE compression joints and fittings shall be supplied complete with suitable pipe joint stiffeners. All steel fittings shall be epoxy coated and all nuts and bolts galvanised. Rate shall include supply, lay, bed, joint , pressure test, sterilize and flushing of HDPE pipelines
| 5.1 | Network reticulation pipework HDPE DN50 (OD 63), SDR17, PN 10 | m | 386 |  | 0
| 5.2 | Equal tee compression fitting DN 50 x 50 x 50 mm | nr | 2 |  | 0
| 5.3 | Equal tee compression fitting DN 40 x 40 x 40 mm | nr | 1 |  | 0
| 5.4 | Compression reducer coupling 50mm x 40mm | nr | 6 |  | 0
| 5.5 | Compression reducer coupling 40mm x 32mm | nr | 2 |  | 0
| 5.6 | Network reticulation pipework HDPE DN 40mm, SDR17, PN 10 | m | 62 |  | 0
| 5.7 | Network reticulation pipework HDPE DN 32mm, SDR17, PN 10 | m | 84 |  | 0
| 5.8 | Compression fitting, elbow 90o DN 50mm | nr | 3 |  | 0
| 5.9 | End cap DN 32mm (compression type) | nr | 2 |  | 0
| 5.1 | Supply and install GI pipes 25mm dia c/w fittings to tap stands c/w isolating stop cock | nr | 8 |  | 0
| 5.11 | Supply and install heavy weight brass garden bib tap (non-lever arm type) | nr | 16 |  | 0
| 5.12 | Compression tee DN 40 x 40 x 1" male branch to connect to tap stand pipework | nr | 6 |  | 0
| 5.13 | Compression tee DN 32 x 32 x 1" male branch to connect to tap stand pipework | nr | 2 |  | 0
| 5.14 | Compression tee DN 50 x 50 x 1 1/2" male br., 1 No. female to male 1 1/2" to 1" thr. spigot to connect to tap stand pipework | nr | 5 |  | 0
| 5.15 | Gate Valve, double flange, 40 mm non-rising spindle type, with 2 No. flanged restraining adapters st. fl. to PE DN 40, complete with valve riser and valve box to suit | nr | 4 |  | 0
Air valve assembly consisting of 1 No. compression tee with threaded male 1 1/2" branch vertically upwards, 1 No. female to male thr. spigot, 1 No. Stopcock, thr. dble. socket 1", and 1 No. Single air valve, thr. female 1". RATE ONLY
| 5.16.1 | Compression tee DN 50 x 50 x 1 1/2" male br., 1 No. female to male 1 1/2" to 1" thr. spigot | set | 1
| 5.16.2 | Compression tee DN 40 x 40 x 1 1/2" male br., 1 No. female to male 1 1/2" to 1" thr. Spigot | set | 1
| 5.16.3 | Compression tee DN 32 x 32 x 1" male br, 1 No. female to male 1" to 1" thr. spigot | set | 1
|  | Carry forward |  |  |  | 0
|  | Brought forward |  |  |  | 0
| Bill No. 6: Concrete Works to all Pipelines |  |  |  |  | 0
All unreinforced concrete works shall be in medium strength concrete unless otherwise indicated. Where bends less than 45o are obtained by bending the pipe, radius not less than 35 x pipe diameter, and provided there is no compression joint with 5 metres of either end of radius, no separate thrust block is required.
| 6.1 | Over excavate in trench bed at all gate valves, air valve assemblies and steel fittings and cast support slab to full width of trench with other dimensions being the length of the valve or the fitting between flanges or between the compression tightening nuts and depth below trench bed of 150 mm | nr | 5 |  | 0
| 6.2 | At all 45o and 90o bends, pipeline tees, and end caps, provide and subsequently remove shuttering and cast thrust blocks against undisturbed trench bed and trench wall | nr | 8 |  | 0
| 6.3 | Supply all materials and cast and complete air-valve chamber. RATE ONLY | nr | 1
| Bill No. 7: Water Distribution Network | Electromechanical |  |  |  | 0
Bidder shall supply details of proposed pumpset c/w shroud, and standby generator for which there shall be a local agent
proposed submersible hybrid DC/AC pumpset manufacturer and agent:
proposed standby generator manufacturer and agent:
|  | confirm manufactures brochures included with bid |  | yes / no
No change from these manufacturers or agents shall be permitted without prior written approval from the Consultant
Submersible 48 VDC Borehole Pump
| 7.1 | Supply and install a hybrid DC/AC borehole submersible pump suitable for a borehole of ID 5" capable of being powered from either a 48 VDC or a nominal 230 VAC source c/w cabled connection to power sources located within 10 m of borehole head, pumping into an overhead tank with top water inlet 14 m above ground.. . |  | nr | 1
Information provided to guide Bidder
|  | Ground elevation at borehole (approximate) | masl | 1301
|  | Yield | m3/hr | 1.3 | tbc
|  | Pump installation level below ground surface | m | 30 | tbc
|  | Riser pipe diameter | mm | DN 50
|  | Dynamic water level below ground surface | m | 22 | tbc
|  | Top water level in overhead tank | masl | 1319
Information to be provided by Bidder
|  | Manufacturers Pump reference No. | ref.
|  | Maximum flow at Installation indicated above | m3/hr
|  | Maximum pump head at installation indicated above | m3/hr
|  | Optimum flow at Installation indicated above | m3/hr
|  | Optimum head at Installation indicated above | m3/hr
|  | Pump efficiency at installation | %
|  | Input power required by pump | W
|  | Output power required by solar array | W
|  | No. of solar panels and arrays offered and guaranteed to meet requirement | nr
| 7.2 | Solar arrays to meet requirements c/w security fence and gate and lightning protection as per Drawing to be included in this Option
| 7.2.1 | Supply, install, erect and connect solar arrays to meet requirements c/w lightning protection as per Drawing and Specification | nr | 1 |  | 0
| 7.2.2 | Provide all materials and construct fenced and gated compound to contain solar array and associated chambers to Specification | LS | 1 |  | 0
| 7.2.3 | Supply and install DN 25 water pipe take-off from rising main and standpipe for solar cleansing system | LS | 1 |  | 0
| 7.2.4 | Provide solar array cleansing step ladder and extendable washer to Specification | LS | 1 |  | 0
Supply and Installation of 220 VAC standby generator of rated power
| 7.3 | Supply, Install and connect by manually operated changeover switch standby generator capable of providing the VAC power required to operate the submersible borehole pump as specified above at half-load c/w roofed lockable waterproof steel protection cabinet. | nr | 1 |  | 0
Information to be provided by Bidder
Manufacturers Generator Set reference No.
|  | Output kVA at 1500rpm, 220V, single-phase, 50Hz, with power factor of 1.0 | kVA
|  | Fuel type (petrol/diesel) | type
|  | Fuel tank capacity | l
Air or water cooled
|  | Sub-total |  |  |  | 0
|  | Contingencies (10%) |  |  |  | 0
|  | Taxes (VAT @16%) |  |  |  | 0
|  | Total |  |  |  | 0

## Meheba B RHC
UNICEF
Solar Powered Borehole Schemes in institutions in Meheba Refugee Camp & Host Communities
Meheba B RHC
Bill No. RHC1:
Item | Description | Unit | Qty | Rate (ZMW) | Amount (ZMW)
Bill No. out, Demolition and Site Clearance |  |  |  |  | 0
1.1 | In collaboration with the Inspector of Works, and based upon pipe lengths and alignment shown on layout plan, agree upon final alignment of pipelines, road crossings, location of all tees, bends, isolating valves, air valves, washouts, tapstands, and consumer connection offtakes. Set out pipeline centre-lines, survey, agree upon Starting Surfaces, and final lengths and produce final plans at horizontal scale of 1:200 for approval before proceeding further. | LS | 1 |  | 0
1.2 | General Clearance for urban land & rough grass land along pipeline wayleaves (trench width plus 0.5 m on either side) | ha | 0.1 |  | 0
1.3 | Removal of tree stumps within approved alignment. PROVISIONAL SUM | nr | 1 |  | 0
1.4 | Cut down and remove trees and tree stumps within approved alignment only if specifically directed to do so by Inspector of Works following agreement from the Host Community PROVISIONAL SUM | nr | 1 |  | 0
Bill No. 2: Excavation and backfilling of trenches - all pipelines |  |  |  |  | 0
2.1 | Excavate test pits along centre line of proposed pipeline to depth of 1m at least every 50 m | nr | 9 |  | 0
2.2 | Excavate and trim trench bed to depth not exceeding 1 m to ensure minimum cover to pipeline of 600 mm | m | 367.2 |  | 0
2.3 | Excavate and trim trench to depth not exceeding 1.5 m to ensure minimum cover to pipeline of 900 mm | m | 40.8 |  | 0
2.4 | Over excavate trench by a further depth of 150mm in areas identified by the Inspector of Works as requiring imported granular backfill RATE ONLY | m3 | 3.672 |  | 0
2.5 | Import, place and compact granular backfill in areas identified by the Inspector of Works as requiring imported granular backfill. RATE ONLY, | m3 | 3.672 |  | 0
2.6 | Place and compact sidefill and backfill using selected excavated material free of stones and tree roots to depth 300 mm above crown of pipe, and after compaction, other excavated material thereafter to final surface | m | 367.2 |  | 0
2.7 | Dispose of all surplus excavated material off-site | LS | 1 |  | 0
Bill No. 3: Supply and Installation of rising main- borehole to elevated water tank |  |  |  |  | 0
All PE compression joints and fittings shall be supplied complete with suitable pipe joint stiffeners. All steel fittings shall be epoxy coated and all nuts and bolts galvanised. Rate shall include supply, lay, bed, joint , pressure test, sterilize and flushing of HDPE pipelines
3.1 | Raw water rising main from borehole to the Elevated Tank , HDPE DN50 (OD 63), SDR17, PN 10 | m | 51 |  | 0
3.2 | Supply and Installation of DN 40 parallel Woltman type bulk water meter, metrological class B, minimum display 1 m3/hr, suitable for vertical mounting, within water tank inlet riser pipe complete with strainer (metallic double flanged body c/w lockable meter box pipe surround). The meter assembly shall comprise: 1 No. DN50 to DN40 reducer, 1 DN40 500mm long straight pipe length, 1 DN 40 mm double flanged vertically mounted parallel Woltman type meter, located approximately 1.5 m above ground level, 1 DN 40 250 mm straight pipe length, and one DN40 to DN50 reducer. | set | 1 |  | 0
3.3 | Gate Valve, double flange, 50 mm non-rising spindle type, with 2 No. flanged restraining adapters st. fl. to PE DN 50, complete with valve riser and valve box to suit | set | 1 |  | 0
3.4 | Supply and install DN 25 water pipe take-off from rising mainand standpipe for solar cleansing system | LS | 1 |  | 0
3.5 | Provide solar array cleansing step ladder and extendable washer to Specification | LS | 1 |  | 0
| Carry forward |  |  |  | 0
| Brought forward |  |  |  | 0
Bill No. 4: Tanks, Tankstands and Tap Stands |  |  |  |  | 0
Bidder shall supply outline details of water tank stand and tank c/w, pipework and fittings.
water tank stand manufacturer:
HDPE cylindrical tank manufacturer:
HDPE cylindrical tank supplier (if different):
Contractor shall supply full set of structural calculations and drawings for water tank stand certified by a registered structural engineer for written approval prior to fabrication.
4.1 | Conduct geotechnical investigations and design foundation and tank stand for the elevated tank | LS | 1 |  | 0
4.2 | Tank reinforced concrete foundations 1 m x 1m x 1.5 m deep inc. excavation, shuttering, concreting, curing, backfilling and disposal of excess spoil material from site | nr | 6 |  | 0
Supply and install 2 No. HDPE cylindrical tank on Contractor designed six vertical members) mild steel tankstand c/w with inlet float valves, all inflow, valved connecting, outflow, overflow, and scour (washout) pipework, fittings, adaptors and 6m high steel stand c/w access ladder and lightning arrestor.
4.3 | Capacity 10m3.(two no. of 5m3) | nr | 1 |  | 0
4.4 | Supply and paint all mild steel in tank stand with two coats of zinc 82% rich paint in dry film | LS | 1 |  | 0
4.5 | Leak testing and disinfection of tank and pipework | nr | 1 |  | 0
4.6 | Provide & install float level indicator gauge on side of tank readable from ground level adjacent to tank | nr | 1 |  | 0
4.7 | Provide and install chlorine cartridge type inline doser in lockable chamber at start of tank outlet pipe c/w twelve months supply of chlorine cartridges. | LS | 1 |  | 0
4.8 | Provide materials for and construct tap stand and associated drainage | nr | 4 |  | 0
Bill No. 5: Supply and Install Water Distribution Network |  |  |  |  | 0
All PE compression joints and fittings shall be supplied complete with suitable pipe joint stiffeners. All steel fittings shall be epoxy coated and all nuts and bolts galvanised. Rate shall include supply, lay, bed, joint , pressure test, sterilize and flushing of HDPE pipelines
5.1 | Network reticulation pipework HDPE DN50 (OD 63), SDR17, PN 10 | m | 204 |  | 0
5.2 | Equal tee compression fitting DN 40 x 40 x 40 mm | nr | 1 |  | 0
5.3 | Unequal reducing tee compression fitting DN 50 x 50 x 40 mm | nr | 1 |  | 0
5.4 | Unequal reducing tee compression fitting DN 40 x 40 x 32 mm | nr | 4 |  | 0
5.5 | Compression reducer coupling 50mm x 40mm | nr | 5 |  | 0
5.6 | Network reticulation pipework HDPE DN 40mm, SDR17, PN 10 | m | 153 |  | 0
5.7 | Compression fitting, elbow 90o DN 50mm | nr | 2 |  | 0
5.8 | Compression fitting, elbow 90o DN 40mm | nr | 5 |  | 0
5.9 | End cap DN 32mm (compression type) | nr | 4 |  | 0
5.1 | Saddle clamp 32mm x 3/4" to supply individual consumer connection | nr | 4 |  | 0
5.11 | Supply and install GI pipes 25mm dia c/w fittings to tap stands c/w isolating stop cock | nr | 4 |  | 0
5.12 | Supply and install heavy weight brass garden bib tap (non-lever arm type) | nr | 8 |  | 0
5.13 | Compression tee DN 40 x 40 x 1" male branch to connect to tap stand pipework | nr | 1 |  | 0
5.14 | Compression tee DN 32 x 32 x 1" male branch to connect to tap stand pipework | nr | 0 |  | 0
5.15 | Compression tee DN 50 x 50 x 1 1/2" male br., 1 No. female to male 1 1/2" to 1" thr. spigot to connect to tap stand pipework | nr | 3 |  | 0
5.16 | Gate Valve, double flange, 40 mm non-rising spindle type, with 2 No. flanged restraining adapters st. fl. to PE DN 40, complete with valve riser and valve box to suit | nr | 3 |  | 0
Air valve assembly consisting of 1 No. compression tee with threaded male 1 1/2" branch vertically upwards, 1 No. female to male thr. spigot, 1 No. Stopcock, thr. dble. socket 1", and 1 No. Single air valve, thr. female 1". RATE ONLY
5.17.1 | Compression tee DN 50 x 50 x 1 1/2" male br., 1 No. female to male 1 1/2" to 1" thr. spigot | set | 1
5.17.2 | Compression tee DN 40 x 40 x 1 1/2" male br., 1 No. female to male 1 1/2" to 1" thr. Spigot | set | 1
| Carry forward |  |  |  | 0
| Brought forward |  |  |  | 0
Bill No. 6: Concrete Works to all Pipelines |  |  |  |  | 0
All unreinforced concrete works shall be in medium strength concrete unless otherwise indicated. Where bends less than 45o are obtained by bending the pipe, radius not less than 35 x pipe diameter, and provided there is no compression joint with 5 metres of either end of radius, no separate thrust block is required.
6.1 | Over excavate in trench bed at all gate valves, air valve assemblies and steel fittings and cast support slab to full width of trench with other dimensions being the length of the valve or the fitting between flanges or between the compression tightening nuts and depth below trench bed of 150 mm | nr | 4 |  | 0
6.2 | At all 45o and 90o bends, pipeline tees, and end caps, provide and subsequently remove shuttering and cast thrust blocks against undisturbed trench bed and trench wall | nr | 12 |  | 0
6.3 | Supply all materials and cast and complete air-valve chamber. RATE ONLY | nr | 1
Bill No. 7: Water Distribution Network | Electromechanical |  |  |  | 0
Bidder shall supply details of proposed pumpset c/w shroud, and standby generator for which there shall be a local agent
proposed submersible hybrid DC/AC pumpset manufacturer and agent:
proposed standby generator manufacturer and agent:
| confirm manufactures brochures included with bid |  | yes / no
No change from these manufacturers or agents shall be permitted without prior written approval from the Consultant
Submersible 48 VDC Borehole Pump
7.1 | Supply and install a hybrid DC/AC borehole submersible pump suitable for a borehole of ID 5" capable of being powered from either a 48 VDC or a nominal 230 VAC source c/w cabled connection to power sources located within 10 m of borehole head, pumping into an overhead tank with top water inlet 14 m above ground.. . |  | nr | 1
Information provided to guide Bidder
| Ground elevation at borehole (approximate) | masl | 1322
| Yield | m3/hr | 0.5 | tbc
| Pump installation level below ground surface | m | 39 | tbc
| Riser pipe diameter | mm | DN 50
| Dynamic water level below ground surface | m | 30 | tbc
| Top water level in overhead tank | masl | 1336
Information to be provided by Bidder
| Manufacturers Pump reference No. | ref.
| Maximum flow at Installation indicated above | m3/hr
| Maximum pump head at installation indicated above | m3/hr
| Optimum flow at Installation indicated above | m3/hr
| Optimum head at Installation indicated above | m3/hr
| Pump efficiency at installation | %
| Input power required by pump | W
| Output power required by solar array | W
| No. of solar panels and arrays offered and guaranteed to meet requirement | nr
7.2 | Solar arrays to meet requirements c/w security fence and gate and lightning protection as per Drawing to be included in this Option
7.2.1 | Supply, install, erect and connect solar arrays to meet requirements c/w lightning protection as per Drawing and Specification | nr | 1 |  | 0
7.2.2 | Provide all materials and construct fenced and gated compound to contain solar array and associated chambers to Specification | LS | 1 |  | 0
7.2.3 | Supply and install DN 25 water pipe take-off from rising main and standpipe for solar cleansing system | LS | 1 |  | 0
7.2.4 | Provide solar array cleansing step ladder and extendable washer to Specification | LS | 1 |  | 0
Supply and Installation of 220 VAC standby generator of rated power
7.3 | Supply, Install and connect by manually operated changeover switch standby generator capable of providing the VAC power required to operate the submersible borehole pump as specified above at half-load c/w roofed lockable waterproof steel protection cabinet. | nr | 1 |  | 0
Information to be provided by Bidder
Manufacturers Generator Set reference No.
| Output kVA at 1500rpm, 220V, single-phase, 50Hz, with power factor of 1.0 | kVA
| Fuel type (petrol/diesel) | type
| Fuel tank capacity | l
Air or water cooled
| Sub-total |  |  |  | 0
| Contingencies (10%) |  |  |  | 0
| Taxes (VAT @16%) |  |  |  | 0
| Total |  |  |  | 0

## Meheba A RHC & Pr Sch
UNICEF
Solar Powered Borehole Schemes in institutions in Kaoma District Refugee Camp & Host Communities
Meheba A RHC with extension to Primary School
Bill No. RHC2:
Item | Description | Unit | Qty | Rate (ZMW) | Amount (ZMW)
Bill No. out, Demolition and Site Clearance |  |  |  |  | 0
1.1 | In collaboration with the Inspector of Works, and based upon pipe lengths and alignment shown on layout plan, agree upon final alignment of pipelines, road crossings, location of all tees, bends, isolating valves, air valves, washouts, tapstands, and consumer connection offtakes. Set out pipeline centre-lines, survey, agree upon Starting Surfaces, and final lengths and produce final plans at horizontal scale of 1:200 for approval before proceeding further. | LS | 1 |  | 0
1.2 | General Clearance for urban land & rough grass land along pipeline wayleaves (trench width plus 0.5 m on either side) | ha | 0.1 |  | 0
1.3 | Removal of tree stumps within approved alignment. PROVISIONAL SUM | nr | 1 |  | 0
1.4 | Cut down and remove trees and tree stumps within approved alignment only if specifically directed to do so by Inspector of Works following agreement from the Host Community PROVISIONAL SUM | nr | 1 |  | 0
Bill No. 2: Excavation and backfilling of trenches - all pipelines |  |  |  |  | 0
2.1 | Excavate test pits along centre line of proposed pipeline to depth of 1m at least every 50 m | nr | 5 |  | 0
2.2 | Excavate and trim trench bed to depth not exceeding 1 m to ensure minimum cover to pipeline of 600 mm | m | 219.6 |  | 0
2.3 | Excavate and trim trench to depth not exceeding 1.5 m to ensure minimum cover to pipeline of 900 mm | m | 24.4 |  | 0
2.4 | Over excavate trench by a further depth of 150mm in areas identified by the Inspector of Works as requiring imported granular backfill RATE ONLY | m3 | 2.196 |  | 0
2.5 | Import, place and compact granular backfill in areas identified by the Inspector of Works as requiring imported granular backfill. RATE ONLY, | m3 | 2.196 |  | 0
2.6 | Place and compact sidefill and backfill using selected excavated material free of stones and tree roots to depth 300 mm above crown of pipe, and after compaction, other excavated material thereafter to final surface | m | 219.6 |  | 0
2.7 | Dispose of all surplus excavated material off-site | LS | 1 |  | 0
Bill No. 3: Supply and Installation of rising main- borehole to elevated water tank |  |  |  |  | 0
All PE compression joints and fittings shall be supplied complete with suitable pipe joint stiffeners. All steel fittings shall be epoxy coated and all nuts and bolts galvanised. Rate shall include supply, lay, bed, joint , pressure test, sterilize and flushing of HDPE pipelines
3.1 | Raw water rising main from borehole to the Elevated Tank , HDPE DN50 (OD 63), SDR17, PN 10 | m | 62 |  | 0
3.2 | Compression fitting, elbow 45o DN 50mm | nr | 1 |  | 0
3.3 | Supply and Installation of DN 40 parallel Woltman type bulk water meter, metrological class B, minimum display 1 m3/hr, suitable for vertical mounting, within water tank inlet riser pipe complete with strainer (metallic double flanged body c/w lockable meter box pipe surround). The meter assembly shall comprise: 1 No. DN50 to DN40 reducer, 1 DN40 500mm long straight pipe length, 1 DN 40 mm double flanged vertically mounted parallel Woltman type meter, located approximately 1.5 m above ground level, 1 DN 40 250 mm straight pipe length, and one DN40 to DN50 reducer. | set | 1 |  | 0
3.4 | Gate Valve, double flange, 50 mm non-rising spindle type, with 2 No. flanged restraining adapters st. fl. to PE DN 50, complete with valve riser and valve box to suit | set | 1 |  | 0
3.5 | Supply and install DN 25 water pipe take-off from rising mainand standpipe for solar cleansing system | LS | 1 |  | 0
3.6 | Provide solar array cleansing step ladder and extendable washer to Specification | LS | 1 |  | 0
| Carry forward |  |  |  | 0
| Brought forward |  |  |  | 0
Bill No. 4: Tanks, Tankstands and Tap Stands |  |  |  |  | 0
Bidder shall supply outline details of water tank stand and tank c/w, pipework and fittings.
water tank stand manufacturer:
HDPE cylindrical tank manufacturer:
HDPE cylindrical tank supplier (if different):
Contractor shall supply full set of structural calculations and drawings for water tank stand certified by a registered structural engineer for written approval prior to fabrication.
4.1 | Conduct geotechnical investigations and design foundation and tank stand for the elevated tank | LS | 1 |  | 0
4.2 | Tank reinforced concrete foundations 1 m x 1m x 1.5 m deep inc. excavation, shuttering, concreting, curing, backfilling and disposal of excess spoil material from site | nr | 6 |  | 0
Supply and install 2 No. HDPE cylindrical tank on Contractor designed six vertical members) mild steel tankstand c/w with inlet float valves, all inflow, valved connecting, outflow, overflow, and scour (washout) pipework, fittings, adaptors and 6m high steel stand c/w access ladder and lightning arrestor.
4.3 | Capacity 10m3.(two no. of 5m3) | nr | 1 |  | 0
4.4 | Supply and paint all mild steel in tank stand with two coats of zinc 82% rich paint in dry film | LS | 1 |  | 0
4.5 | Leak testing and disinfection of tank and pipework | nr | 1 |  | 0
4.6 | Provide & install float level indicator gauge on side of tank readable from ground level adjacent to tank | nr | 1 |  | 0
4.7 | Provide and install chlorine cartridge type inline doser in lockable chamber at start of tank outlet pipe c/w twelve months supply of chlorine cartridges. | LS | 1 |  | 0
4.8 | Provide materials for and construct tap stand and associated drainage | nr | 2 |  | 0
Bill No. 5: Supply and Install Water Distribution Network |  |  |  |  | 0
All PE compression joints and fittings shall be supplied complete with suitable pipe joint stiffeners. All steel fittings shall be epoxy coated and all nuts and bolts galvanised. Rate shall include supply, lay, bed, joint , pressure test, sterilize and flushing of HDPE pipelines
5.1 | Equal tee compression fitting DN 40 x 40 x 40 mm | nr | 1 |  | 0
5.2 | Unequal reducing tee compression fitting DN 40 x 40 x 32 mm | nr | 6 |  | 0
5.3 | Network reticulation pipework HDPE DN 40mm, SDR17, PN 10 | m | 48
5.4 | Network reticulation pipework HDPE DN 40mm, SDR17, PN 10 | m | 114 |  | 0
5.5 | Network reticulation pipework HDPE DN 32mm, SDR17, PN 10 | m | 20 |  | 0
5.6 | Compression fitting, elbow 90o DN 40mm | nr | 4 |  | 0
5.7 | End cap DN 32mm (compression type) | nr | 6 |  | 0
5.8 | Saddle clamp 32mm x 3/4" to supply individual consumer connection | nr | 6 |  | 0
5.9 | Supply and install GI pipes 25mm dia c/w fittings to tap stands c/w isolating stop cock | nr | 2 |  | 0
5.1 | Supply and install heavy weight brass garden bib tap (non-lever arm type) | nr | 4 |  | 0
5.11 | Compression tee DN 40 x 40 x 1" male branch to connect to tap stand pipework | nr | 2 |  | 0
5.12 | Gate Valve, double flange, 40 mm non-rising spindle type, with 2 No. flanged restraining adapters st. fl. to PE DN 40, complete with valve riser and valve box to suit | nr | 3 |  | 0
Air valve assembly consisting of 1 No. compression tee with threaded male 1 1/2" branch vertically upwards, 1 No. female to male thr. spigot, 1 No. Stopcock, thr. dble. socket 1", and 1 No. Single air valve, thr. female 1". RATE ONLY
5.13 | Compression tee DN 40 x 40 x 1 1/2" male br., 1 No. female to male 1 1/2" to 1" thr. Spigot | set | 1
| Carry forward |  |  |  | 0
| Brought forward |  |  |  | 0
Bill No. 6: Concrete Works to all Pipelines |  |  |  |  | 0
All unreinforced concrete works shall be in medium strength concrete unless otherwise indicated. Where bends less than 45o are obtained by bending the pipe, radius not less than 35 x pipe diameter, and provided there is no compression joint with 5 metres of either end of radius, no separate thrust block is required.
6.1 | Over excavate in trench bed at all gate valves, air valve assemblies and steel fittings and cast support slab to full width of trench with other dimensions being the length of the valve or the fitting between flanges or between the compression tightening nuts and depth below trench bed of 150 mm | nr | 4 |  | 0
6.2 | At all 45o and 90o bends, pipeline tees, and end caps, provide and subsequently remove shuttering and cast thrust blocks against undisturbed trench bed and trench wall | nr | 12 |  | 0
6.3 | Supply all materials and cast and complete air-valve chamber. RATE ONLY | nr | 1
Bill No. 7: | Electromechanical |  |  |  | 0
Bidder shall supply details of proposed pumpset c/w shroud, and standby generator for which there shall be a local agent
proposed submersible hybrid DC/AC pumpset manufacturer and agent:
proposed standby generator manufacturer and agent:
| confirm manufactures brochures included with bid |  | yes / no
No change from these manufacturers or agents shall be permitted without prior written approval from the Consultant
Submersible 48 VDC Borehole Pump
7.1 | Supply and install a hybrid DC/AC borehole submersible pump suitable for a borehole of ID 5" capable of being powered from either a 48 VDC or a nominal 230 VAC source c/w cabled connection to power sources located within 10 m of borehole head, pumping into an overhead tank with top water inlet 14 m above ground.. . |  | nr | 1
Information provided to guide Bidder
| Ground elevation at borehole (approximate) | masl | 1362
| Yield | m3/hr | 2.4 | tbc
| Pump installation level below ground surface | m | 35 | tbc
| Riser pipe diameter | mm | DN 50
| Dynamic water level below ground surface | m | 25 | tbc
| Top water level in overhead tank | masl | 1376
Information to be provided by Bidder
| Manufacturers Pump reference No. | ref.
| Maximum flow at Installation indicated above | m3/hr
| Maximum pump head at installation indicated above | m3/hr
| Optimum flow at Installation indicated above | m3/hr
| Optimum head at Installation indicated above | m3/hr
| Pump efficiency at installation | %
| Input power required by pump | W
| Output power required by solar array | W
| No. of solar panels and arrays offered and guaranteed to meet requirement | nr
7.2 | Solar arrays to meet requirements c/w security fence and gate and lightning protection as per Drawing to be included in this Option
7.2.1 | Supply, install, erect and connect solar arrays to meet requirements c/w lightning protection as per Drawing and Specification | nr | 1 |  | 0
7.2.2 | Provide all materials and construct fenced and gated compound to contain solar array and associated chambers to Specification | LS | 1 |  | 0
7.2.3 | Supply and install DN 25 water pipe take-off from rising mainand standpipe for solar cleansing system | LS | 1 |  | 0
7.2.4 | Provide solar array cleansing step ladder and extendable washer to Specification | LS | 1 |  | 0
Supply and Installation of 220 VAC standby generator of rated power
7.3 | Supply, Install and connect by manually operated changeover switch standby generator capable of providing the VAC power required to operate the submersible borehole pump as specified above at half-load c/w roofed lockable waterproof steel protection cabinet. | nr | 1 |  | 0
Information to be provided by Bidder
Manufacturers Generator Set reference No.
| Output kVA at 1500rpm, 220V, single-phase, 50Hz, with power factor of 1.0 | kVA
| Fuel type (petrol/diesel) | type
| Fuel tank capacity | l
Air or water cooled
| Sub-total |  |  |  | 0
| Contingencies (10%) |  |  |  | 0
| Taxes (VAT @16%) |  |  |  | 0
| Total for Block A Rural Health Centre |  |  |  | 0
Meheba A Primary School Transfer Pipeline from Meheba A Rural Health Clinic
Bill 8. Transfer Pipeline from Rural Health Centre to Primary School
Bill No. 8,1 Demolition and Site Clearance |  |  |  |  | 0
8.1.1 | In collaboration with the Inspector of Works, and based upon pipe lengths and alignment shown on layout plan, agree upon final alignment of pipelines, road crossings, location of all tees, bends, isolating valves, air valves, washouts, tapstands, and consumer connection offtakes. Set out pipeline centre-lines, survey, agree upon Starting Surfaces, and final lengths and produce final plans at horizontal scale of 1:200 for approval before proceeding further. | LS | 1 |  | 0
8.1..2 | General Clearance for urban land & rough grass land along pipeline wayleaves (trench width plus 0.5 m on either side) | ha | 0.1 |  | 0
8.1.3 | Removal of tree stumps within approved alignment. PROVISIONAL SUM | nr | 5 |  | 0
8.1.4 | Cut down and remove trees and tree stumps within approved alignment only if specifically directed to do so by Inspector of Works following agreement from the Host Community PROVISIONAL SUM | nr | 4 |  | 0
Bill No.8.2: Excavation and backfilling of trenches - all pipelines |  |  |  |  | 0
8.2.1 | Excavate test pits along centre line of proposed pipeline to depth of 1m at least every 50 m | nr | 5 |  | 0
8.2.2 | Excavate and trim trench bed to depth not exceeding 1 m to ensure minimum cover to pipeline of 600 mm | m | 216 |  | 0
8.2.3 | Excavate and trim trench to depth not exceeding 1.5 m to ensure minimum cover to pipeline of 900 mm | m | 24.4 |  | 0
8.2.4 | Over excavate trench by a further depth of 150mm in areas identified by the Inspector of Works as requiring imported granular backfill RATE ONLY | m3 | 2.196 |  | 0
8.2.5 | Import, place and compact granular backfill in areas identified by the Inspector of Works as requiring imported granular backfill. RATE ONLY, | m3 | 2.196 |  | 0
8.2.6 | Place and compact sidefill and backfill using selected excavated material free of stones and tree roots to depth 300 mm above crown of pipe, and after compaction, other excavated material thereafter to final surface | m | 240 |  | 0
8.2.7 | Dispose of all surplus excavated material off-site | LS | 1 |  | 0
Bill No. 8.3: Supply and Installation of transfer main- RHC to Primary School elevated water tank |  |  |  |  | 0
All PE compression joints and fittings shall be supplied complete with suitable pipe joint stiffeners. All steel fittings shall be epoxy coated and all nuts and bolts galvanised. Rate shall include supply, lay, bed, joint , pressure test, sterilize and flushing of HDPE pipelines
8.3.1 | HDPE DN50 pipe SDR17, PN 10 | m | 160
8.3.2 | HDPE DN40 pipe SDR17, PN 10 | m | 80
8.3.3 | Compression fitting, elbow 90o DN 50mm | nr | 1
8.3.4 | Compression fitting, elbow 45o DN 50mm | nr | 2
8.3.5 | Equal tee compression fitting DN 50 x 50 x 50 mm | nr | 1
8.3.6 | Reducer DN 50 to DN 40 | nr | 1
8.3.7 | Supply and Installation of DN 40 parallel Woltman type bulk water meter, metrological class B, minimum display 1 m3/hr, suitable for vertical mounting, within water tank inlet riser pipe complete with strainer (metallic double flanged body c/w lockable meter box pipe surround). The meter assembly shall comprise: 1 No. DN50 to DN40 reducer, 1 DN40 500mm long straight pipe length, 1 DN 40 mm double flanged vertically mounted parallel Woltman type meter, located approximately 1.5 m above ground level, 1 DN 40 250 mm straight pipe length, and one DN40 to DN50 reducer. | set | 1 |  | 0
8.3.8 | Gate Valve, double flange, 50 mm non-rising spindle type, with 2 No. flanged restraining adapters st. fl. to PE DN 50, complete with valve riser and valve box to suit | set | 1 |  | 0
Bill 8.4 Concrete Works to Transfer Pipeline |  |  |  |  | 0
8.4.1 | At all 45o and 90o bends, pipeline tees, and end caps, provide and subsequently remove shuttering and cast thrust blocks against undisturbed trench bed and trench wall | nr | 3 |  | 0
| Sub-total |  |  |  | 0
| Contingencies (10%) |  |  |  | 0
| Taxes (VAT @16%) |  |  |  | 0
| Total |  |  |  | 0
Meheba A Primary School Storage and Distribution System
Item | Description | Unit | Qty | Rate (ZMW) | Amount (ZMW)
Bill No.9.1 Demolition and Site Clearance |  |  |  |  | 0
9.1.1 | In collaboration with the Inspector of Works, and based upon pipe lengths and alignment shown on layout plan, agree upon final alignment of pipelines, road crossings, location of all tees, bends, isolating valves, air valves, washouts, tapstands, and consumer connection offtakes. Set out pipeline centre-lines, survey, agree upon Starting Surfaces, and final lengths and produce final plans at horizontal scale of 1:200 for approval before proceeding further. | LS | 1 |  | 0
9.1.2 | General Clearance for urban land & rough grass land along pipeline wayleaves (trench width plus 0.5 m on either side) | ha | 0.1 |  | 0
9.1.3 | Removal of tree stumps within approved alignment. PROVISIONAL SUM | nr | 1 |  | 0
9.1.4 | Cut down and remove trees and tree stumps within approved alignment only if specifically directed to do so by Inspector of Works following agreement from the Host Community PROVISIONAL SUM | nr | 1 |  | 0
Bill No. 9.2: Excavation and backfilling of trenches - distribution pipelines |  |  |  |  | 0
9.2.1 | Excavate test pits along centre line of proposed pipeline to depth of 1m at least every 50 m | nr | 18 |  | 0
9.2.2 | Excavate and trim trench bed to depth not exceeding 1 m to ensure minimum cover to pipeline of 600 mm | m | 810 |  | 0
9.2.3 | Excavate and trim trench to depth not exceeding 1.5 m to ensure minimum cover to pipeline of 900 mm | m | 90 |  | 0
9.2.4 | Over excavate trench by a further depth of 150mm in areas identified by the Inspector of Works as requiring imported granular backfill RATE ONLY | m3 | 8.1 |  | 0
9.2.5 | Import, place and compact granular backfill in areas identified by the Inspector of Works as requiring imported granular backfill. RATE ONLY, | m3 | 8.1 |  | 0
9.2.6 | Place and compact sidefill and backfill using selected excavated material free of stones and tree roots to depth 300 mm above crown of pipe, and after compaction, other excavated material thereafter to final surface | m | 810 |  | 0
9.2.7 | Dispose of all surplus excavated material off-site | LS | 1 |  | 0
Bill No. 9.3: Tanks, Tankstands and Tap Stands |  |  |  |  | 0
Bidder shall supply outline details of water tank stand and tank c/w, pipework and fittings.
water tank stand manufacturer:
HDPE cylindrical tank manufacturer:
HDPE cylindrical tank supplier (if different):
Contractor shall supply full set of structural calculations and drawings for water tank stand certified by a registered structural engineer for written approval prior to fabrication.
9.4.1 | Conduct geotechnical investigations and design foundation and tank stand for the elevated tank | LS | 1 |  | 0
9.4.2 | Tank reinforced concrete foundations 1 m x 1m x 1.5 m deep inc. excavation, shuttering, concreting, curing, backfilling and disposal of excess spoil material from site | nr | 6 |  | 0
Supply and install 2 No. HDPE cylindrical tank on Contractor designed six vertical members) mild steel tankstand c/w with inlet float valves, all inflow, valved connecting, outflow, overflow, and scour (washout) pipework, fittings, adaptors and 10m high steel stand c/w access ladder and lightning arrestor.
9.4.3 | Capacity 12m3.(two no. of 6.0m3) | nr | 1 |  | 0
9.4.4 | Supply and paint all mild steel in tank stand with two coats of zinc 82% rich paint in dry film | LS | 1 |  | 0
9.4.5 | Leak testing and disinfection of tank and pipework | nr | 1 |  | 0
9.4.6 | Provide & install float level indicator gauge on side of tank readable from ground level adjacent to tank | nr | 1 |  | 0
9.4.7 | Provide and install chlorine cartridge type inline doser in lockable chamber at start of tank outlet pipe c/w twelve months supply of chlorine cartridges. | LS | 1 |  | 0
9.4.8 | Provide materials for and construct tap stand and associated drainage | nr | 8 |  | 0
| Carry forward |  |  |  | 0
| Brought forward |  |  |  | 0
Bill No. 9.5: Supply and Install Water Distribution Network |  |  |  |  | 0
All PE compression joints and fittings shall be supplied complete with suitable pipe joint stiffeners. All steel fittings shall be epoxy coated and all nuts and bolts galvanised. Rate shall include supply, lay, bed, joint , pressure test, sterilize and flushing of HDPE pipelines
9.5.1 | Network reticulation pipework HDPE DN50 (OD 63), SDR17, PN 10 | m | 825 |  | 0
9.5.2 | Equal tee compression fitting DN 50 x 50 x 50 mm | nr | 2 |  | 0
9.5.3 | Unequal reducing tee compression fitting DN 50 x 50 x 32 mm | nr | 1 |  | 0
9.5.4 | Compression reducer coupling 50mm x 40mm | nr | 4 |  | 0
9.5.5 | Compression reducer coupling 50mm x 32mm | nr | 1 |  | 0
9.5.6 | Network reticulation pipework HDPE DN 32mm, SDR17, PN 10 | m | 50 |  | 0
9.5.7 | Compression fitting, elbow 90o DN 50mm | nr | 6 |  | 0
9.5.8 | Compression fitting, elbow 90o DN 32mm | nr | 1 |  | 0
9.5.9 | End cap DN 32mm (compression type) | nr | 2 |  | 0
9.5.10 | Supply and install GI pipes 25mm dia c/w fittings to tap stands c/w isolating stop cock | nr | 8 |  | 0
9.5.11 | Supply and install heavy weight brass garden bib tap (non-lever arm type) | nr | 16 |  | 0
9.5.12 | Compression tee DN 32 x 32 x 1" male branch to connect to tap stand pipework | nr | 2 |  | 0
9.5.13 | Compression tee DN 50 x 50 x 1 1/2" male br., 1 No. female to male 1 1/2" to 1" thr. spigott to connect to tap stand pipework | nr | 6 |  | 0
9.5.14 | Gate Valve, double flange, 40 mm non-rising spindle type, with 2 No. flanged restraining adapters st. fl. to PE DN 40, complete with valve riser and valve box to suit | nr | 2 |  | 0
9.5.15 | Air valve assembly consisting of 1 No. compression tee with threaded male 1 1/2" branch vertically upwards, 1 No. female to male thr. spigot, 1 No. Stopcock, thr. dble. socket 1", and 1 No. Single air valve, thr. female 1". RATE ONLY
9.5.15.1 | Compression tee DN 50 x 50 x 1 1/2" male br., 1 No. female to male 1 1/2" to 1" thr. spigot | set | 1
9.5.15.2 | Compression tee DN 32 x 32 x 1" male br, 1 No. female to male 1" to 1" thr. spigot | set | 0
Bill No. 9.6: Concrete Works to all Pipelines |  |  |  |  | 0
All unreinforced concrete works shall be in medium strength concrete unless otherwise indicated. Where bends less than 45o are obtained by bending the pipe, radius not less than 35 x pipe diameter, and provided there is no compression joint with 5 metres of either end of radius, no separate thrust block is required.
9.6.1 | Over excavate in trench bed at all gate valves, air valve assemblies and steel fittings and cast support slab to full width of trench with other dimensions being the length of the valve or the fitting between flanges or between the compression tightening nuts and depth below trench bed of 150 mm | nr | 3 |  | 0
9.6.2 | At all 45o and 90o bends, pipeline tees, and end caps, provide and subsequently remove shuttering and cast thrust blocks against undisturbed trench bed and trench wall | nr | 12 |  | 0
9.6.3 | Supply all materials and cast and complete air-valve chamber. RATE ONLY | nr | 1
| Sub-total |  |  |  | 0
| Contingencies (10%) |  |  |  | 0
| Taxes (VAT @16%) |  |  |  | 0
| Total |  |  |  | 0

## Kakaindu RHC & to Pr Sch
UNICEF
Solar Powered Borehole Schemes in institutions in Meheba Refugee Camp & Host Communities
Kakaindu RHC with Primary School extension
Bill No. RHC3:
Item | Description | Unit | Qty | Rate (ZMW) | Amount (ZMW)
Bill No. out, Demolition and Site Clearance |  |  |  |  | 0
1.1 | In collaboration with the Inspector of Works, and based upon pipe lengths and alignment shown on layout plan, agree upon final alignment of pipelines, road crossings, location of all tees, bends, isolating valves, air valves, washouts, tapstands, and consumer connection offtakes. Set out pipeline centre-lines, survey, agree upon Starting Surfaces, and final lengths and produce final plans at horizontal scale of 1:200 for approval before proceeding further. | LS | 1 |  | 0
1.2 | General Clearance for urban land & rough grass land along pipeline wayleaves (trench width plus 0.5 m on either side) | ha | 0.1 |  | 0
1.3 | Removal of tree stumps within approved alignment. PROVISIONAL SUM | nr | 1 |  | 0
1.4 | Cut down and remove trees and tree stumps within approved alignment only if specifically directed to do so by Inspector of Works following agreement from the Host Community PROVISIONAL SUM | nr | 1 |  | 0
Bill No. 2: Excavation and backfilling of trenches - all pipelines |  |  |  |  | 0
2.1 | Excavate test pits along centre line of proposed pipeline to depth of 1m at least every 50 m | nr | 7 |  | 0
2.2 | Excavate and trim trench bed to depth not exceeding 1 m to ensure minimum cover to pipeline of 600 mm | m | 264.5 |  | 0
2.3 | Excavate and trim trench to depth not exceeding 1.5 m to ensure minimum cover to pipeline of 900 mm | m | 21 |  | 0
2.4 | Over excavate trench by a further depth of 150mm in areas identified by the Inspector of Works as requiring imported granular backfill RATE ONLY | m3 | 0.945 |  | 0
2.5 | Import, place and compact granular backfill in areas identified by the Inspector of Works as requiring imported granular backfill. RATE ONLY, | m3 | 0.945 |  | 0
2.6 | Place and compact sidefill and backfill using selected excavated material free of stones and tree roots to depth 300 mm above crown of pipe, and after compaction, other excavated material thereafter to final surface | m | 264.5 |  | 0
2.7 | Dispose of all surplus excavated material off-site | LS | 1 |  | 0
Bill No. 3: Supply and Installation of rising main- borehole to elevated water tank |  |  |  |  | 0
All PE compression joints and fittings shall be supplied complete with suitable pipe joint stiffeners. All steel fittings shall be epoxy coated and all nuts and bolts galvanised. Rate shall include supply, lay, bed, joint , pressure test, sterilize and flushing of HDPE pipelines
3.1 | Raw water rising main from borehole to the Elevated Tank , HDPE DN50 (OD 63), SDR17, PN 10 | m | 57 |  | 0
3.2 | Compression fitting, elbow 45o DN 50mm | nr | 1 |  | 0
3.3 | Supply and Installation of DN 40 parallel Woltman type bulk water meter, metrological class B, minimum display 1 m3/hr, suitable for vertical mounting, within water tank inlet riser pipe complete with strainer (metallic double flanged body c/w lockable meter box pipe surround). The meter assembly shall comprise: 1 No. DN50 to DN40 reducer, 1 DN40 500mm long straight pipe length, 1 DN 40 mm double flanged vertically mounted parallel Woltman type meter, located approximately 1.5 m above ground level, 1 DN 40 250 mm straight pipe length, and one DN40 to DN50 reducer. | set | 1 |  | 0
3.4 | Gate Valve, double flange, 50 mm non-rising spindle type, with 2 No. flanged restraining adapters st. fl. to PE DN 50, complete with valve riser and valve box to suit | set | 1 |  | 0
3.5 | Supply and install DN 25 water pipe take-off from rising mainand standpipe for solar cleansing system | LS | 1 |  | 0
3.6 | Provide solar array cleansing step ladder and extendable washer to Specification | LS | 1 |  | 0
| Carry forward |  |  |  | 0
| Brought forward |  |  |  | 0
Bill No. 4: Tanks, Tankstands and Tap Stands |  |  |  |  | 0
Bidder shall supply outline details of water tank stand and tank c/w, pipework and fittings.
water tank stand manufacturer:
HDPE cylindrical tank manufacturer:
HDPE cylindrical tank supplier (if different):
Contractor shall supply full set of structural calculations and drawings for water tank stand certified by a registered structural engineer for written approval prior to fabrication.
4.1 | Conduct geotechnical investigations and design foundation and tank stand for the elevated tank | LS | 1 |  | 0
4.2 | Tank reinforced concrete foundations 1 m x 1m x 1.5 m deep inc. excavation, shuttering, concreting, curing, backfilling and disposal of excess spoil material from site | nr | 6 |  | 0
Supply and install 2 No. HDPE cylindrical tank on Contractor designed six vertical members) mild steel tankstand c/w with inlet float valves, all inflow, valved connecting, outflow, overflow, and scour (washout) pipework, fittings, adaptors and 6m high steel stand c/w access ladder and lightning arrestor.
4.3 | Capacity 10m3.(2 no at 5 m3) | nr | 1 |  | 0
4.4 | Supply and paint all mild steel in tank stand with two coats of zinc 82% rich paint in dry film | LS | 1 |  | 0
4.5 | Leak testing and disinfection of tank and pipework | nr | 1 |  | 0
4.6 | Provide & install float level indicator gauge on side of tank readable from ground level adjacent to tank | nr | 1 |  | 0
4.7 | Provide and install chlorine cartridge type inline doser in lockable chamber at start of tank outlet pipe c/w twelve months supply of chlorine cartridges. | LS | 1 |  | 0
4.8 | Provide materials for and construct tap stand and associated drainage | nr | 2 |  | 0
Bill No. 5: Supply and Install Water Distribution Network |  |  |  |  | 0
All PE compression joints and fittings shall be supplied complete with suitable pipe joint stiffeners. All steel fittings shall be epoxy coated and all nuts and bolts galvanised. Rate shall include supply, lay, bed, joint , pressure test, sterilize and flushing of HDPE pipelines
5.1 | Compression reducer coupling 40mm x 32mm | nr | 1 |  | 0
5.2 | Network reticulation pipework HDPE DN 40mm, SDR17, PN 10 | m | 200 |  | 0
5.3 | Network reticulation pipework HDPE DN 32mm, SDR17, PN 10 | m | 18 |  | 0
5.4 | Compression fitting, elbow 90o DN 32mm | nr | 1 |  | 0
5.5 | End cap DN 32mm (compression type) | nr | 3 |  | 0
5.6 | Saddle clamp 32mm x 3/4" to supply individual consumer connection | nr | 1 |  | 0
5.7 | Supply and install GI pipes 25mm dia c/w fittings to tap stands c/w isolating stop cock | nr | 2 |  | 0
5.8 | Supply and install heavy weight brass garden bib tap (non-lever arm type) | nr | 4 |  | 0
5.9 | Compression tee DN 40 x 40 x 1" male branch to connect to tap stand pipework | nr | 2 |  | 0
5.1 | Gate Valve, double flange, 40 mm non-rising spindle type, with 2 No. flanged restraining adapters st. fl. to PE DN 40, complete with valve riser and valve box to suit | nr | 1 |  | 0
Air valve assembly consisting of 1 No. compression tee with threaded male 1 1/2" branch vertically upwards, 1 No. female to male thr. spigot, 1 No. Stopcock, thr. dble. socket 1", and 1 No. Single air valve, thr. female 1". RATE ONLY
5.12 | Compression tee DN 40 x 40 x 1 1/2" male br., 1 No. female to male 1 1/2" to 1" thr. Spigot | set | 1
| Carry forward |  |  |  | 0
| Brought forward |  |  |  | 0
Bill No. 6: Concrete Works to all Pipelines |  |  |  |  | 0
All unreinforced concrete works shall be in medium strength concrete unless otherwise indicated. Where bends less than 45o are obtained by bending the pipe, radius not less than 35 x pipe diameter, and provided there is no compression joint with 5 metres of either end of radius, no separate thrust block is required.
6.1 | Over excavate in trench bed at all gate valves, air valve assemblies and steel fittings and cast support slab to full width of trench with other dimensions being the length of the valve or the fitting between flanges or between the compression tightening nuts and depth below trench bed of 150 mm | nr | 2 |  | 0
6.2 | At all 45o and 90o bends, pipeline tees, and end caps, provide and subsequently remove shuttering and cast thrust blocks against undisturbed trench bed and trench wall | nr | 4 |  | 0
6.3 | Supply all materials and cast and complete air-valve chamber. RATE ONLY | nr | 1
Bill No. 7: Water Distribution Network | Electromechanical |  |  |  | 0
Bidder shall supply details of proposed pumpset c/w shroud, and standby generator for which there shall be a local agent
proposed submersible hybrid DC/AC pumpset manufacturer and agent:
proposed standby generator manufacturer and agent:
| confirm manufactures brochures included with bid |  | yes / no
No change from these manufacturers or agents shall be permitted without prior written approval from the Consultant
Submersible 48 VDC Borehole Pump
7.1 | Supply and install a hybrid DC/AC borehole submersible pump suitable for a borehole of ID 5" capable of being powered from either a 48 VDC or a nominal 230 VAC source c/w cabled connection to power sources located within 10 m of borehole head, pumping into an overhead tank with top water inlet 14 m above ground.. . |  | nr | 1
Information provided to guide Bidder
| Ground elevation at borehole (approximate) | masl | 1402
| Yield | m3/hr | 1 | tbc
| Pump installation level below ground surface | m | 20 | tbc
| Riser pipe diameter | mm | DN 50
| Dynamic water level below ground surface | m | 15 | tbc
| Top water level in overhead tank | masl | 1416
Information to be provided by Bidder
| Manufacturers Pump reference No. | ref.
| Maximum flow at Installation indicated above | m3/hr
| Maximum pump head at installation indicated above | m3/hr
| Optimum flow at Installation indicated above | m3/hr
| Optimum head at Installation indicated above | m3/hr
| Pump efficiency at installation | %
| Input power required by pump | W
| Output power required by solar array | W
| No. of solar panels and arrays offered and guaranteed to meet requirement | nr
7.2 | Solar arrays to meet requirements c/w security fence and gate and lightning protection as per Drawing to be included in this Option
7.2.1 | Supply, install, erect and connect solar arrays to meet requirements c/w lightning protection as per Drawing and Specification | nr | 1 |  | 0
7.2.2 | Provide all materials and construct fenced and gated compound to contain solar array and associated chambers to Specification | LS | 1 |  | 0
7.2.3 | Supply and install DN 25 water pipe take-off from rising main and standpipe for solar cleansing system | LS | 1 |  | 0
7.2.4 | Provide solar array cleansing step ladder and extendable washer to Specification | LS | 1 |  | 0
Supply and Installation of 220 VAC standby generator of rated power
7.3 | Supply, Install and connect by manually operated changeover switch standby generator capable of providing the VAC power required to operate the submersible borehole pump as specified above at half-load c/w roofed lockable waterproof steel protection cabinet. | nr | 1 |  | 0
Information to be provided by Bidder
Manufacturers Generator Set reference No.
| Output kVA at 1500rpm, 220V, single-phase, 50Hz, with power factor of 1.0 | kVA
| Fuel type (petrol/diesel) | type
| Fuel tank capacity | l
Air or water cooled
| Sub-total |  |  |  | 0
| Contingencies (10%) |  |  |  | 0
| Taxes (VAT @16%) |  |  |  | 0
| Total |  |  |  | 0

## Meheba G RHC & Pr Sch
UNICEF
Solar Powered Borehole Schemes in institutions in Meheba Refugee Camp & Host Communities
Meheba Block G RHC and Primary School
Bill No. RHC4:
Item | Description | Unit | Qty | Rate (ZMW) | Amount (ZMW)
Bill No. out, Demolition and Site Clearance |  |  |  |  | 0
1.1 | In collaboration with the Inspector of Works, and based upon pipe lengths and alignment shown on layout plan, agree upon final alignment of pipelines, road crossings, location of all tees, bends, isolating valves, air valves, washouts, tapstands, and consumer connection offtakes. Set out pipeline centre-lines, survey, agree upon Starting Surfaces, and final lengths and produce final plans at horizontal scale of 1:200 for approval before proceeding further. | LS | 1 |  | 0
1.2 | General Clearance for urban land & rough grass land along pipeline wayleaves (trench width plus 0.5 m on either side) | ha | 0.1 |  | 0
1.3 | Removal of tree stumps within approved alignment. PROVISIONAL SUM | nr | 1 |  | 0
1.4 | Cut down and remove trees and tree stumps within approved alignment only if specifically directed to do so by Inspector of Works following agreement from the Host Community PROVISIONAL SUM | nr | 1 |  | 0
Bill No. 2: Excavation and backfilling of trenches - all pipelines |  |  |  |  | 0
2.1 | Excavate test pits along centre line of proposed pipeline to depth of 1m at least every 50 m | nr | 8 |  | 0
2.2 | Excavate and trim trench bed to depth not exceeding 1 m to ensure minimum cover to pipeline of 600 mm | m | 318.6 |  | 0
2.3 | Excavate and trim trench to depth not exceeding 1.5 m to ensure minimum cover to pipeline of 900 mm | m | 35.4 |  | 0
2.4 | Over excavate trench by a further depth of 150mm in areas identified by the Inspector of Works as requiring imported granular backfill RATE ONLY | m3 | 3.186 |  | 0
2.5 | Import, place and compact granular backfill in areas identified by the Inspector of Works as requiring imported granular backfill. RATE ONLY, | m3 | 3.186 |  | 0
2.6 | Place and compact sidefill and backfill using selected excavated material free of stones and tree roots to depth 300 mm above crown of pipe, and after compaction, other excavated material thereafter to final surface | m | 318.6 |  | 0
2.7 | Dispose of all surplus excavated material off-site | LS | 1 |  | 0
Bill No. 3: Supply and Installation of rising main- borehole to elevated water tank |  |  |  |  | 0
All PE compression joints and fittings shall be supplied complete with suitable pipe joint stiffeners. All steel fittings shall be epoxy coated and all nuts and bolts galvanised. Rate shall include supply, lay, bed, joint , pressure test, sterilize and flushing of HDPE pipelines
3.1 | Raw water rising main from borehole to the Elevated Tank , HDPE DN50 (OD 63), SDR17, PN 10 | m | 114 |  | 0
3.2 | Supply and Installation of DN 40 parallel Woltman type bulk water meter, metrological class B, minimum display 1 m3/hr, suitable for vertical mounting, within water tank inlet riser pipe complete with strainer (metallic double flanged body c/w lockable meter box pipe surround). The meter assembly shall comprise: 1 No. DN50 to DN40 reducer, 1 DN40 500mm long straight pipe length, 1 DN 40 mm double flanged vertically mounted parallel Woltman type meter, located approximately 1.5 m above ground level, 1 DN 40 250 mm straight pipe length, and one DN40 to DN50 reducer. | set | 1 |  | 0
3.3 | Gate Valve, double flange, 50 mm non-rising spindle type, with 2 No. flanged restraining adapters st. fl. to PE DN 50, complete with valve riser and valve box to suit | set | 1 |  | 0
3.4 | Supply and install DN 25 water pipe take-off from rising mainand standpipe for solar cleansing system | LS | 1 |  | 0
3.5 | Provide solar array cleansing step ladder and extendable washer to Specification | LS | 1 |  | 0
| Carry forward |  |  |  | 0
| Brought forward |  |  |  | 0
Bill No. 4: Tanks, Tankstands and Tap Stands |  |  |  |  | 0
Bidder shall supply outline details of water tank stand and tank c/w, pipework and fittings.
water tank stand manufacturer:
HDPE cylindrical tank manufacturer:
HDPE cylindrical tank supplier (if different):
Contractor shall supply full set of structural calculations and drawings for water tank stand certified by a registered structural engineer for written approval prior to fabrication.
4.1 | Conduct geotechnical investigations and design foundation and tank stand for the elevated tank | LS | 1 |  | 0
4.2 | Tank reinforced concrete foundations 1 m x 1m x 1.5 m deep inc. excavation, shuttering, concreting, curing, backfilling and disposal of excess spoil material from site | nr | 6 |  | 0
Supply and install 2 No. HDPE cylindrical tank on Contractor designed six vertical members) mild steel tankstand c/w with inlet float valves, all inflow, valved connecting, outflow, overflow, and scour (washout) pipework, fittings, adaptors and 6m high steel stand c/w access ladder and lightning arrestor.
4.3 | Capacity 10m3.(two no. of 5m3) | nr | 1 |  | 0
4.4 | Supply and paint all mild steel in tank stand with two coats of zinc 82% rich paint in dry film | LS | 1 |  | 0
4.5 | Leak testing and disinfection of tank and pipework | nr | 1 |  | 0
4.6 | Provide & install float level indicator gauge on side of tank readable from ground level adjacent to tank | nr | 1 |  | 0
4.7 | Provide and install chlorine cartridge type inline doser in lockable chamber at start of tank outlet pipe c/w twelve months supply of chlorine cartridges. | LS | 1 |  | 0
4.8 | Provide materials for and construct tap stand and associated drainage | nr | 4 |  | 0
Bill No. 5: Supply and Install Water Distribution Network |  |  |  |  | 0
All PE compression joints and fittings shall be supplied complete with suitable pipe joint stiffeners. All steel fittings shall be epoxy coated and all nuts and bolts galvanised. Rate shall include supply, lay, bed, joint , pressure test, sterilize and flushing of HDPE pipelines
5.1 | Equal tee compression fitting DN 40 x 40 x 40 mm | nr | 1 |  | 0
5.2 | Compression reducer coupling 40mm x 32mm | nr | 1 |  | 0
5.3 | Network reticulation pipework HDPE DN 40mm, SDR17, PN 10 | m | 147 |  | 0
5.4 | Network reticulation pipework HDPE DN 32mm, SDR17, PN 10 | m | 93 |  | 0
5.5 | Compression fitting, elbow 90o DN 40mm | nr | 3 |  | 0
5.6 | End cap DN 32mm (compression type) | nr | 7 |  | 0
5.7 | Saddle clamp 32mm x 3/4" to supply individual consumer connection | nr | 6 |  | 0
5.8 | Supply and install GI pipes 25mm dia c/w fittings to tap stands c/w isolating stop cock | nr | 4 |  | 0
5.9 | Supply and install heavy weight brass garden bib tap (non-lever arm type) | nr | 8 |  | 0
5.1 | Compression tee DN 40 x 40 x 1" male branch to connect to tap stand pipework | nr | 3 |  | 0
5.11 | Compression tee DN 32 x 32 x 1" male branch to connect to tap stand pipework | nr | 1 |  | 0
5.12 | Compression tee DN 50 x 50 x 1 1/2" male br., 1 No. female to male 1 1/2" to 1" thr. spigot to connect to tap stand pipework | nr | 0 |  | 0
5.13 | Gate Valve, double flange, 40 mm non-rising spindle type, with 2 No. flanged restraining adapters st. fl. to PE DN 40, complete with valve riser and valve box to suit | nr | 2 |  | 0
Air valve assembly consisting of 1 No. compression tee with threaded male 1 1/2" branch vertically upwards, 1 No. female to male thr. spigot, 1 No. Stopcock, thr. dble. socket 1", and 1 No. Single air valve, thr. female 1". RATE ONLY
5.14.1 | Compression tee DN 40 x 40 x 1 1/2" male br., 1 No. female to male 1 1/2" to 1" thr. Spigot | set | 1
5.14.2 | Compression tee DN 32 x 32 x 1" male br, 1 No. female to male 1" to 1" thr. spigot | set | 0
| Carry forward |  |  |  | 0
| Brought forward |  |  |  | 0
Bill No. 6: Concrete Works to all Pipelines |  |  |  |  | 0
All unreinforced concrete works shall be in medium strength concrete unless otherwise indicated. Where bends less than 45o are obtained by bending the pipe, radius not less than 35 x pipe diameter, and provided there is no compression joint with 5 metres of either end of radius, no separate thrust block is required.
6.1 | Over excavate in trench bed at all gate valves, air valve assemblies and steel fittings and cast support slab to full width of trench with other dimensions being the length of the valve or the fitting between flanges or between the compression tightening nuts and depth below trench bed of 150 mm | nr | 3 |  | 0
6.2 | At all 45o and 90o bends, pipeline tees, and end caps, provide and subsequently remove shuttering and cast thrust blocks against undisturbed trench bed and trench wall | nr | 12 |  | 0
6.3 | Supply all materials and cast and complete air-valve chamber. RATE ONLY | nr | 1
Bill No. 7: Water Distribution Network | Electromechanical |  |  |  | 0
Bidder shall supply details of proposed pumpset c/w shroud, and standby generator for which there shall be a local agent
proposed submersible hybrid DC/AC pumpset manufacturer and agent:
proposed standby generator manufacturer and agent:
| confirm manufactures brochures included with bid |  | yes / no
No change from these manufacturers or agents shall be permitted without prior written approval from the Consultant
Submersible 48 VDC Borehole Pump
7.1 | Supply and install a hybrid DC/AC borehole submersible pump suitable for a borehole of ID 5" capable of being powered from either a 48 VDC or a nominal 230 VAC source c/w cabled connection to power sources located within 10 m of borehole head, pumping into an overhead tank with top water inlet 14 m above ground.. . |  | nr | 1
Information provided to guide Bidder
| Ground elevation at borehole (approximate) | masl | 1297
| Yield | m3/hr | 2 | tbc
| Pump installation level below ground surface | m | 27 | tbc
| Riser pipe diameter | mm | DN 50
| Dynamic water level below ground surface | m | 20 | tbc
| Top water level in overhead tank | masl | 1311
Information to be provided by Bidder
| Manufacturers Pump reference No. | ref.
| Maximum flow at Installation indicated above | m3/hr
| Maximum pump head at installation indicated above | m3/hr
| Optimum flow at Installation indicated above | m3/hr
| Optimum head at Installation indicated above | m3/hr
| Pump efficiency at installation | %
| Input power required by pump | W
| Output power required by solar array | W
| No. of solar panels and arrays offered and guaranteed to meet requirement | nr
7.2 | Solar arrays to meet requirements c/w security fence and gate and lightning protection as per Drawing to be included in this Option
7.2.1 | Supply, install, erect and connect solar arrays to meet requirements c/w lightning protection as per Drawing and Specification | nr | 1 |  | 0
7.2.2 | Provide all materials and construct fenced and gated compound to contain solar array and associated chambers to Specification | LS | 1 |  | 0
7.2.3 | Supply and install DN 25 water pipe take-off from rising main and standpipe for solar cleansing system | LS | 1 |  | 0
7.2.4 | Provide solar array cleansing step ladder and extendable washer to Specification | LS | 1 |  | 0
Supply and Installation of 220 VAC standby generator of rated power
7.3 | Supply, Install and connect by manually operated changeover switch standby generator capable of providing the VAC power required to operate the submersible borehole pump as specified above at half-load c/w roofed lockable waterproof steel protection cabinet. | nr | 1 |  | 0
Information to be provided by Bidder
Manufacturers Generator Set reference No.
| Output kVA at 1500rpm, 220V, single-phase, 50Hz, with power factor of 1.0 | kVA
| Fuel type (petrol/diesel) | type
| Fuel tank capacity | l
Air or water cooled
| Sub-total |  |  |  | 0
| Contingencies (10%) |  |  |  | 0
| Taxes (VAT @16%) |  |  |  | 0
| Total |  |  |  | 0

## Meheba Block D RHC & Pr. Sch.
UNICEF
Solar Powered Borehole Schemes in institutions in Meheba Refugee Camp & Host Communities
Meheba Block D RHC with extension to Primary School
Bill No. RHC5:
| Item | Description | Unit | Qty | Rate (ZMW) | Amount (ZMW)
| Bill No. out, Demolition and Site Clearance |  |  |  |  | 0
| 1.1 | In collaboration with the Inspector of Works, and based upon pipe lengths and alignment shown on layout plan, agree upon final alignment of pipelines, road crossings, location of all tees, bends, isolating valves, air valves, washouts, tapstands, and consumer connection offtakes. Set out pipeline centre-lines, survey, agree upon Starting Surfaces, and final lengths and produce final plans at horizontal scale of 1:200 for approval before proceeding further. | LS | 1 |  | 0
| 1.2 | General Clearance for urban land & rough grass land along pipeline wayleaves (trench width plus 0.5 m on either side) | ha | 0.2 |  | 0
| 1.3 | Removal of tree stumps within approved alignment. PROVISIONAL SUM | nr | 1 |  | 0
| 1.4 | Cut down and remove trees and tree stumps within approved alignment only if specifically directed to do so by Inspector of Works following agreement from the Host Community PROVISIONAL SUM | nr | 1 |  | 0
| Bill No. 2: Excavation and backfilling of trenches - all pipelines |  |  |  |  | 0
| 2.1 | Excavate test pits along centre line of proposed pipeline to depth of 1m at least every 50 m | nr | 11 |  | 0
| 2.2 | Excavate and trim trench bed to depth not exceeding 1 m to ensure minimum cover to pipeline of 600 mm | m | 468.9 |  | 0
| 2.3 | Excavate and trim trench to depth not exceeding 1.5 m to ensure minimum cover to pipeline of 900 mm | m | 52.1 |  | 0
| 2.4 | Over excavate trench by a further depth of 150mm in areas identified by the Inspector of Works as requiring imported granular backfill RATE ONLY | m3 | 4.689 |  | 0
| 2.5 | Import, place and compact granular backfill in areas identified by the Inspector of Works as requiring imported granular backfill. RATE ONLY, | m3 | 4.689 |  | 0
| 2.6 | Place and compact sidefill and backfill using selected excavated material free of stones and tree roots to depth 300 mm above crown of pipe, and after compaction, other excavated material thereafter to final surface | m | 468.9 |  | 0
| 2.7 | Dispose of all surplus excavated material off-site | LS | 1 |  | 0
| Bill No. 3: Supply and Installation of rising main- borehole to elevated water tank |  |  |  |  | 0
All PE compression joints and fittings shall be supplied complete with suitable pipe joint stiffeners. All steel fittings shall be epoxy coated and all nuts and bolts galvanised. Rate shall include supply, lay, bed, joint , pressure test, sterilize and flushing of HDPE pipelines
| 3.1 | Raw water rising main from borehole to the Elevated Tank , HDPE DN50 (OD 63), SDR17, PN 10 | m | 31 |  | 0
| 3.2 | Compression fitting, elbow 45o DN 50mm | nr | 1 |  | 0
| 3.3 | Compression fitting, elbow 90o DN 50mm | nr | 1
| 3.4 | Supply and Installation of DN 40 parallel Woltman type bulk water meter, metrological class B, minimum display 1 m3/hr, suitable for vertical mounting, within water tank inlet riser pipe complete with strainer (metallic double flanged body c/w lockable meter box pipe surround). The meter assembly shall comprise: 1 No. DN50 to DN40 reducer, 1 DN40 500mm long straight pipe length, 1 DN 40 mm double flanged vertically mounted parallel Woltman type meter, located approximately 1.5 m above ground level, 1 DN 40 250 mm straight pipe length, and one DN40 to DN50 reducer. | set | 1 |  | 0
| 3.5 | Gate Valve, double flange, 50 mm non-rising spindle type, with 2 No. flanged restraining adapters st. fl. to PE DN 50, complete with valve riser and valve box to suit | set | 1 |  | 0
| 3.6 | Supply and install DN 25 water pipe take-off from rising mainand standpipe for solar cleansing system | LS | 1 |  | 0
| 3.7 | Provide solar array cleansing step ladder and extendable washer to Specification | LS | 1 |  | 0
|  | Carry forward |  |  |  | 0
|  | Brought forward |  |  |  | 0
| Bill No. 4: Tanks, Tankstands and Tap Stands |  |  |  |  | 0
Bidder shall supply outline details of water tank stand and tank c/w, pipework and fittings.
water tank stand manufacturer:
HDPE cylindrical tank manufacturer:
HDPE cylindrical tank supplier (if different):
Contractor shall supply full set of structural calculations and drawings for water tank stand certified by a registered structural engineer for written approval prior to fabrication.
| 4.1 | Conduct geotechnical investigations and design foundation and tank stand for the elevated tank | LS | 1 |  | 0
| 4.2 | Tank reinforced concrete foundations 1 m x 1m x 1.5 m deep inc. excavation, shuttering, concreting, curing, backfilling and disposal of excess spoil material from site | nr | 6 |  | 0
Supply and install 1 No. HDPE cylindrical tank on Contractor designed mild steel tankstand c/w with inlet float valve, all inflow, outflow, overflow, and scour (washout) pipework, fittings, adaptors and 6m high steel stand c/w access ladder and lightning arrestor.
| 4.3 | Capacity 15 m3. (2 no. 7.5 m3 tanks) | nr | 1 |  | 0
| 4.4 | Supply and paint all mild steel in tank stand with two coats of zinc 82% rich paint in dry film | LS | 1 |  | 0
| 4.5 | Leak testing and disinfection of tank and pipework | nr | 1 |  | 0
| 4.6 | Provide and install chlorine cartridge type inline doser in lockable chamber at start of tank outlet pipe c/w twelve months supply of chlorine cartridges. | LS | 1 |  | 0
| 4.7 | Provide materials for and construct tap stand and associated drainage | nr | 8 |  | 0
| Bill No. 5: Supply and Install Water Distribution Network |  |  |  |  | 0
All PE compression joints and fittings shall be supplied complete with suitable pipe joint stiffeners. All steel fittings shall be epoxy coated and all nuts and bolts galvanised. Rate shall include supply, lay, bed, joint , pressure test, sterilize and flushing of HDPE pipelines
| 5.1 | Network reticulation pipework HDPE DN50 (OD 63), SDR17, PN 10 | m | 181 |  | 0
| 5.2 | Equal tee compression fitting DN 50 x 50 x 50 mm | nr | 1 |  | 0
| 5.3 | Equal tee compression fitting DN 40 x 40 x 40 mm | nr | 1 |  | 0
| 5.4 | Unequal reducing tee compression fitting DN 50 x 50 x 40 mm | nr | 1 |  | 0
| 5.5 | Unequal reducing tee compression fitting DN 50 x 50 x 32 mm | nr | 2 |  | 0
| 5.6 | Unequal reducing tee compression fitting DN 40 x 40 x 32 mm | nr | 6 |  | 0
| 5.7 | Equal tee compression fitting DN 32 x 32 x 32 mm | nr | 1 |  | 0
| 5.8 | Compression reducer coupling 50mm x 32mm | nr | 2 |  | 0
| 5.9 | Network reticulation pipework HDPE DN 40mm, SDR17, PN 10 | m | 252 |  | 0
| 5.1 | Network reticulation pipework HDPE DN 32mm, SDR17, PN 10 | m | 57 |  | 0
| 5.11 | Compression fitting, elbow 90o DN 50mm | nr | 1 |  | 0
| 5.12 | End cap DN 32mm (compression type) | nr | 13 |  | 0
| 5.13 | Saddle clamp 32mm x 3/4" to supply individual consumer connection | nr | 13 |  | 0
| 5.14 | Supply and install GI pipes 25mm dia c/w fittings to tap stands c/w isolating stop cock | nr | 2 |  | 0
| 5.15 | Supply and install heavy weight brass garden bib tap (non-lever arm type) | nr | 4 |  | 0
| 5.16 | Compression tee DN 40 x 40 x 1" male branch to connect to tap stand pipework | nr | 1 |  | 0
| 5.17 | Compression tee DN 32 x 32 x 1" male branch to connect to tap stand pipework | nr | 1 |  | 0
Air valve assembly consisting of 1 No. compression tee with threaded male 1 1/2" branch vertically upwards, 1 No. female to male thr. spigot, 1 No. Stopcock, thr. dble. socket 1", and 1 No. Single air valve, thr. female 1". RATE ONLY
| 5.18.1 | Compression tee DN 50 x 50 x 1 1/2" male br., 1 No. female to male 1 1/2" to 1" thr. spigot | set | 1
| 5.18.2 | Compression tee DN 40 x 40 x 1 1/2" male br., 1 No. female to male 1 1/2" to 1" thr. Spigot | set | 1
| 5.18.3 | Compression tee DN 32 x 32 x 1" male br, 1 No. female to male 1" to 1" thr. spigot | set | 1
|  | Carry forward |  |  |  | 0
|  | Brought forward |  |  |  | 0
| Bill No. 6: Concrete Works to all Pipelines |  |  |  |  | 0
All unreinforced concrete works shall be in medium strength concrete unless otherwise indicated. Where bends less than 45o are obtained by bending the pipe, radius not less than 35 x pipe diameter, and provided there is no compression joint with 5 metres of either end of radius, no separate thrust block is required.
| 6.1 | Over excavate in trench bed at all gate valves, air valve assemblies and steel fittings and cast support slab to full width of trench with other dimensions being the length of the valve or the fitting between flanges or between the compression tightening nuts and depth below trench bed of 150 mm | nr | 1 |  | 0
| 6.2 | At all 45o and 90o bends, pipeline tees, and end caps, provide and subsequently remove shuttering and cast thrust blocks against undisturbed trench bed and trench wall | nr | 23 |  | 0
| 6.3 | Supply all materials and cast and complete air-valve chamber. RATE ONLY | nr | 1
| Bill No. 7: Water Distribution Network | Electromechanical |  |  |  | 0
Bidder shall supply details of proposed pumpset c/w shroud, and standby generator for which there shall be a local agent
proposed submersible hybrid DC/AC pumpset manufacturer and agent:
proposed standby generator manufacturer and agent:
|  | confirm manufactures brochures included with bid |  | yes / no
No change from these manufacturers or agents shall be permitted without prior written approval from the Consultant
Submersible 48 VDC Borehole Pump
| 7.1 | Supply and install a hybrid DC/AC borehole submersible pump suitable for a borehole of ID 5" capable of being powered from either a 48 VDC or a nominal 230 VAC source c/w cabled connection to power sources located within 10 m of borehole head, pumping into an overhead tank with top water inlet 14 m above ground.. . |  | nr | 1
Information provided to guide Bidder
|  | Ground elevation at borehole (approximate) | masl | 1307
|  | Yield | m3/hr | 3 | tbc
|  | Pump installation level below ground surface | m | 36 | tbc
|  | Riser pipe diameter | mm | DN 50
|  | Dynamic water level below ground surface | m | 25 | tbc
|  | Top water level in overhead tank | masl | 1321
Information to be provided by Bidder
|  | Manufacturers Pump reference No. | ref.
|  | Maximum flow at Installation indicated above | m3/hr
|  | Maximum pump head at installation indicated above | m3/hr
|  | Optimum flow at Installation indicated above | m3/hr
|  | Optimum head at Installation indicated above | m3/hr
|  | Pump efficiency at installation | %
|  | Input power required by pump | W
|  | Output power required by solar array | W
|  | No. of solar panels and arrays offered and guaranteed to meet requirement | nr
| 7.2 | Solar arrays to meet requirements c/w security fence and gate and lightning protection as per Drawing to be included in this Option
| 7.2.1 | Supply, install, erect and connect solar arrays to meet requirements c/w lightning protection as per Drawing and Specification | nr | 1 |  | 0
| 7.2.2 | Provide all materials and construct fenced and gated compound to contain solar array and associated chambers to Specification | LS | 1 |  | 0
| 7.2.3 | Supply and install DN 25 water pipe take-off from rising main and standpipe for solar cleansing system | LS | 1 |  | 0
| 7.2.4 | Provide solar array cleansing step ladder and extendable washer to Specification | LS | 1 |  | 0
Supply and Installation of 220 VAC standby generator of rated power
| 7.3 | Supply, Install and connect by manually operated changeover switch standby generator capable of providing the VAC power required to operate the submersible borehole pump as specified above at half-load c/w roofed lockable waterproof steel protection cabinet. | nr | 1 |  | 0
Information to be provided by Bidder
Manufacturers Generator Set reference No.
|  | Output kVA at 1500rpm, 220V, single-phase, 50Hz, with power factor of 1.0 | kVA
|  | Fuel type (petrol/diesel) | type
|  | Fuel tank capacity | l
Air or water cooled
|  | Sub-total |  |  |  | 0
|  | Contingencies (10%) |  |  |  | 0
|  | Taxes (VAT @16%) |  |  |  | 0
|  | Total |  |  |  | 0
Meheba D Primary School supplied from Meheba D Rural Health Clinic
Meheba D Primary School Transfer Pipeline from Meheba D Rural Health Clinic
Bill 8. Transfer Pipeline from Rural Health Centre to Primary School
| Bill No. 8,1 Demolition and Site Clearance |  |  |  |  | 0
| 8.1.1 | In collaboration with the Inspector of Works, and based upon pipe lengths and alignment shown on layout plan, agree upon final alignment of pipelines, road crossings, location of all tees, bends, isolating valves, air valves, washouts, tapstands, and consumer connection offtakes. Set out pipeline centre-lines, survey, agree upon Starting Surfaces, and final lengths and produce final plans at horizontal scale of 1:200 for approval before proceeding further. | LS | 1 |  | 0
| 8.1..2 | General Clearance for urban land & rough grass land along pipeline wayleaves (trench width plus 0.5 m on either side) | ha | 0.02 |  | 0
| 8.1.3 | Removal of tree stumps within approved alignment. PROVISIONAL SUM | nr | 1 |  | 0
| 8.1.4 | Cut down and remove trees and tree stumps within approved alignment only if specifically directed to do so by Inspector of Works following agreement from the Host Community PROVISIONAL SUM | nr | 1 |  | 0
| Bill No.8.2: Excavation and backfilling of trenches - all pipelines |  |  |  |  | 0
| 8.2.1 | Excavate test pits along centre line of proposed pipeline to depth of 1m at least every 50 m | nr | 4 |  | 0
| 8.2.2 | Excavate and trim trench bed to depth not exceeding 1 m to ensure minimum cover to pipeline of 600 mm | m | 150 |  | 0
| 8.2.3 | Excavate and trim trench to depth not exceeding 1.5 m to ensure minimum cover to pipeline of 1000 mm | m | 17 |  | 0
| 8.2.4 | Over excavate trench by a further depth of 150mm in areas identified by the Inspector of Works as requiring imported granular backfill RATE ONLY | m3 | 2.196 |  | 0
| 8.2.5 | Import, place and compact granular backfill in areas identified by the Inspector of Works as requiring imported granular backfill. RATE ONLY, | m3 | 2.196 |  | 0
| 8.2.6 | Place and compact sidefill and backfill using selected excavated material free of stones and tree roots to depth 300 mm above crown of pipe, and after compaction, other excavated material thereafter to final surface | m | 167 |  | 0
| 8.2.7 | Dispose of all surplus excavated material off-site | LS | 1 |  | 0
| 8.2.8 | Supply and install DN 100 steel pipe sleeve beneath public road to carry DN 50 HDPE transfer pipe, the DN 50 HDPE pipe within the sleeve to be free of joints | m | 15 |  | 0
| Bill No. 8.3: Supply and Installation of transfer main- RHC to Primary School elevated water tank |  |  |  |  | 0
All PE compression joints and fittings shall be supplied complete with suitable pipe joint stiffeners. All steel fittings shall be epoxy coated and all nuts and bolts galvanised. Rate shall include supply, lay, bed, joint , pressure test, sterilize and flushing of HDPE pipelines
| 8.3.1 | HDPE DN50 pipe SDR17, PN 10 | m | 167
| 8.3.2 | Compression fitting, elbow 45o DN 50mm | nr | 1
| 8.3.3 | Equal tee compression fitting DN 50 x 50 x 50 mm | nr | 1
| 8.3.4 | Supply and Installation of DN 40 parallel Woltman type bulk water meter, metrological class B, minimum display 1 m3/hr, suitable for vertical mounting, within water tank inlet riser pipe complete with strainer (metallic double flanged body c/w lockable meter box pipe surround). The meter assembly shall comprise: 1 No. DN50 to DN40 reducer, 1 DN40 500mm long straight pipe length, 1 DN 40 mm double flanged vertically mounted parallel Woltman type meter, located approximately 1.5 m above ground level, 1 DN 40 250 mm straight pipe length, and one DN40 to DN50 reducer. | set | 1 |  | 0
| 8.3.5 | Gate Valve, double flange, 50 mm non-rising spindle type, with 2 No. flanged restraining adapters st. fl. to PE DN 50, complete with valve riser and valve box to suit | set | 1 |  | 0
| Bill 8.4 Concrete Works to Transfer Pipeline |  |  |  |  | 0
| 8.4.1 | At all 45o and 90o bends, pipeline tees, and end caps, provide and subsequently remove shuttering and cast thrust blocks against undisturbed trench bed and trench wall | nr | 1 |  | 0
|  | Sub-total |  |  |  | 0
|  | Contingencies (10%) |  |  |  | 0
|  | Taxes (VAT @16%) |  |  |  | 0
|  | Total |  |  |  | 0
Meheba D Primary School Storage and Distribution System
Bill 9:
| Item | Description | Unit | Qty | Rate (ZMW) | Amount (ZMW)
| Bill No. 9.1 Demolition and Site Clearance |  |  |  |  | 0
| 9.1.1 | In collaboration with the Inspector of Works, and based upon pipe lengths and alignment shown on layout plan, agree upon final alignment of pipelines, road crossings, location of all tees, bends, isolating valves, air valves, washouts, tapstands, and consumer connection offtakes. Set out pipeline centre-lines, survey, agree upon Starting Surfaces, and final lengths and produce final plans at horizontal scale of 1:200 for approval before proceeding further. | LS | 1 |  | 0
| 9.1.2 | General Clearance for urban land & rough grass land along pipeline wayleaves (trench width plus 0.5 m on either side) | ha | 0.2 |  | 0
| 9.1.3 | Removal of tree stumps within approved alignment. PROVISIONAL SUM | nr | 1 |  | 0
| 9.1.4 | Cut down and remove trees and tree stumps within approved alignment only if specifically directed to do so by Inspector of Works following agreement from the Host Community PROVISIONAL SUM | nr | 1 |  | 0
| Bill No. 2: Excavation and backfilling of trenches - all pipelines |  |  |  |  | 0
| 9.2.1 | Excavate test pits along centre line of proposed pipeline to depth of 1m at least every 50 m | nr | 11 |  | 0
| 9.2.2 | Excavate and trim trench bed to depth not exceeding 1 m to ensure minimum cover to pipeline of 600 mm | m | 484.2 |  | 0
| 9.2.3 | Excavate and trim trench to depth not exceeding 1.5 m to ensure minimum cover to pipeline of 900 mm | m | 53.8 |  | 0
| 9.2.4 | Over excavate trench by a further depth of 150mm in areas identified by the Inspector of Works as requiring imported granular backfill RATE ONLY | m3 | 4.842 |  | 0
| 9.2.5 | Import, place and compact granular backfill in areas identified by the Inspector of Works as requiring imported granular backfill. RATE ONLY, | m3 | 4.842 |  | 0
| 9.2.6 | Place and compact sidefill and backfill using selected excavated material free of stones and tree roots to depth 300 mm above crown of pipe, and after compaction, other excavated material thereafter to final surface | m | 484.2 |  | 0
| 9.2.7 | Dispose of all surplus excavated material off-site | LS | 1 |  | 0
| Bill No. 9.3: Tanks, Tankstands and Tap Stands |  |  |  |  | 0
Bidder shall supply outline details of water tank stand and tank c/w, pipework and fittings.
water tank stand manufacturer:
HDPE cylindrical tank manufacturer:
HDPE cylindrical tank supplier (if different):
Contractor shall supply full set of structural calculations and drawings for water tank stand certified by a registered structural engineer for written approval prior to fabrication.
| 9.3.1 | Conduct geotechnical investigations and design foundation and tank stand for the elevated tank | LS | 1 |  | 0
| 9.3.2 | Tank reinforced concrete foundations 1 m x 1m x 1.5 m deep inc. excavation, shuttering, concreting, curing, backfilling and disposal of excess spoil material from site | nr | 6 |  | 0
Supply and install 2 No. HDPE cylindrical tank on Contractor designed six vertical members) mild steel tankstand c/w with inlet float valves, all inflow, valved connecting, outflow, overflow, and scour (washout) pipework, fittings, adaptors and 10m high steel stand c/w access ladder and lightning arrestor.
| 9.3.3 | Capacity 15m3.(two no. of 7.5m3) | nr | 1 |  | 0
| 9.3.4 | Supply and paint all mild steel in tank stand with two coats of zinc 82% rich paint in dry film | LS | 1 |  | 0
| 9.3.5 | Leak testing and disinfection of tank and pipework | nr | 1 |  | 0
| 9.3.6 | Provide & install float level indicator gauge on side of tank readable from ground level adjacent to tank | nr | 1 |  | 0
| 9.3.7 | Provide and install chlorine cartridge type inline doser in lockable chamber at start of tank outlet pipe c/w twelve months supply of chlorine cartridges. | LS | 1 |  | 0
| 9.3.8 | Provide materials for and construct tap stand and associated drainage | nr | 8 |  | 0
|  | Carry forward |  |  |  | 0
|  | Brought forward |  |  |  | 0
| Bill No.9.4: Supply and Install Water Distribution Network |  |  |  |  | 0
All PE compression joints and fittings shall be supplied complete with suitable pipe joint stiffeners. All steel fittings shall be epoxy coated and all nuts and bolts galvanised. Rate shall include supply, lay, bed, joint , pressure test, sterilize and flushing of HDPE pipelines
| 9.4.1 | Network reticulation pipework HDPE DN50 (OD 63), SDR17, PN 10 | m | 386 |  | 0
| 9.4.2 | Equal tee compression fitting DN 50 x 50 x 50 mm | nr | 2 |  | 0
| 9.4.3 | Equal tee compression fitting DN 40 x 40 x 40 mm | nr | 1 |  | 0
| 9.4.4 | Compression reducer coupling 50mm x 40mm | nr | 6 |  | 0
| 9.4.5 | Compression reducer coupling 40mm x 32mm | nr | 2 |  | 0
| 9.4.6 | Network reticulation pipework HDPE DN 40mm, SDR17, PN 10 | m | 62 |  | 0
| 9.4.7 | Network reticulation pipework HDPE DN 32mm, SDR17, PN 10 | m | 84 |  | 0
| 9.4.8 | Compression fitting, elbow 90o DN 50mm | nr | 3 |  | 0
| 9.4.9 | End cap DN 32mm (compression type) | nr | 2 |  | 0
| 9.4.10 | Supply and install GI pipes 25mm dia c/w fittings to tap stands c/w isolating stop cock | nr | 8 |  | 0
| 9.4.11 | Supply and install heavy weight brass garden bib tap (non-lever arm type) | nr | 16 |  | 0
| 9.4.12 | Compression tee DN 40 x 40 x 1" male branch to connect to tap stand pipework | nr | 6 |  | 0
| 9.4.13 | Compression tee DN 32 x 32 x 1" male branch to connect to tap stand pipework | nr | 2 |  | 0
| 9.4.14 | Compression tee DN 50 x 50 x 1 1/2" male br., 1 No. female to male 1 1/2" to 1" thr. spigot to connect to tap stand pipework | nr | 5 |  | 0
| 9.4.15 | Gate Valve, double flange, 40 mm non-rising spindle type, with 2 No. flanged restraining adapters st. fl. to PE DN 40, complete with valve riser and valve box to suit | nr | 4 |  | 0
Air valve assembly consisting of 1 No. compression tee with threaded male 1 1/2" branch vertically upwards, 1 No. female to male thr. spigot, 1 No. Stopcock, thr. dble. socket 1", and 1 No. Single air valve, thr. female 1". RATE ONLY
| 9.4.16.1 | Compression tee DN 50 x 50 x 1 1/2" male br., 1 No. female to male 1 1/2" to 1" thr. spigot | set | 1
| 9.4.16.2 | Compression tee DN 40 x 40 x 1 1/2" male br., 1 No. female to male 1 1/2" to 1" thr. Spigot | set | 1
| 9.4.16.3 | Compression tee DN 32 x 32 x 1" male br, 1 No. female to male 1" to 1" thr. spigot | set | 1
|  | Carry forward |  |  |  | 0
|  | Brought forward |  |  |  | 0
| Bill No. 9.5: Concrete Works to all Pipelines |  |  |  |  | 0
All unreinforced concrete works shall be in medium strength concrete unless otherwise indicated. Where bends less than 45o are obtained by bending the pipe, radius not less than 35 x pipe diameter, and provided there is no compression joint with 5 metres of either end of radius, no separate thrust block is required.
| 9.5.1 | Over excavate in trench bed at all gate valves, air valve assemblies and steel fittings and cast support slab to full width of trench with other dimensions being the length of the valve or the fitting between flanges or between the compression tightening nuts and depth below trench bed of 150 mm | nr | 5 |  | 0
| 9.5.2 | At all 45o and 90o bends, pipeline tees, and end caps, provide and subsequently remove shuttering and cast thrust blocks against undisturbed trench bed and trench wall | nr | 8 |  | 0
| 9.5.3 | Supply all materials and cast and complete air-valve chamber. RATE ONLY | nr | 1
|  | Sub-total |  |  |  | 0
|  | Contingencies (10%) |  |  |  | 0
|  | Taxes (VAT @16%) |  |  |  | 0
|  | Total |  |  |  | 0

## Lumwana Hospital
UNICEF
Solar Powered Borehole Schemes in institutions in Meheba Refugee Camp & Host Communities
Lumwana Hospital
Bill No. RHC6:
Item | Description | Unit | Qty | Rate (ZMW) | Amount (ZMW)
Bill No. out, Demolition and Site Clearance |  |  |  |  | 0
1.1 | In collaboration with the Inspector of Works, and based upon pipe lengths and alignment shown on layout plan, agree upon final alignment of pipelines, road crossings, location of all tees, bends, isolating valves, air valves, washouts, tapstands, and consumer connection offtakes. Set out pipeline centre-lines, survey, agree upon Starting Surfaces, and final lengths and produce final plans at horizontal scale of 1:200 for approval before proceeding further. | LS | 1 |  | 0
1.2 | General Clearance for urban land & rough grass land along pipeline wayleaves (trench width plus 0.5 m on either side) | ha | 0.1 |  | 0
1.3 | Removal of tree stumps within approved alignment. PROVISIONAL SUM | nr | 1 |  | 0
1.4 | Cut down and remove trees and tree stumps within approved alignment only if specifically directed to do so by Inspector of Works following agreement from the Host Community PROVISIONAL SUM | nr | 1 |  | 0
Bill No. 2: Excavation and backfilling of trenches - all pipelines |  |  |  |  | 0
2.1 | Excavate test pits along centre line of proposed pipeline to depth of 1m at least every 50 m | nr | 9 |  | 0
2.2 | Excavate and trim trench bed to depth not exceeding 1 m to ensure minimum cover to pipeline of 600 mm | m | 367.2 |  | 0
2.3 | Excavate and trim trench to depth not exceeding 1.5 m to ensure minimum cover to pipeline of 900 mm | m | 40.8 |  | 0
2.4 | Over excavate trench by a further depth of 150mm in areas identified by the Inspector of Works as requiring imported granular backfill RATE ONLY | m3 | 3.672 |  | 0
2.5 | Import, place and compact granular backfill in areas identified by the Inspector of Works as requiring imported granular backfill. RATE ONLY, | m3 | 3.672 |  | 0
2.6 | Place and compact sidefill and backfill using selected excavated material free of stones and tree roots to depth 300 mm above crown of pipe, and after compaction, other excavated material thereafter to final surface | m | 367.2 |  | 0
2.7 | Dispose of all surplus excavated material off-site | LS | 1 |  | 0
Bill No. 3: Supply and Installation of rising main- borehole to elevated water tank |  |  |  |  | 0
All PE compression joints and fittings shall be supplied complete with suitable pipe joint stiffeners. All steel fittings shall be epoxy coated and all nuts and bolts galvanised. Rate shall include supply, lay, bed, joint , pressure test, sterilize and flushing of HDPE pipelines
3.1 | Raw water rising main from borehole to the Elevated Tank , HDPE DN50 (OD 63), SDR17, PN 10 | m | 51 |  | 0
3.2 | Supply and Installation of DN 40 parallel Woltman type bulk water meter, metrological class B, minimum display 1 m3/hr, suitable for vertical mounting, within water tank inlet riser pipe complete with strainer (metallic double flanged body c/w lockable meter box pipe surround). The meter assembly shall comprise: 1 No. DN50 to DN40 reducer, 1 DN40 500mm long straight pipe length, 1 DN 40 mm double flanged vertically mounted parallel Woltman type meter, located approximately 1.5 m above ground level, 1 DN 40 250 mm straight pipe length, and one DN40 to DN50 reducer. | set | 1 |  | 0
3.3 | Gate Valve, double flange, 50 mm non-rising spindle type, with 2 No. flanged restraining adapters st. fl. to PE DN 50, complete with valve riser and valve box to suit | set | 1 |  | 0
3.4 | Supply and install DN 25 water pipe take-off from rising mainand standpipe for solar cleansing system | LS | 1 |  | 0
3.5 | Provide solar array cleansing step ladder and extendable washer to Specification | LS | 1 |  | 0
| Carry forward |  |  |  | 0
| Brought forward |  |  |  | 0
Bill No. 4: Tanks, Tankstands and Tap Stands |  |  |  |  | 0
Bidder shall supply outline details of water tank stand and tank c/w, pipework and fittings.
water tank stand manufacturer:
HDPE cylindrical tank manufacturer:
HDPE cylindrical tank supplier (if different):
Contractor shall supply full set of structural calculations and drawings for water tank stand certified by a registered structural engineer for written approval prior to fabrication.
4.1 | Conduct geotechnical investigations and design foundation and tank stand for the elevated tank | LS | 1 |  | 0
4.2 | Tank reinforced concrete foundations 1 m x 1m x 1.5 m deep inc. excavation, shuttering, concreting, curing, backfilling and disposal of excess spoil material from site | nr | 6 |  | 0
Supply and install 2 No. HDPE cylindrical tank on Contractor designed six vertical members) mild steel tankstand c/w with inlet float valves, all inflow, valved connecting, outflow, overflow, and scour (washout) pipework, fittings, adaptors and 6m high steel stand c/w access ladder and lightning arrestor.
4.3 | Capacity 10m3.(two no. of 5m3) | nr | 1 |  | 0
4.4 | Supply and paint all mild steel in tank stand with two coats of zinc 82% rich paint in dry film | LS | 1 |  | 0
4.5 | Leak testing and disinfection of tank and pipework | nr | 1 |  | 0
4.6 | Provide & install float level indicator gauge on side of tank readable from ground level adjacent to tank | nr | 1 |  | 0
4.7 | Provide and install chlorine cartridge type inline doser in lockable chamber at start of tank outlet pipe c/w twelve months supply of chlorine cartridges. | LS | 1 |  | 0
4.8 | Provide materials for and construct tap stand and associated drainage | nr | 4 |  | 0
Bill No. 5: Supply and Install Water Distribution Network |  |  |  |  | 0
All PE compression joints and fittings shall be supplied complete with suitable pipe joint stiffeners. All steel fittings shall be epoxy coated and all nuts and bolts galvanised. Rate shall include supply, lay, bed, joint , pressure test, sterilize and flushing of HDPE pipelines
5.1 | Network reticulation pipework HDPE DN50 (OD 63), SDR17, PN 10 | m | 204 |  | 0
5.2 | Equal tee compression fitting DN 40 x 40 x 40 mm | nr | 1 |  | 0
5.3 | Unequal reducing tee compression fitting DN 50 x 50 x 40 mm | nr | 1 |  | 0
5.4 | Unequal reducing tee compression fitting DN 40 x 40 x 32 mm | nr | 4 |  | 0
5.5 | Compression reducer coupling 50mm x 40mm | nr | 5 |  | 0
5.6 | Network reticulation pipework HDPE DN 40mm, SDR17, PN 10 | m | 153 |  | 0
5.7 | Compression fitting, elbow 90o DN 50mm | nr | 2 |  | 0
5.8 | Compression fitting, elbow 90o DN 40mm | nr | 5 |  | 0
5.9 | End cap DN 32mm (compression type) | nr | 4 |  | 0
5.1 | Saddle clamp 32mm x 3/4" to supply individual consumer connection | nr | 4 |  | 0
5.11 | Supply and install GI pipes 25mm dia c/w fittings to tap stands c/w isolating stop cock | nr | 4 |  | 0
5.12 | Supply and install heavy weight brass garden bib tap (non-lever arm type) | nr | 8 |  | 0
5.13 | Compression tee DN 40 x 40 x 1" male branch to connect to tap stand pipework | nr | 1 |  | 0
5.14 | Compression tee DN 32 x 32 x 1" male branch to connect to tap stand pipework | nr | 0 |  | 0
5.15 | Compression tee DN 50 x 50 x 1 1/2" male br., 1 No. female to male 1 1/2" to 1" thr. spigot to connect to tap stand pipework | nr | 3 |  | 0
5.16 | Gate Valve, double flange, 40 mm non-rising spindle type, with 2 No. flanged restraining adapters st. fl. to PE DN 40, complete with valve riser and valve box to suit | nr | 3 |  | 0
Air valve assembly consisting of 1 No. compression tee with threaded male 1 1/2" branch vertically upwards, 1 No. female to male thr. spigot, 1 No. Stopcock, thr. dble. socket 1", and 1 No. Single air valve, thr. female 1". RATE ONLY
5.17.1 | Compression tee DN 50 x 50 x 1 1/2" male br., 1 No. female to male 1 1/2" to 1" thr. spigot | set | 1
5.17.2 | Compression tee DN 40 x 40 x 1 1/2" male br., 1 No. female to male 1 1/2" to 1" thr. Spigot | set | 1
| Carry forward |  |  |  | 0
| Brought forward |  |  |  | 0
Bill No. 6: Concrete Works to all Pipelines |  |  |  |  | 0
All unreinforced concrete works shall be in medium strength concrete unless otherwise indicated. Where bends less than 45o are obtained by bending the pipe, radius not less than 35 x pipe diameter, and provided there is no compression joint with 5 metres of either end of radius, no separate thrust block is required.
6.1 | Over excavate in trench bed at all gate valves, air valve assemblies and steel fittings and cast support slab to full width of trench with other dimensions being the length of the valve or the fitting between flanges or between the compression tightening nuts and depth below trench bed of 150 mm | nr | 4 |  | 0
6.2 | At all 45o and 90o bends, pipeline tees, and end caps, provide and subsequently remove shuttering and cast thrust blocks against undisturbed trench bed and trench wall | nr | 12 |  | 0
6.3 | Supply all materials and cast and complete air-valve chamber. RATE ONLY | nr | 1
Bill No. 7: Water Distribution Network | Electromechanical |  |  |  | 0
Bidder shall supply details of proposed pumpset c/w shroud, and standby generator for which there shall be a local agent
proposed submersible hybrid DC/AC pumpset manufacturer and agent:
proposed standby generator manufacturer and agent:
| confirm manufactures brochures included with bid |  | yes / no
No change from these manufacturers or agents shall be permitted without prior written approval from the Consultant
Submersible 48 VDC Borehole Pump
7.1 | Supply and install a hybrid DC/AC borehole submersible pump suitable for a borehole of ID 5" capable of being powered from either a 48 VDC or a nominal 230 VAC source c/w cabled connection to power sources located within 10 m of borehole head, pumping into an overhead tank with top water inlet 14 m above ground.. . |  | nr | 1
Information provided to guide Bidder
| Ground elevation at borehole (approximate) | masl | 1322
| Yield | m3/hr | 0.5 | tbc
| Pump installation level below ground surface | m | 39 | tbc
| Riser pipe diameter | mm | DN 50
| Dynamic water level below ground surface | m | 30 | tbc
| Top water level in overhead tank | masl | 1336
Information to be provided by Bidder
| Manufacturers Pump reference No. | ref.
| Maximum flow at Installation indicated above | m3/hr
| Maximum pump head at installation indicated above | m3/hr
| Optimum flow at Installation indicated above | m3/hr
| Optimum head at Installation indicated above | m3/hr
| Pump efficiency at installation | %
| Input power required by pump | W
| Output power required by solar array | W
| No. of solar panels and arrays offered and guaranteed to meet requirement | nr
7.2 | Solar arrays to meet requirements c/w security fence and gate and lightning protection as per Drawing to be included in this Option
7.2.1 | Supply, install, erect and connect solar arrays to meet requirements c/w lightning protection as per Drawing and Specification | nr | 1 |  | 0
7.2.2 | Provide all materials and construct fenced and gated compound to contain solar array and associated chambers to Specification | LS | 1 |  | 0
7.2.3 | Supply and install DN 25 water pipe take-off from rising main and standpipe for solar cleansing system | LS | 1 |  | 0
7.2.4 | Provide solar array cleansing step ladder and extendable washer to Specification | LS | 1 |  | 0
Supply and Installation of 220 VAC standby generator of rated power
7.3 | Supply, Install and connect by manually operated changeover switch standby generator capable of providing the VAC power required to operate the submersible borehole pump as specified above at half-load c/w roofed lockable waterproof steel protection cabinet. | nr | 1 |  | 0
Information to be provided by Bidder
Manufacturers Generator Set reference No.
| Output kVA at 1500rpm, 220V, single-phase, 50Hz, with power factor of 1.0 | kVA
| Fuel type (petrol/diesel) | type
| Fuel tank capacity | l
Air or water cooled
| Sub-total |  |  |  | 0
| Contingencies (10%) |  |  |  | 0
| Taxes (VAT @16%) |  |  |  | 0
| Total |  |  |  | 0

## Block D Transit Center 36
UNICEF
Solar Powered Borehole Schemes in institutions in Meheba Refugee Camp & Host Communities
Block D Transit Center 36
Bill No. TC1
| Item | Description | Unit | Qty | Rate (ZMW) | Amount (ZMW)
| Bill No. out, Demolition and Site Clearance |  |  |  |  | 0
| 1.1 | In collaboration with the Inspector of Works, and based upon pipe lengths and alignment shown on layout plan, agree upon final alignment of pipelines, road crossings, location of all tees, bends, isolating valves, air valves, washouts, tapstands, and consumer connection offtakes. Set out pipeline centre-lines, survey, agree upon Starting Surfaces, and final lengths and produce final plans at horizontal scale of 1:200 for approval before proceeding further. | LS | 1 |  | 0
| 1.2 | General Clearance for urban land & rough grass land along pipeline wayleaves (trench width plus 0.5 m on either side) | ha | 0.3 |  | 0
| 1.3 | Removal of tree stumps within approved alignment. PROVISIONAL SUM | nr | 1 |  | 0
| 1.4 | Cut down and remove trees and tree stumps within approved alignment only if specifically directed to do so by Inspector of Works following agreement from the Host Community PROVISIONAL SUM | nr | 1 |  | 0
| Bill No. 2: Excavation and backfilling of trenches - all pipelines |  |  |  |  | 0
| 2.1 | Excavate test pits along centre line of proposed pipeline to depth of 1m at least every 50 m | nr | 27 |  | 0
| 2.2 | Excavate and trim trench bed to depth not exceeding 1 m to ensure minimum cover to pipeline of 600 mm | m | 1215 |  | 0
| 2.3 | Excavate and trim trench to depth not exceeding 1.5 m to ensure minimum cover to pipeline of 900 mm | m | 135 |  | 0
| 2.4 | Over excavate trench by a further depth of 150mm in areas identified by the Inspector of Works as requiring imported granular backfill RATE ONLY | m3 | 12.15 |  | 0
| 2.5 | Import, place and compact granular backfill in areas identified by the Inspector of Works as requiring imported granular backfill. RATE ONLY, | m3 | 12.15 |  | 0
| 2.6 | Place and compact sidefill and backfill using selected excavated material free of stones and tree roots to depth 300 mm above crown of pipe, and after compaction, other excavated material thereafter to final surface | m | 1215 |  | 0
| 2.7 | Dispose of all surplus excavated material off-site | LS | 1 |  | 0
| Bill No. 3: Supply and Installation of rising main- borehole to elevated water tank |  |  |  |  | 0
All PE compression joints and fittings shall be supplied complete with suitable pipe joint stiffeners. All steel fittings shall be epoxy coated and all nuts and bolts galvanised. Rate shall include supply, lay, bed, joint , pressure test, sterilize and flushing of HDPE pipelines
| 3.1 | Raw water rising main from borehole to the Elevated Tank , HDPE DN50 (OD 63), SDR17, PN 10 | m | 135 |  | 0
| 3.2 | Compression fitting, elbow 45o DN 50mm | nr | 0 |  | 0
| 3.3 | Compression fitting, elbow 90o DN 50mm | nr | 1
| 3.4 | Supply and Installation of DN 40 parallel Woltman type bulk water meter, metrological class B, minimum display 1 m3/hr, suitable for vertical mounting, within water tank inlet riser pipe complete with strainer (metallic double flanged body c/w lockable meter box pipe surround). The meter assembly shall comprise: 1 No. DN50 to DN40 reducer, 1 DN40 500mm long straight pipe length, 1 DN 40 mm double flanged vertically mounted parallel Woltman type meter, located approximately 1.5 m above ground level, 1 DN 40 250 mm straight pipe length, and one DN40 to DN50 reducer. | set | 1 |  | 0
| 3.5 | Gate Valve, double flange, 50 mm non-rising spindle type, with 2 No. flanged restraining adapters st. fl. to PE DN 50, complete with valve riser and valve box to suit | set | 1 |  | 0
| 3.6 | Supply and install DN 25 water pipe take-off from rising mainand standpipe for solar cleansing system | LS | 1 |  | 0
| 3.7 | Provide solar array cleansing step ladder and extendable washer to Specification | LS | 1 |  | 0
|  | Carry forward |  |  |  | 0
|  | Brought forward |  |  |  | 0
| Bill No. 4: Tanks, Tankstands and Tap Stands |  |  |  |  | 0
Bidder shall supply outline details of water tank stand and tank c/w, pipework and fittings.
water tank stand manufacturer:
HDPE cylindrical tank manufacturer:
HDPE cylindrical tank supplier (if different):
Contractor shall supply full set of structural calculations and drawings for water tank stand certified by a registered structural engineer for written approval prior to fabrication.
| 4.1 | Conduct geotechnical investigations and design foundation and tank stand for the elevated tank | LS | 1 |  | 0
| 4.2 | Tank reinforced concrete foundations 1 m x 1m x 1.5 m deep inc. excavation, shuttering, concreting, curing, backfilling and disposal of excess spoil material from site | nr | 6 |  | 0
Supply and install 2 No. HDPE cylindrical tank on Contractor designed six vertical members) mild steel tankstand c/w with inlet float valves, all inflow, valved connecting, outflow, overflow, and scour (washout) pipework, fittings, adaptors and 6m high steel stand c/w access ladder and lightning arrestor.
| 4.3 | Capacity 20m3.(two no. of 10m3) | nr | 1 |  | 0
| 4.4 | Supply and paint all mild steel in tank stand with two coats of zinc 82% rich paint in dry film | LS | 1 |  | 0
| 4.5 | Leak testing and disinfection of tank and pipework | nr | 1 |  | 0
| 4.6 | Provide & install float level indicator gauge on side of tank readable from ground level adjacent to tank | nr | 1 |  | 0
| 4.7 | Provide and install chlorine cartridge type inline doser in lockable chamber at start of tank outlet pipe c/w twelve months supply of chlorine cartridges. | LS | 1 |  | 0
| 4.8 | Provide materials for and construct tap stand and associated drainage | nr | 5 |  | 0
| Bill No. 5: Supply and Install Water Distribution Network |  |  |  |  | 0
All PE compression joints and fittings shall be supplied complete with suitable pipe joint stiffeners. All steel fittings shall be epoxy coated and all nuts and bolts galvanised. Rate shall include supply, lay, bed, joint , pressure test, sterilize and flushing of HDPE pipelines
| 5.1 | Network reticulation pipework HDPE DN50 (OD 63), SDR17, PN 10 | m | 1078 |  | 0
| 5.2 | Equal tee compression fitting DN 50 x 50 x 50 mm | nr | 5 |  | 0
| 5.3 | Unequal reducing tee compression fitting DN 50 x 50 x 40 mm | nr | 18 |  | 0
| 5.4 | Compression reducer coupling 50mm x 40mm | nr | 10 |  | 0
| 5.5 | Compression reducer coupling 50mm x 32mm | nr | 1 |  | 0
131 | 5.6 | Network reticulation pipework HDPE DN 40mm, SDR17, PN 10 | m | 131 |  | 0
| 5.7 | Network reticulation pipework HDPE DN 32mm, SDR17, PN 10 | m | 6 |  | 0
| 5.8 | Compression fitting, elbow 45o DN 50mm | nr | 2 |  | 0
| 5.9 | Compression fitting, elbow 90o DN 50mm | nr | 9 |  | 0
| 5.1 | End cap DN 32mm (compression type) | nr | 22 |  | 0
| 5.11 | Saddle clamp 32mm x 3/4" to supply individual consumer connection | nr | 20 |  | 0
| 5.12 | Supply and install GI pipes 25mm dia c/w fittings to tap stands c/w isolating stop cock | nr | 5 |  | 0
| 5.13 | Supply and install heavy weight brass garden bib tap (non-lever arm type) | nr | 10 |  | 0
| 5.14 | Compression tee DN 50 x 50 x 1 1/2" male br., 1 No. female to male 1 1/2" to 1" thr. spigot to connect to tap stand pipework | nr | 5 |  | 0
| 5.15 | Gate Valve, double flange, 40 mm non-rising spindle type, with 2 No. flanged restraining adapters st. fl. to PE DN 40, complete with valve riser and valve box to suit | nr | 5 |  | 0
Air valve assembly consisting of 1 No. compression tee with threaded male 1 1/2" branch vertically upwards, 1 No. female to male thr. spigot, 1 No. Stopcock, thr. dble. socket 1", and 1 No. Single air valve, thr. female 1". RATE ONLY
| 5.16.1 | Compression tee DN 50 x 50 x 1 1/2" male br., 1 No. female to male 1 1/2" to 1" thr. spigot | set | 1
| 5.16.2 | Compression tee DN 40 x 40 x 1 1/2" male br., 1 No. female to male 1 1/2" to 1" thr. Spigot | set | 1
|  | Carry forward |  |  |  | 0
|  | Brought forward |  |  |  | 0
| Bill No. 6: Concrete Works to all Pipelines |  |  |  |  | 0
All unreinforced concrete works shall be in medium strength concrete unless otherwise indicated. Where bends less than 45o are obtained by bending the pipe, radius not less than 35 x pipe diameter, and provided there is no compression joint with 5 metres of either end of radius, no separate thrust block is required.
| 6.1 | Over excavate in trench bed at all gate valves, air valve assemblies and steel fittings and cast support slab to full width of trench with other dimensions being the length of the valve or the fitting between flanges or between the compression tightening nuts and depth below trench bed of 150 mm | nr | 6 |  | 0
| 6.2 | At all 45o and 90o bends, pipeline tees, and end caps, provide and subsequently remove shuttering and cast thrust blocks against undisturbed trench bed and trench wall | nr | 57 |  | 0
| 6.3 | Supply all materials and cast and complete air-valve chamber. RATE ONLY | nr | 1
| Bill No. 7: Water Distribution Network | Electromechanical |  |  |  | 0
Bidder shall supply details of proposed pumpset c/w shroud, and standby generator for which there shall be a local agent
proposed submersible hybrid DC/AC pumpset manufacturer and agent:
proposed standby generator manufacturer and agent:
|  | confirm manufactures brochures included with bid |  | yes / no
No change from these manufacturers or agents shall be permitted without prior written approval from the Consultant
Submersible 48 VDC Borehole Pump
| 7.1 | Supply and install a hybrid DC/AC borehole submersible pump suitable for a borehole of ID 5" capable of being powered from either a 48 VDC or a nominal 230 VAC source c/w cabled connection to power sources located within 10 m of borehole head, pumping into an overhead tank with top water inlet 14 m above ground.. . |  | nr | 1
Information provided to guide Bidder
|  | Ground elevation at borehole (approximate) | masl | 1404
|  | Yield | m3/hr | 2.1 | tbc
|  | Pump installation level below ground surface | m | 44 | tbc
|  | Riser pipe diameter | mm | DN 50
|  | Dynamic water level below ground surface | m | 38 | tbc
|  | Top water level in overhead tank | masl | 1420
Information to be provided by Bidder
|  | Manufacturers Pump reference No. | ref.
|  | Maximum flow at Installation indicated above | m3/hr
|  | Maximum pump head at installation indicated above | m3/hr
|  | Optimum flow at Installation indicated above | m3/hr
|  | Optimum head at Installation indicated above | m3/hr
|  | Pump efficiency at installation | %
|  | Input power required by pump | W
|  | Output power required by solar array | W
|  | No. of solar panels and arrays offered and guaranteed to meet requirement | nr
| 7.2 | Solar arrays to meet requirements c/w security fence and gate and lightning protection as per Drawing to be included in this Option
| 7.2.1 | Supply, install, erect and connect solar arrays to meet requirements c/w lightning protection as per Drawing and Specification | nr | 1 |  | 0
| 7.2.2 | Provide all materials and construct fenced and gated compound to contain solar array and associated chambers to Specification | LS | 1 |  | 0
| 7.2.3 | Supply and install DN 25 water pipe take-off from rising main and standpipe for solar cleansing system | LS | 1 |  | 0
| 7.2.4 | Provide solar array cleansing step ladder and extendable washer to Specification | LS | 1 |  | 0
Supply and Installation of 220 VAC standby generator of rated power
| 7.3 | Supply, Install and connect by manually operated changeover switch standby generator capable of providing the VAC power required to operate the submersible borehole pump as specified above at half-load c/w roofed lockable waterproof steel protection cabinet. | nr | 1 |  | 0
Information to be provided by Bidder
Manufacturers Generator Set reference No.
|  | Output kVA at 1500rpm, 220V, single-phase, 50Hz, with power factor of 1.0 | kVA
|  | Fuel type (petrol/diesel) | type
|  | Fuel tank capacity | l
Air or water cooled
|  | Sub-total |  |  |  | 0
|  | Contingencies (10%) |  |  |  | 0
|  | Taxes (VAT @16%) |  |  |  | 0
|  | Total |  |  |  | 0