ANNEX 1: SCHEDULE OF REQUIREMENTS – LOT 1

Scope of Work - Dialysis Centre (LOT 1) - Supply and installation of Dialysis Centre Bent Bya / 40 KW Off-grid (with grid switch) Solar Power System

Project Location: 26.625923,   13.623148.  Bent Bya, Libya

The system is designed to cover the Essential loads in Supply and installation of Dialysis Centre Bent Bya / 40 KW Off-grid (with grid switch) Solar Power System and the system will be grid interactive connected with battery backup system, which will allow many power sources options.

The system will import from the grid when loads are being more than the generated from PV and supply surplus electricity to the batteries when PV generates more than the loads, the batteries can be charged from Grid if PV output is not enough for loads and batteries.

The Contractor shall perform a detailed engineering site survey to acquire all necessary information for preparation of design documentation and discuss technical issues with representatives of all relevant stakeholders.

Contractor shall submit shop drawings for all architectural, civil, electrical and a complete photovoltaic solar system works, including a single line diagram showing all the components of the PV system, DC and AC distribution boards, PV Arrays lay out and battery backup systems connections and cables, wires cross section for all the system to be approved by the Engineer before executing the work.

Contractor shall submit the catalogues of each component showing the requested specifications stated at the bill of quantity.

The contractor shall submit the Manufacture testing certificate, country of origin, certified characteristics, test performance curves, spare parts regular (as recommended by manufacturer , maintenance manuals and manufacturer’s warranty for each components of the system.

As-built drawings and writing setting parameters shall be submitted after handing over the work.

Upon completion of the installation, the contractor shall organize an on-site training program for operation and maintenance purpose involving nominated employer's staff. Such a program shall be carried out during the commissioning phase. The cost of the training shall be deemed to have been included in the tendered rates.

The price includes all builders’ works, making good and reinstatement including necessary materials and workmanship as well as removal of unwanted materials to dump sites approved by the engineer to complete the job successfully.

All the electrical works shall be executed according to IEEE Standards, specifications and supervisor Engineer instructions.

The contractor shall arrange for all required safety measures, signs, and protections around the sites.

Delivery Requirements

| Delivery Requirements |  |
| --- | --- |
| Delivery date and time | Bidder shall deliver the goods Click or tap here to enter text. after Contract signature. |
| Delivery Terms (INCOTERMS 2020) | DAP |
| Customs clearance (must be linked to INCOTERM | ☐ Not applicable Shall be done by: ☐ Name of organisation (where applicable) ☐ Supplier/bidder ☐ Freight Forwarder |
| Exact Address(es) of Delivery Location(s) | Dialysis Centre Bent Bya, Libya |
| Distribution of shipping documents (if using freight forwarder) | As per the BoQ |
| Packing Requirements | As per the BoQ |
| Training on Operations and Maintenance | As per the BoQ |
| Warranty Period | One Year after completion of works and acceptance certificate approved by UNDP Engineer |
| After-sales service and local service support requirements | As per the BoQ |
| Preferred Mode of Transport | Land |

ANNEX 1: SCHEDULE OF REQUIREMENTS – LOT 2

Scope of work  - Isolation centre & Medical Lab (LOT 2) - Supply and installation of Isolation centre & Medical Lab Bent Bya / 45 KW Off-grid (with grid switch) Solar Power System

Project Location: 26.645228,   13.656177.  Bent Bya Libya

The system is designed to cover the Essential loads in Supply and installation of Isolation centre & Medical Lab Bent Bya  /  45 KW Off-grid (with grid switch) Solar Power System and the system will be grid interactive connected with battery backup system, which will allow many power sources options.

The system will import from the grid when loads are being more than the generated from PV and supply surplus electricity to the batteries when PV generates more than the loads, the batteries can be charged from Grid if PV output is not enough for loads and batteries.

The Contractor shall perform a detailed engineering site survey to acquire all necessary information for preparation of design documentation and discuss technical issues with representatives of all relevant stakeholders.

Contractor shall submit shop drawings for all architectural, civil, electrical and a complete photovoltaic solar system works, including a single line diagram showing all the components of the PV system, DC and AC distribution boards, PV Arrays lay out and battery backup systems connections and cables, wires cross section for all the system to be approved by the Engineer before executing the work.

Contractor shall submit the catalogues of each component showing the requested specifications stated at the bill of quantity.

The contractor shall submit the Manufacture testing certificate, country of origin, certified characteristics, test performance curves, spare parts regular (as recommended by manufacturer, maintenance manuals and manufacturer’s warranty for each components of the system.

As-built drawings and writing setting parameters shall be submitted after handing over the work.
Upon completion of the installation, the contractor shall organize an on-site training program for operation and maintenance purpose involving nominated employer's staff. Such a program shall be carried out during the commissioning phase. The cost of the training shall be deemed to have been included in the tendered rates.
The price includes all builders’ works, making good and reinstatement including necessary materials and workmanship as well as removal of unwanted materials to dump sites approved by the engineer to complete the job successfully.
All the electrical works shall be executed according to IEEE Standards, specifications and supervisor Engineer instructions.

The contractor shall arrange for all required safety measures, signs, and protections around the sites.

Delivery Requirements

| Delivery Requirements |  |
| --- | --- |
| Delivery date and time | Bidder shall deliver the goods Click or tap here to enter text. after Contract signature. |
| Delivery Terms (INCOTERMS 2020) | DAP |
| Customs clearance (must be linked to INCOTERM | ☐ Not applicable Shall be done by: ☐ Name of organisation (where applicable) ☐ Supplier/bidder ☐ Freight Forwarder |
| Exact Address(es) of Delivery Location(s) | Isolation centre & Medical Lab Bent Bya, Libya. |
| Distribution of shipping documents (if using freight forwarder) | As per the BoQ |
| Packing Requirements | As per the BoQ |
| Training on Operations and Maintenance | As per the BoQ |
| Warranty Period | One Year after completion of works and acceptance certificate approved by UNDP Engineer |
| After-sales service and local service support requirements | As per the BoQ |
| Preferred Mode of Transport | Choose an item. |