ITB Scope of the Works (SoW) and Work Schedules Template

eSourcing Reference: ITB/2021/22717

GENERAL INFORMATION

Works Description: 	Rehabilitation and Construction of One-Stop-Shop (OSS) Infrastructure Facilities;

Project Location: 	Okugu Refugee Camp, Jewi Refugee Camp, and Pungindo II Refugee Camp - Gambella Regional State, Ethiopia;

No of Project Sites:	3 Sites

Construction Duration: 	150 Calendar Days (5 months) for the Whole Works;

DNP Period: 	12 Months

Design Review Unique ID: 	M22635914

Type of Competition:	Open International Tender

Type of the Contract:	Short Form Construction Contract

Expected Start Date:  	01st August 2021

Partner:	United Nations High Commissioner for Refugees (UNHCR)

Implementing Agency:	United Nations Office for Project Services (UNOPS)

Project Purpose:	Construction of the OSS Registration Model towards operational and functional Infrastructure Facilities meeting the Local Construction Practice and relevant standards for construction of infrastructure projects in Ethiopia.

Project Output:	Construction of OSS Registration Model; staff and guest toilets; Construction of new Guard house; External works such as walkways, power and water supply.

PART I:  SCHEDULE OF WORKS

- PROJECT BACKGROUND

UNHCR, the UN Refugee Agency, together with UNICEF, Vital Events Registration Agency (VERA) and the Agency for Refugees and Returnees Affairs (ARRA) has identified 27 centers to establish One-Stop-Shop (OSS) Registration Model located at different parts of the country; where the refugees can access services such as the registration of births, marriages, divorces, and deaths and receive protection referrals and civil documentation. These services will also be available to people from the local communities surrounding the camp. The establishment of the UNHCR centers, also known as a One-Stop-Shop (OSS), marks the beginning of a process that will lead to a government-owned digitalized and harmonized model for refugees’ assistance that will also serve local communities. The initiative is in line with the Global Compact on Refugees which promotes the provision of common services and infrastructure for both refugees and local communities. The list of 27 OSS sites is depicted under the table below.

| Ser. No | UNHCR Sub-Office | Refugee Camp/Site | GPS Coordinates ( One - Stop Shop registration center) |
| --- | --- | --- | --- |
| 1 | Shire | Mai-Aini Camp | 13°39 ̍28.4 ̍ ̍N 38 °09 ̍26.86 ̍ ̍E |
| 2 |  | Adi Harush Camp | 13°58 ̍85.9 ̍ ̍N 38 °13 ̍30.42 ̍ ̍E |
| 3 |  | Shimelba Camp | 14°10 ̍25.0 ̍ ̍N 37°43 ̍17.3 ̍ ̍E |
| 4 |  | Hitsats Camp | 14°06 ̍14.2 ̍ ̍N 37°57 ̍41.6 ̍ ̍E |
| 5 |  | Aysaita Camp | 13°58 ̍85.9 ̍ ̍N 38 °13 ̍30.42 ̍ ̍E |
| 6 |  | Barahle Camp | 13°58 ̍85.9 ̍ ̍N 38 °13 ̍30.42 ̍ ̍E |
| 7 | Gambella | Pugnido Camp (Nuer Site) | 7042’78.8’' N, 34014’94.7' E |
| 8 |  | Pugnido Camp (Agnuak) | 7038’99.6’' N, 34016’0.34’' E |
| 9 |  | Kule Camp | 8.284897 N, 34.25206 E |
| 10 |  | Jewi Camp | 8.145354 N, 34.711963 E |
| 11 |  | Okugo Camp | 6.494384 N, 35.128506 E |
| 12 |  | Tierkidi Camp | 8.275372 N, 34.274078 E |
| 13 |  | Pugnido II Camp | 7042’19.8’’N, 34014’43.9’' E |
| 14 |  | Ngueyyiel Camp | 8.303518 N, 34.324561 E |
| 15 | Asosa | Sherkole Camp | N 10.371960, E 034.611790 |
| 16 |  | Bambasi Camp | N 09.778400, E 034.779110 |
| 17 |  | Tongo Camp | N 09.380600,E 034.421350 |
| 18 |  | Tsore Camp | N 10.2374080, E 034.6116290 |
| 19 |  | Gure-Shembola Camp | N 09.524010, E 034.496870 |
| 20 | Jigjiga | Kebribeyah Camp | 9.091817 N, 43.176103 E |
| 21 |  | Aw-barre Camp | 9.788279 N, 43.232779 E |
| 22 |  | Sheder Camp | 9.699634 N, 43.132174 E |
| 23 | Melkadida | Bokolmanyo Camp | 4.541028 N, 41.533141 E |
| 24 |  | Melkadida Camp | 4.522819 N, 41.723127 E |
| 25 |  | Kobe Camp | 4.480976 N, 41.748822 E |
| 26 |  | Hilaweyn Camp | 4.363201 N, 41.863665 E |
| 27 |  | Buramino Camp | 4.301314 N, 41.914823 E |

Table-1:  List of OSS Sites for Rehabilitation/ Construction

Given the context described above, UNHCR embarked on the construction of OSS registration facilities in all refugee camps. In 2018, UNHCR funded the construction of 16 OSS structures with the aim to have functional infrastructures at the end of 2018. Currently the construction of 16 OSS centers that include facilities such as registration offices, waiting area, reception, archives, litigation/protection room, and server room including toilets have not been fully completed. 11 further OSS facilities are under preparation to start construction very soon. There exists the need to rehabilitate and complete these facilities to the required standard and allow the next phase of the registration process to commence soon.

Among the 27 OSS selected sites, this tender would specifically refer to the construction of the three sites highlighted in table 1 above, all located in Gambella Regional State: Namely; Jewi Camp Site, Okugo Camp Site, and Pungindo-II Refugee Camp.

- GENERAL DESCRIPTION OF THE WORKS

UNOPS intends to construct infrastructure facilities referred as One-Stop-Shop (OSS) Registration Model so that the refugees can access services such as the registration of births, marriages, divorces, and deaths and receive protection referrals and civil documentation. The scope of work includes the construction of a One-Stop Shop (OSS) Registration Model building, staff and guest toilets, guard post and external facilities on the proposed sites in Jewi Camp Site, Okugo Camp Site and Pungindo-II Refugee Camp, all located in Gambella Region, Ethiopia. The scope of works will include:

- Construction of about 250 m2 area OSS Registration Building Model;

- Construction of Staff and Guest Toilets as separated for men and women including provisions and access for PWD;

- Construction of Guard Post;

- Elevated water tanker for supply of water to the flush toilets and water points via gravity;

- Piping works for ensuring proper water supply from elevated tankers and waste water drainage systems to the proposed latrines including manholes;

- A water point included corresponding to COVID-19 response;

- Access, Parking and external walkways as necessary.

- External facilities such as fencing and septic tanks.

The construction of the OSS Center will include the following works:

a)	Mobilization

- Site preparations, sign board, site safety and security works;

b)  	Civil Works

  - Earthwork: Setting out of the building structures, site clearing and excavation, backfill with 	selected material (95% Proctor) and cart away as directed by the site supervisor;

  - Foundation work: Strip masonry foundation for the OSS Building, Guard post and toilet buildings;

  - Concrete Ground Floor: Reinforced concrete floor for the buildings on top of well compacted fill material and crushed stone hardcore as detailed on the drawings;

  - Concrete structural Frame: Reinforced concrete for ground beams, vertical columns, and top tie beams of C-25 concrete grade and high strength reinforcement bars;

  - Walls made of Hollow Concrete Block 3.4m high around the perimeter and partition of the buildings;

  - Steel Roof Structure:  Supply and fix steel truss and purlins for the OSS Center, guard post and toilets;

  - Roof Sheeting:  CIS sheet roofing cover for the OSS Center, guard post and toilets all as per the drawings;

  - Finishing:  Ceramic tile finish for the floors of the OSS and toilet buildings. Plastered and Painted for the internal walls and rendering for external walls. Plastered and painted internal wall surface of toilets with ceramic wall tiling.  Chipwood ceiling for the OSS Center all as per the drawing.

  - Door and Windows: 38mm thick LTZ steel framed metal door and windows with 5mm and 4mm glazing fixed for windows and top of doors.

c)	Mechanical, Electrical and Plumbing (MEP) Works

  - Water Supply:  10,000-liter water reservoir Water to be filled from a borehole. The water reservoir will be seated on raised masonry platform. Water supply provided to all the toilets and water point for drinking and washing purposes.

  - Supply and fix sanitary fixtures such as hand wash basin and squatting pan at the toilets;

  - Waste Water Drainage: Construction of septic tank for the toilet and connection of UPVC pipes between the fixture and the septic, manholes using stone masonry and vent pipes for 	the pit latrine;

  - Storm water Drainage System:  Construction of gutter, downpipes from roof of the buildings and splash apron as per the drawings.

  - Fire extinguishers: Supply and fix fire extinguishers as per the drawings;

  - Power Supply:  No grid power in the vicinity. PV system will be provided by UNHCR for power source to provide lightings, and power sockets.

  - Electrical Installation: Installation of cables from the switch panel and wiring in the buildings for lighting, and power sockets all as per the drawing;

  - Electrical fixtures: Supply and fix fittings for lighting in buildings and external lightings and power sockets all as per the electrical drawings.

- TECHNICAL SPECIFICATIONS

Details the works description and technical requirements including a detailed description of all the work to be performed by the Contractor, including temporary work and the Employer’s technical requirements and references to this contract, drawings and BoQ included separately and form part of this contract.

For further specifications and details, please refer to the following technical specifications compiled and documents separately and remain part of the SoW.

- Technical Specification for Civil Works – Section A;

- Technical Specifications for Electrical Works – Section –B;

- Technical Specifications for Sanitary Works – Section -C

- DRAWINGS

The respective sites are provided with the following drawings:

| No. | Annexure | Drawing Description (Title) | Drawing Number | Date | Revision Number |
| --- | --- | --- | --- | --- | --- |
| A. Architectural Drawings |  |  |  |  |  |
| 1 | AR | Site Plan | AR 01/12 | 02/05/21 | Rev-0 |
| 2 | AR | Ground Floor Plan – Registration Model | AR 02/12 | 02/05/21 | Rev-0 |
| 3 | AR | Roof Plan – Registration Model | AR 03/12 | 02/05/21 | Rev-0 |
| 4 | AR | Section & Elevation – Registration Model | AR 04/12 | 02/05/21 | Rev-0 |
| 5 | AR | Elevation – Registration Model | AR 05/12 | 02/05/21 | Rev-0 |
| 6 | AR | Window/Door Schedule – Registration Model | AR 06/12 | 02/05/21 | Rev-0 |
| 7 | AR | Guest & Toilets Plan | AR 07/12 | 02/05/21 | Rev-0 |
| 8 | AR | Staff Toilet Plan | AR 08/12 | 02/05/21 | Rev-0 |
| 9 | AR | Guard Post Block | AR 09/12 | 02/05/21 | Rev-0 |
| 10 | AR | Gate and Fence Details | AR 10/12 | 02/05/21 | Rev-0 |
| 11 | AR | Generator House | AR 11/12 | 02/05/21 | Rev-0 |
| 12 | AR | Water Reservoir Plan and Hand wash trough Details | AR 12/12 | 02/05/21 | Rev-0 |
| B. Structural Drawings |  |  |  |  |  |
| 13 | ST | Structural Notes | ST 01/10 | 02/05/21 | Rev-0 |
| 14 | ST | Ground Floor Slab Reinforcement, Beam and Column Layout | ST 02/10 | 02/05/21 | Rev-0 |
| 15 | ST | Roof Beam and Truss Layout | ST 03/10 | 02/05/21 | Rev-0 |
| 16 | ST | Beam and Column Details | ST 04/10 | 02/05/21 | Rev-0 |
| 17 | ST | Beam and Truss Details | ST 05/10 | 02/05/21 | Rev-0 |
| 18 | ST | Truss Details | ST 06/10 | 02/05/21 | Rev-0 |
| 19 | ST | Staff Toilet Structural Details | ST 07/10 | 02/05/21 | Rev-0 |
| 20 | ST | Guest Toilet Structural Details | ST 08/10 | 02/05/21 | Rev-0 |
| 21 | ST | Guard Post Structural Details | ST 09/10 | 02/05/21 | Rev-0 |
| 22 | ST | Water Tanker Support Details | ST 10/10 | 02/05/21 | Rev-0 |
| C. Electrical Drawings |  |  |  |  |  |
| 23 | EL | Electrical Installation Site Plan | EL 01/06 | 02/05/21 | Rev-0 |
| 24 | EL | Electrical Installation Plan - Lighting | EL 02/06 | 02/05/21 | Rev-0 |
| 25 | EL | Socket Outlet, firefighting and Fan Layout | EL 03/06 | 02/05/21 | Rev-0 |
| 26 | EL | Distribution Board Schedule | EL 04/06 | 02/05/21 | Rev-0 |
| 27 | EL | Data and Tele Outlet | EL 05/06 | 02/05/21 | Rev-0 |
| 28 | EL | Earthing Detail, Manhole and Lightening Protection | EL 06/06 | 02/05/21 | Rev-0 |
| D. Sanitary Drawings |  |  |  |  |  |
| 29 | SN | Site Sanitary Plan | SN 01/04 | 02/05/21 | Rev-0 |
| 30 | SN | Sanitary Layout and Details for Staff Toilets | SN 02/04 | 02/05/21 | Rev-0 |
| 31 | SN | Sanitary Layout and Details for Guest Toilets | SN 03/04 | 02/05/21 | Rev-0 |
| 32 | SN | Septic Tank Details | SN 04/04 | 02/05/21 | Rev-0 |

- STANDARDS AND PROCEDURES

The quality of all materials and workmanship used in the execution of the works shall comply with the requirements of the most recent issues of the following standards:

Ethiopian Building Code Standards:

- ES EN 1990:2015		Basis of Structural Design

- ES EN 1991:2015		Action on Structures (Part 1; 1.1, 1.4)

- ES EN 1992:2015		Design of Concrete Structures (Part 1; 1.1 and 1.2)

- ES EN 1998:2015		Design of Structures for Earthquake Resistance (Part 1 and 5)

- ES EN 1993:2015		Design of Steel Structures (Part 1.1)

- The UNOPS Planning and Design Manual

- UNOPS Environmental Management System Handbook 2014, Guidelines and Policies, which can be downloaded from UNOPS website (https://www.ungm.org/UNUser/Documents/DownloadPublicDocument?docId=1016855):

- Environmental Management Plan - EMP (to be attached with this Tender)

- Local and International Practice for Quality Management;

- UNOPS Occupational Health and Safety Requirements

- PROGRAMME REQUIREMENTS

The successful bidder will be expected to submit a contract programme in accordance with Sub-Clause 7.2.

The Contract Programme must be in such form and detail as the Employer’s Representative requires and must contain as a minimum:

- The order in which the Contractor proposes to carry out the Works;

- The time limits within which submission of any Contractor’s documents are required under the Contract.

The Contract Programme must be prepared in sufficient detail to ensure the adequate planning, execution and monitoring of the Works. The networked activities must be detailed enough to provide a meaningful measurement tool for progress of works.

The Contract Programme must be resource loaded and include material, plant and labour. The labour resource assignment must be further broken down to clearly identify types (trade and/or discipline) and number of resources allocated to an activity.

The Contract Programme must be accompanied by and/or detail:

- A programme narrative that describes the inclusions and assumptions made in preparing the 	Contract Programme;

- A general description of the arrangements and methods which the Contractor proposes to adopt for carrying out the Works;

- The critical path for the Works and a complete critical path analysis for the execution of the Works which must show clearly the links between activities and the float times available within the Contract Programme and the earliest start/earliest finish and latest start/latest finish times for each and every activity;

- The Preliminary Programme may be prepared in MS Excel or MS Project. The Outline Statement of Proposed methods demonstrates the Bidder’s capacity to identify the core or sensitive components required to complete the works within the required quality expectations and indicated the approach that the Bidder intends to use in order to execute those components.

- Details, and durations on Site, of the resources proposed to achieve the Contract Programme;

- A manpower (resource) histogram detailing cumulative and monthly volumes by trade for the duration of the Works;

- A detailed cash flow estimate, in quarterly periods, of all payments to which the Contractor may be entitled under the Contract;

- A schedule of all submittals and material procurement activities, including time for submittals, re-submittals and reviews and time for any fabrication and delivery of manufactured products and samples. The interdependence of design, procurement and construction activities must be included in this schedule.

- TESTING

The Basic Test requirements are given under the following table. However, the Contractor need to conduct other relevant tests as necessary and required by the UNOPS Project Manager.

| No | Description of test | Required result |
| --- | --- | --- |
| 1 | Compactions | 95% Standard Proctor Test |
| 2 | Cement: | Ordinal Portland Cement - ASTM C150-74 |
| 3 | Concrete Aggregates: Sand and Gravel Gradation | ASTM C33 |
| 4 | Concrete: Compressive Strength and Slump Test | Euro-Code: 25 Mpa Cube Crushing strength: Slump Test- ASTM C143 |
| 5 | Reinforcement Bar: Yield Strength | 460 Mpa |
| 6 | Roof Steel Structure - Hollow Sections: Yield Strength and Ultimate Strength | Yiled: 275 Mpa Ultime: 350 Mpa |

- REPORTING REQUIREMENTS

Monthly, Quarterly and Final Report with the following minimum information:

- Executive Summary of construction activities during the month;

- Background information of the construction work;

- Detail work executed during the month;

- Resource supply: Materials, workmen, equipment and tools;

- Quality supervision and procedures made in the execution of the works;

- Approvals made to construction resources on the basis of submittals, mock ups, tests, certificates, product catalogues etc...

- Any changes, work orders and variations issued;

- Any challenges and/or compensation events or unforeseeable obstructions;

- Any defectives works identified during supervision and proposal for rectifications;

- Detail work Plan for the next month as distinguished by weekly plans;

- Pictures of the works at each stage

- DOCUMENTATION

The contractor shall keep and make available as required the below documents:

- Drawings and specifications of works

- Instructions given by the engineer on the site book

- Any official letters/e-mail communications between UNOPS and the contractor

- Work plan

- Monthly reports

- Financial updates: Payments made and the outstanding balances;

- Claims and Variations

- Handover Certificates.

- TIMING AND CONSTRUCTION MILESTONES

The Contractor must comply with the following timing requirements:

| No. | Construction Milestones | Duration (approx.) | Remarks (if any) |
| --- | --- | --- | --- |
| 1 | Mobilization | 14 Calendar days | Contractor to mobilize immediately after signing of agreement. UNOPS shall issue a letter of intent to the successful bidder and shall be taken adequate to initiate contractor to mobilize. |
| 2 | Construction of registration model, staff and guest toilets including construction of guard post | 120 Calendar Days | Construction works at the three sites to take place concurrently. |
| 3 | External works: walkways and circulation, water supply and fencing works | 30 calendar Days | - |
| 4 | Commissioning for Handover: Testing, commissioning and site clearing works | 7 calendar days |  |
| T o t a l Calendar Days |  | 5 Months |  |

- Mobilization Period: mobilization shall commence within 14 days after signing of the contract. It shall include the following activities during this time:

- Site Possession;

- Setting out

- Submission of Work Program;

- Submission of Safety and Health (H&S) and Environment Management Plans;

- Arrangement and submission of Bank Guarantee (BG) for Performance;

- Site Preparations such as site office, storage areas, access to the workmen and equipment etc;

- Resource Mobilization to the site; and

- Issuance of the necessary Insurances to the works, personnel, equipment and third-party all according to the contract.

- Construction of the Whole Works:

- Concrete Columns and Ring beams;

- Roof steel structure such as trusses, purlin and rafter made of hollow sections'

- Roof steel sheet work;

- walls;

- Finishing works such as plastering, painting, ceiling and tiling works;

- Electrical Installation works

- Plumbing works

- Defects Notification Period (DNP):  12 Months

- A snagging list identification and updating;

- Rectification of the snagging list;

- Technical and Financial Closure of the project; and

- Final Handover.

PART II:  SCHEDULE OF SITE

- DESCRIPTION OF THE SITE

Three new sites proposed for construction of the OSS center, namely: Okugu, Jewi and Puiginido II are located under Gambella UNHCR sub-office, although the former is found far from Gambella town in the Southern Nations and Nationalities, and Peoples (SNNP) region close to South Sudan border.

- Okugu Camp - OSS Center

- Location: The Okugu camp is located in the SNNP Region over 200 Km South of Gambella town close to the South Sudan boundary. The nearest town to the camp is Dimma town only 7 Km to the West. (GPS: Coordinates of 6.494384 N, 35.128506 E);

- Site: The Okugu OSS sites with an estimated area of 1,155 m2 (33.0m x 35.0m) is currently open land bounded by paved road to the North-West, existing refugee reception center to the South-East, temporary toilets for the refugees to the North-East and scattered refugee households to the South-West.

Okugu Site / Google Map

- The land has no formal land ownership title-deed but it was noted that it is government owned land managed by ARRA. This site has a sloppy topography of approximately 15% towards the road (North-west) and covered by grass, shrubs and trees.

Okugu – Site Topography

- Urban Features: The neighborhood of the project site is characterized by grass land. The land and its vicinity has no historical, cultural and archeological significance. Additionally, within the camp, there are various facilities such as health center, food distribution building, safe house, refugee shelters, school, church, playground and other partner’s buildings. There is also a military base at a distance of 5km from the camp. Dima town is also located within 7 Km from the Camp.

- Existing Infrastructure (Utilities and accessibility):  The main road from Dimma town to Okugu camp is asphalt road. The proposed land is located at a close proximity to the main asphalt road and is accessed through gravel road which branches from the main asphalt road that stretches from Dima town to Ethio-South Sudan boarder.

- The water source is from Akobo river with piping system and distribution the refugee camp, offices and amenities. The water supply is managed by DRC. The water supply system to the Center can be tapped from the pipeline passing proximate to the site.  Since the existing water source is treated and clean water, it is scarce and not adequate capacity for construction purposes. Consequently, water for construction purpose need to be transported from the nearby river.

- No power grid system available at the camp and the OSS site. The only power source to be considered are Generator and/or Solar power.  The team realized during the visit that UNHCR is planning to provide power to the OSS via generator. However always recommended to use renewable energy such as PV solar power or wind.

- No storm water drainage system for the site and its surrounding. Due to the sloppy terrain of the site, storm water drainage of the site needs careful planning and consideration. Surface water from the upstream, rainwater from the roof of the building and the site premises shall be collected and channeled to the adjacent grave road.

- No ICT cabling to the site. Recommended to consider connection of the site with fiber cabling from the offices.

- Neighborhood character: At the time of site visit, the town has been noted to be peaceful. However, a high level of robbery is common as the area is well known by its gold mining resources. Moreover, abduction of children by Murle tribesmen crossing the border from South Sudan is common in the area. Travel to Dima starting from "Megenteya" area is only allowed by UNDSS with escort by federal police. Additionally, there exist UN Dima curfew daily between 22hr -06hr. If conflict happens, there might be restriction of movement to the camp. Consequently, delay on the project may happen.

- Sub-surface Condition: The site is predominantly covered with stiff red clay soil to a depth of 3.0m. The site is infested with termite; hence precautions need to be taken in the use of wood and eucalyptus as construction material for the OSS centers. No information regarding the availability of ground water.  The DRC representative who is responsible for the water distribution within the camp advised that there is a pipe passing through the proposed site. DRC shall be consulted during construction work of the OSS sites regarding the actual locations of buried water pipelines.  Pursuant to the Ethiopian Building Code Standard, the Okugu site is free of seismic hazard with zero ground motion.

- Jewi Camp – OSS Center

- Location: The camp is located at a distance of 19 km from Gambella town to the East at a geographical coordinate of 8.145354N, 34.711963E. The nearest town to the site with access to various urban amenities is Gambella.

- Site:  The site is also located at a distance of 200m from UNHCR office and exactly in front of the road. The site is proximate to the UNHCR sub office and the refugee camps as well as its accessibility from the main road.

- The land has no formal land ownership title-deed but it was noted that it is government owned land managed by ARRA. No requirement for ownership permit of the land during construction. All the sites are generally flat land with gentle slope and covered with grass, shrubs and trees.

Site Topography of Jewi Site

- Urban Features: The neighborhood of the project site is characterized by grass land covered by shrubs and trees. The land and its vicinity has no historical, cultural and archeological significance. Additionally, within the camp, there are various facilities such as health center, food distribution building, safe house, refugee shelters, school, church, playground and other partner’s buildings.

- Existing Infrastructure (Utilities and accessibility): The main road from Gambella town to Jewi is asphalt road with internal roads to and within the camp made of gravel roads. Proposed OSS center 2 and 3 are located immediately after the internal road. Hence no problem of accessing the site during and after construction.

- The water supply of the camp is managed by Jewi Water Supply Bureau. The source of the supply is Baro river with piping system and distribution the refugee camp, offices and amenities. The water supply system to the Center can be tapped from the pipeline passing proximate to the site.  Since the existing water source is treated and clean water, it is scarce and not adequate capacity for construction purposes. Consequently, water for construction purpose need to be transported from the nearby river.

- No power grid system available at the camp and the OSS site. The only power source to be considered are Generator and/or Solar power.  The team realized during the visit that UNHCR is planning to provide power to the OSS via generator. However always recommended to use renewable energy such as PV solar power or wind.

- No storm water drainage system for the site and its surrounding. Surface water from the upstream, rainwater from the roof of the building and the site premises shall be collected and channeled to the adjacent grave road.

- No ICT cabling to the site. Recommended to consider connection of the site with fiber cabling from the offices.

- Neighborhood character: Conflicts between the two major communities i.e. Angwake and Nuer usually occur. However, at the time of assessment, no conflict in Gambella town has been noticed and the security situation of the camps is peaceful. Robbery has been reported and hence, movement during nightfall is not recommended. Gambella UN curfew exists during 22:00 -06:00hr. Construction period shall consider the risk of project delay during the seasonal conflicts and the consequent restrictions of movement in the region.

- Sub-surface Condition: The site is predominantly covered top clays soil of 30-40 cm depth followed by weathered rock. No information regarding the availability of ground water. Most of the areas are covered by grass and there is no clear indication if there is a buried structure or not. On the other hand, all the proposed sites are surrounded by other facilities hence there might be buried utilities around especially along water lines. Hence special precautions and advise from ARRA need to be sought during excavation work of the new development on the sites. Pursuant to the Ethiopian Building Code Standard, the entire Gambella region is free of seismic hazard with zero ground motion.

- Climate: The climate of the Gambella Region is formed under the influence of the tropical monsoon from the Indian Ocean, which are characterized with high rainfall in the wet period from May to October and has little rainfall during the dry period from November to April. The mean annual temperature of the Region varies from 17.3 to 28.3 degree Celsius and annual monthly temperature varies throughout the year from 27 to 33 degrees Celsius. At higher altitudes it ranges from 1,900-2,100 mm. The annual evapo-transpiration in the Gambella reaches about 1,612 mm and the maximum value occurs in March and is about 212 mm. The region endowed with a vast marginal land which is suitable for agriculture and other economic activities. The existing land cover (vegetation) types of the region are identified as cultivated land, forest land, wood land, bush land, shrub land, grass land, bamboo, wet (marsh land), etc.

- Pugnido II Camp – OSS Center

- Location: The camp is located about 70 Km South of Gambella town at a distance of 13 km from UNHCR Pungido field office close to existing Pungido Agnuak and Pungido Nuer OSS sites. The proposed site is located exactly in front of Pungido II Refugee camp health center with geographical coordinates of 7.7055 N, 34.245528E. The closest town for the OSS centers is Pungido.

- Site: The site with an area of about 2,000 m2 is currently open land bounded by a gravel road to the East and South surrounded by farm land. There exist two small shops at one corner of the site. However, after a thorough discussion with ARRA and UNHCR representatives, it has been agreed to exclude these shops from the plot area instead of relocating them. Additionally, there exists a temporary generator room which is built from corrugated iron sheet, which is to be excluded from the plot.

Google Map: Pungindo-II

- The land has no formal land ownership title-deed but it was noted that it is government owned land managed by ARRA. This site topography appears generally flat and bare land with no coverage by grass, shrubs and trees.

- Urban Features: The neighborhood of the project site is characterized by farming area. The land and its vicinity has no historical, cultural and archeological significance. The land is surrounded by various facilities such as health center, food distribution building, a refugee shelter and other partner’s buildings. Besides, urban amenities such as Government, NGO offices Clinic, schools, banks, hotels, church and residences are found in the Pugnido town.

Site Topography – Pungindo -II

- Existing Infrastructure (Utilities and accessibility):  There are gravel roads within the town and also the camp connected to the main road through gravel roads. Internal gravel road exists within the camp. The road is sufficient enough to allow the passage of two cars at a time. The proposed OSS center is located near to the internal road that can serve to access the site during and after construction.

- The water supply of the camp is managed by IRC. IRC provides technical support to UN/NGO working in the camps upon request. There are three boreholes where ground water is being extracted from a depth of 110m. The discharge capacity varies from borehole to borehole. The range of discharge is between 10 to 12lit/sec. IRC distributes a treated and clean water to all the facilities. Six generators are installed and used by IRC for distribution of water. Elevated water tanks exist at different locations. There is a nearby elevated water which can be used for future supply water to the OSS center.

- No power grid system available at the camp and the OSS site. The only power source to be considered are Generator and/or Solar power.  The team realized during the visit that UNHCR is planning to provide power to the OSS via generator. However always recommended to use renewable energy such as PV solar power or wind.

- No storm water drainage system for the site and its surrounding. Surface water from the upstream, rainwater from the roof of the building and the site premises shall be collected and channeled to the adjacent grave road.

- No ICT cabling to the site. Recommended to consider connection of the site with fiber cabling from the offices.

- Neighborhood character: Conflicts between the two major communities i.e. Angwake and Nuer usually occur. However, at the time of assessment, no conflict in Gambella town has been noticed and the security situation of the camps is peaceful. Robbery has been reported and hence, movement during nightfall is not recommended. Gambella UN curfew exists during 22:00 -06:00hr. Construction period shall consider the risk of project delay during the seasonal conflicts and the consequent restrictions of movement in the region.

- Sub-surface Condition:  The formation of the soil is similar appears composed of black cotton soil at the top layer to a depth of 50 cm -100cm and followed by weathered rock as the second layer. The weathered rock is found at reasonable depth for use as foundation layer for the buildings. No ground water at shallow depth. It is evident from the information of the existing boreholes that the ground water table is found at an average depth of 110m. There is no significant surface and subsurface features which affects safety of the building, however it was noticed that water distribution pipes are buried at different location by IRC to supply water for the different facilities from reservoir. The proposed OSS center is not yet connected to water supply line. Pursuant to the Ethiopian Building Code Standard, the entire Gambella region is free of seismic hazard with zero ground motion.

- ACCESS AND ACCESS RESTRICTIONS

- Okugu Site: The main road from Dimma town to Okugu camp is asphalt road. The proposed land is located at a close proximity to the main asphalt road and is accessed through gravel road which branches from the main asphalt road that stretches from Dima town to Ethio-South Sudan boarder.

- Jewi Site: The main road from Gambella town to Jewi is asphalt road with internal roads to and within the camp made of gravel roads. The proposed site is located immediately after the internal road. Hence no problem of accessing the site during and after construction.

- Pungindo-II: There are gravel roads within the town and also the camp connected to the main road through gravel roads. Internal gravel road exists within the camp. The road is sufficient enough to allow the passage of two cars at a time. The proposed OSS center is located near to the internal road that can serve to access the site during and after construction.

- No access restriction to the site. However, the sites and their surroundings are managed by ARRA (Agency for Refugees and Returnees Affairs. Although there exists no significant concern in accessing the site, ARRA has stringent security requirement to be examined and considered prior to accessing the site. UNOPS and UNHCR will be continually in contact with ARRA and support the Contractor in securing timely access permit to the site.

- OTHER SITES

The sites for the rehabilitation of the OSS centers are located within the respective refugee Camps under the possession of UNHCR Sub-offices and ARRA. The sites will be readily handed over without any restrictions to the Contractor upon mobilization to the site.

- CONTRACTOR'S SITE FACILITIES

''Location of Contractor's Site Facilities to be discussed and agreed upon during mobilization period''.

- SITE VISIT / INSPECTION

UNOPS Ethiopia Office WILL NOT conduct group site visit. However, prospect Bidders/Contractors are highly encouraged to visit the sites by their own before submitting the bid. Hence site visit is not a compulsory requirement for evaluation.

- ABBREVIATIONS

The following abbreviations have been used in the Bills of Quantities:

For example:

| Abb. | Descriptions |
| --- | --- |
| kg | kilogram |
| t | tonne |
| m | meter |
| m2 | square meter |
| m3 | cubic meter |
| mm | millimeter |
| Nr. | Number |
| ETB | Ethiopian Birr |
| uPVC | un-plasticized poly vinyl chloride |
| HDPE | high density polyethylene |
| GMS | galvanized mild steel |
| LS | Lump Sum |
| PS | Provisional Sum |