## Design info (project team)
Project name:
Project number:
Country:
Project manager:
Design specific information:
Description of works:
Applicable codes/standards:
Design engineer of record:
Design organization:
Construction cost:
Planned procurement date:
Documentation checklist: | Design brief | Concept design | Final design
| Scope of works: | Codes/standards: | Design report:
| Site information: | Design report: | Structural report:
| Geotechnical survey: | Concept drawings: | Structural calculations:
| Feasibility studies: | Outline proposals for structure/services: | Specifications:
| Budget: |  | Schedules:
|  | Outine specifications: | Bill of Quantitites:
Constructible drawings, buildings:
Architectural
Structural
MEP
Insert any relevant notes here.

## Buildings
DESIGN REVIEW CHECKLIST FOR BUILDINGS |  |  |  |  | Project ID (OneUNOPS): | 00000
The following checklist is provided to help review the safety, functionality, and sustainability of UNOPS infrastructure projects. It is derived from the protocols, objectives and requirements provided in the UNOPS Infrastructure Design Planning Manual for Buildings, which lays out the minimum requirements for UNOPS building infrastructure. For design reviewers: This checklist provides a convenient tool by which to assess the design against the minimum requirements of the Design Planning Manual for Buildings. It is to be used in conjunction with the DP Manual. However, the reviewer's responsibility to ensure that the proposed design meets the spirit and intent of the DP Manual extends beyond the strict limits of this checklist. Additionally, when aspects of the proposed design do not meet the minimum requirements, it is not sufficient to merely observe a failure to comply. Whenever possible, the reviewer should provide guidance or suggestions on how to address the issue in an appropriate way. |  |  |  |  | Project name:
Project manager:
Basic project information:
For project managers and design practitioners: For each required item, you will find a color-coded response in the comments box: • Comments marked green meet the minimum requirements of the Design Planning Manual, or these requirements have been deemed not applicable for the proposed infrastructure/project. • Comments marked orange require your attention to meet the specified requirements (or provide additional information as to how the requirement was met). • Comments marked light green have been provisionally accepted but require further consideration or documentation. |  |  |  |  | Insert general comments here. Please mark your initials and the date of the comment.
Code | Protocol | Clause | Approval (drop-down) | Comments INSERT DATE. MARK YOUR INITIALS.
SECTION C: TECHNICAL OBJECTIVES, FUNCTIONAL STATEMENTS AND PERFORMANCE REQUIREMENTS
Site (C1)
C1.PR 1 | Rights of Way/ Rights of Use | The DP MUST investigate existing Rights of Way, both formal and informal, where these cross all or part of the Site. Positions of such rights of way and rights of use MUST be marked on the topographic survey drawings, and positions pegged on site.
C1.PR 2 | Displacement of People | Displacement could occur as a result of people living on the site, or people using the site to earn their living, e.g. growing crops, grazing livestock. Where relevant, DPs MUST consider design solutions that enable continued use of the site.
C1.PR 3 | Bio-Diversity | DPs MUST make enquiries with relevant authorities such as national or international conservation bodies regarding the likelihood of any significant bio-diversity issues arising as a result of the infrastructure project, unless this process has been completed as part of an environmental assessment. Should investigations show that bio-diversity issues exist, the DP MUST report this to the PM, so that UNOPS can bring the issue to the Direct Partner / Donor / Government / national conservation bodies, preferably before any major design work is carried out.
C1.PR 4 | Cultural Heritage | DPs MUST enquire into the possibility that any buildings on the site could be of cultural or historical significance. Should investigations show that cultural heritage issues exist, DPs MUST report this to the PM, so that UNOPS can bring the issue to the Direct Partner / Donor / Government before any major design work is carried out. Should the government have any requirements regarding steps to be taken to protect culturally sensitive buildings or areas, such steps should be clearly stated in the approval documents from the government. The DP MUST ensure these are clearly identified and adhered to in the design documents.
C1.PR 5 | Archaeological Significance | a. DPs MUST enquire into the possibility that the Site is situated on land which could be of archaeological significance, as well as research the subject on internet sites or any other relevant information sources. b. Should investigations show that the Site is on land of any archaeological significance, DPs MUST report this to the PM, so that UNOPS can bring the issue to the Direct Partner / Donor / Government before any major design work is carried out.
C1.PR 6 | Site Environmental Assessment | The PM, with the assistance of the DP, MUST identify any problems with the site and should allow for this in construction estimates. The DP MUST verify with the UNOPS PM whether any specific environmental remediation or control measures are required in the design documentation.
C1.PR 7 | Site Infrastructure Services | DPs MUST consider the following in the initial planning phase: a. Any adverse impact on the site or local populations resulting from the design, and any issues identified in the environmental assessment. b. The potential for positive site impacts resulting from the design.
C1.PR 8 | Demining | UNOPS often works in post conflict areas, where the presence of land mines and unexploded ordinance is a very real danger. The DP MUST not enter the site area until a clearance certificate has been issued and approval for access provided by UNOPS. The DP MUST document any areas that are off limits for the contractor due to demining issues.
C1.PR 9 | Site Ownership | Where possible, the Direct Partner, Donor or Government MUST provide an official deed / document showing ownership, signed and stamped by the relevant authorities.
C1.PR 10 | Technical Surveys/ Reports | DPs MUST obtain all technical surveys necessary to complete the design of the infrastructure. This could include, but are not limited to, environmental assessments, topographical surveys, and geotechnical surveys.
C1.PR 11 | Site Clearing | The DP MUST identify the full extent of any site clearing in the documents, if it forms part of the construction contract. Any site clearing MUST comply with the previously identified requirements from C1.PR 3 to C1.PR 6.
C1.PR 12 | Demolition of Existing Structures | Building: The DP MUST identify the full extent of any demolition in the design documentation if it forms part of the construction contract. The DP MUST ensure that the demolition does not impact any other site infrastructure or adjacent infrastructure.
Materials: The PM, with the aid of the DP, MUST identify the ownership of the demolished materials and ensure it is included in the technical documentation. Consideration should be given to the disposal of construction waste in a social and environmentally responsible manner.
Equipment: If specific equipment is to be reused, the PM must ensure that ownership is determined. The DP MUST determine the suitability of the equipment before the design is completed.
C1.PR 13 | Vehicular access and car parking | The DP MUST check that: a. That vehicle parking is sufficient on the site or on adjacent areas next to site area for the likely volume and size of vehicles. b. The effect of transport to and from the new infrastructure on the existing road system, when positioning entries and egress to and from the site. This could be through application to local municipalities or transport authorities. c. Turning spaces, wheel loads, clearing heights and accessibility for heavy vehicles (e.g., fire engines, flatbed delivery trucks, containerised transport, buses) accessing the site and any required parking spaces.
C1.PR 14 | Accessible parking | a) Parking spaces for persons with disabilities MUST be provided in accordance with the table in the section.
b) For rehabilitation and outpatient facilities for physical therapy, 1 in 5 patient and visitor parking spaces MUST be provided to serve patients whose mobility is affected.
c) For residential facilities, parking spaces provided to serve the facilities MUST comply with the above table. Where at least one parking space is provided for each residential unit, at least one accessible parking space MUST be provided for each residential dwelling unit required to provide mobility features.
Materials Selection (C2)
C2.PR 1 | Fitness for purpose | The choice of building elements and materials MUST take into consideration that the materials fi the requirements as defined in C2.PR2 to C2.PR4.
C2.PR 2 | Local sources | All selection of building materials MUST be carried out on the basis of professional judgement of choices between locally available systems and materials, and systems that require either importation or the establishment or enhancement of a manufacturing facility
C2.PR 3 | Life cycle | Other than the services and equipment, building elements MUST be envisaged to have the required lifetime for the infrastructure project, an acceptable life cycle cost, and which can be recycled safely at the end of their useful life, where feasible.
C2.PR 4 | Hazardous elements and materials | Elements and materials with known hazardous content MUST not be used. Appropriate precautionary measures are required for materials that may be hazardous only during construction activities.
C2.PR 9 | Termite treatment | Termite treatment MUST be specified in any zone that is infested with termites. The treatment is to be carried out during construction and must carry a guarantee of a minimum of ten years.
C2.PR 10 | Insulation | The DP MUST carefully consider insulation, both thermal and acoustic, even in environments where local practice is to not insulate the building.
C2.PR 11 | Fire resistance | Fire resistance MUST be considered with reference to SECTION C4, including the contribution of materials to the spread of fire. Fire doors, walls and stops MUST be incorporated in the design where appropriate.
Structure (C3)
C3.PR 1 | Codes | As per SECTION B2, the DP MUST comply with national or international design codes appropriate to the country in which the structure is built. As a rule, codes are prescriptive and must be researched carefully. The DP will assess the national and UNOPS requirements and apply the stricter standard. Likewise, if no national code is in place, the DP will apply the relevant functional statements, technical parameters and performance recommendations & requirements indicated in this manual.
C3.PR 2 | Progressive collapse | The structure MUST be designed so that if structural damage or failure occurs it will do so in such a way that time is allowed for occupants to evacuate the building prior to total collapse.
C3.PR 3 | Earthquake design | Structural design for earthquake zones MUST be undertaken only by professional structural engineers with specialist experience. Establishing the seismic design parameters is a critical part of the designer's task and all information MUST be obtained from national codes, seismic maps and worldwide sources. When choosing a structural system the designer, both engineer and architect, MUST give consideration to all the strengths and weaknesses of different construction methods and especially pay attention to connection detailing and their ability to withstand seismic action. The designer MUST also give consideration to the use of energy absorbing design features, which are not costly when measured against the life-cycle cost of a building.
C3.PR 4 | Deflections and deformations | The DP MUST check the design for deflections and deformations and ensure not only that the fluctuations are permitted within the relevant standard, but also that such deflections and deformations do not cause damage to other parts of the building or to installed equipment and fittings.
C3.PR 5 | Neighbouring buildings | The DP MUST investigate the potential for neighboring buildings and structures to be affected by the infrastructure works and any negative effects MUST be eliminated or mitigated.
C3.PR 6 | Calculations | In preparing the design calculations, the DP MUST use internationally recognized structural design software or, if working manually, prepare neat and proper records of the design calculations. The design record MUST be made available for third party reviews and checks at any time and MUST be handed over as part of the end users Taking-Over package along with as-built drawings. Design revisions and changes carried out during construction MUST be incorporated in the final design record.
C3.PR 8 | Foundations | When designing foundations, careful analysis of the Geotechnical Investigation is required and all factors such as soil type and soil bearing capacity, water table, and potential for ground movement MUST be taken into consideration by the DP. The history of the site must be investigated, especially to discover if the site is filled and a cut and fill platform exists in the location proposed for the building.
C3.PR 10 | Construction details | The structural engineer and the architect together MUST design details that not only meet the structural requirements but are also not too complex. The local skill level and expected quality achievable MUST be considered so the construction details can be executed without compromising the design intent and can be supervised on site by the site engineer.
C3.PR 11 | Existing buildings | In cases where an existing building is converted and/or renovated, the load bearing structure MUST be subjected to a detailed investigation.
Fire safety (C4)
C4.PR 1 | Structural integrity | All buildings MUST be designed so that their structural integrity is maintained during a fire to permit the evacuation of occupants and provide limited protection of firefighting personnel. For further guidelines and specific parameters stemming from this requirement, please see the relevant section.
C4.PR 2 | Evacuation and escape | All buildings MUST comply with the following requirements for evacuation and escape in the event of a fire. For further guidelines and specific parameters stemming from this requirement, please see the relevant section.
| a. Travel distance | A clearly marked exit door to the outside of the building or a stairwell from upper floors with a maximum travel distance of 40m from the furthest point on the floor
| b. Signage visibility | The exit sign is to be visible from within the corridor. Signage to be provided for guidance in corridors where the exit door is obscured from view.
| c. Exits Number | The minimum number of exits points per floor to be two (2) locations, widely separated to provide alternative escape points. Buildings occupied by more than 500 people per floor require 3 exits and more than 1,000 people per floor require 4 exits. Exception: Small buildings that are less than 100m2 and 20 occupants per floor, for a maximum two story building, may have one exit location
| d. Exits opening direction | A designated exit door is to be provided in all rooms that may be occupied by more than 20 people and must open in the direction of exit path.
| e. Exit door width | All exit door widths (or multiple door assemblies such as double swing doors) must be suitable for the expected numbers of people. The minimum clear width of a designated exit door is 900mm inside the frame.
| f. Width of corridors and stairs | All staircase and corridor widths must be suitable for the expected numbers of people. The minimum clear width of a corridor is 1,500mm and staircase is 1,200mm between wall faces. The projection of any doors into the clear width is not permitted. Exception: The only exception to the requirement for stair width is that stairs serving less than 50 occupants may be 900mm between wall faces.
| g. Dead ends | Dead end corridors must be no more than 6m in length where they branch off from the main egress corridor.
| h. Fire isolated stairs | Where a building contains more than 3 upper floors, one of the exit stairs MUST be a fire isolated stair.
| i. Emergency lighting | All buildings MUST have emergency lighting with battery backup to ensure safe evacuation in the event of power failure, including lit exit lighting and other emergency fixtures located in strategic points in the travel path to the exit.
C4.PR 3 | Fire exits | The number of fire exits required for each building is dependent on the numbers of people in the facility based on the floor area. The table in this section MUST be used for guidance in calculation of the maximum number of occupants within a building. See Table 3 for maximum number of occupants specifications.
C4.PR 5 | Smoke and Fire Seperation | All buildings MUST comply with a number of requirements for smoke and fire separation, laid out in the relevant section.
| a. Smoke separation | Smoke separation is to be achieved with a smoke resistant barrier that completely separates different areas inclusive of ceiling void spaces. See relevant section for zoning and area specificaions.
| b. Internal fire separation | Fire separation is to be achieved, at a minimum, with a 2 hour fire rated barrier that completely separates different areas. No windows are permitted in the fire wall except for certified fire rated window assemblies. See relevant section for building constraints specifications.
| c. Fire separation on the same Property | All new buildings should be separated from existing buildings on the same site See relevant section for seperation specifications. Exception: Where the new building is an extension or modification to an existing building, the separation of buildings does not apply.
| d. Fire separation from adjoining property | Fire separation between the new building and the side or back boundary of the property shall be a minimum of 2.5m for a single story building and 1.0m more of setback for each additional story, where the wall of the new building contains windows facing the boundary. See relevant section for boundary setbacks specifications.
C4.PR 6 | C4.PR 6 Fire detection and protection systems | All buildings MUST comply with a number of requirements for fire detection and protection systems, laid out in the relevant section.
| a. Alarms and detectors | Fire detection systems are required for all buildings greater than 300m2. The systems shall be smoke detectors permanently wired to an audible alarm. Thermal detectors are required to locations such as kitchens where smoke alarms may not be appropriate. If a wired system is not technically feasible, battery-powered detectors with individual alarm capacity shall be used.
| b. Zonal controls | Zonal controls are needed in all buildings greater than 1,000m2 in area. Fire indicator panels (FIPs) should be installed in the facilities that contain multiple detection zones. These will be located in readily accessible locations to assist with the firefighting response. If a connection to municipal fire brigade facilities is feasible, this is required for all buildings greater than 3,000m2 in area
| c. Fire extinguishers | Portable fire extinguishers are required for all buildings as a first response method for a developing fire. These shall be located by the DP on building floor plans. The maximum floor area per extinguisher is 500m2. The maximum travel distance between extinguishers is 45m or 23m, if the building contains a single extinguisher.
| d. Fire hose reels and standpipes | If a hose reel and standpipe system is not technically feasible either due to insufficient water supply, electrical supply for fire pumps, or other factors caused by the remote location of the site or other factors, alternate risk mitigation techniques MUST be provided. See relevant section for possible mitigation techniques.
| e. Fire sprinkler systems | In locations where sprinkler systems are feasible, there are normally existing regulatory frameworks that govern their use and these MUST have precedence in this instance as per the protocol in SECTION B. If a sprinkler system is required, then the DP should seek expert guidance on its design and installation on a ‘one-off’ basis.
C4.PR 7 | Signage | The DP MUST specify signage to be included in the design documentation. In all buildings greater than 300m2 of total floor area, signage MUST be provided in the local language to clearly identify all locations of fire extinguishers, hose reels, stand pipes adjacent to the equipment. Each floor of a building MUST be displayed on a plan mounted on a wall near the entrance to each floor. See relevant section for the information to be identified.
C4.PR 8 | Locks on exit points | All exit points, escape corridors, escape doors, MUST not be lockable in the direction of escape. Door hardware schedules must comply with this requirement.
C4.PR 9 | Emergency equipment | To ensure that emergency equipment is available for use at all times, access doors to hose reels or extinguisher cabinets MUST not be locked. If in the open, controls on the equipment MUST not be locked.
C4.PR 10 | Inflammable liquids | All buildings that contain, or propose to contain, significant volumes of inflammable liquids, such as petroleum, oil or paint products, MUST have special provisions for storage. These provisions are laid out in the relevant section.
| b. | Between 0.3m3 and 1.5m3 of material, the room shall be fire isolated from adjoining spaces with a minimum of 1 hour fire rated enclosure inclusive of door. The room may contain a window to the exterior of the building and have high and low level vents to the exterior.
| c. | Between 1.5m3 and 5.0m3 of material, the room shall be fire isolated from adjoining spaces with a minimum of 2 hour fire rated enclosure inclusive of door. The floor MUST contain a bund to ensure retention of contents in the event of leakage or a drum failure. The room MUST not have a window and MUST have high and low level vents to the exterior.
| d. | More than 5.0m3 of material, the room MUST be separate from the building located a minimum of 6m from the nearest habitable building. Construction as per c) alternative above. Where buildings such as warehouses contain significant volumes of inflammable goods or liquids, these MUST be designed to limit the potential spread of fire, contain any liquids, and have acceptable firefighting capacity.
| e. | Spark proof switches, lights, ventilation fans (if used) are required for all storage capacities greater than 0.3m3. All storage shelving should be spark resistant such as concrete or timber rather than steel shelving.
C4.PR 11 | Firefighting services | In those locations where externally provided governmental, municipal or city-based firefighting services exist, these MUST be consulted for confirmation of all fire protection measures and requirements for firefighting vehicle access; specific hydrant locations, sizes and capacities; FIP locations; and external communication link for detection alarm notifications.
Access and egress (C5)
C5.PR 1 | Circulation space | Each building MUST be designed to: a. Allow movement into and out of the building in a safe and unobstructed manner during normal use. The primary point of access MUST be clearly defined to enable simple access with signage or non-written visual means depending on the design circumstances. b. Have sufficient circulation space within the building to enable its intended function in an efficient and smooth manner. For further guidelines and specific parameters stemming from this requirement, please see the relevant section.
C5.PR 2 | External steps | External steps leading to the entry/exit point of buildings MUST comply with all of the requirements specified in the section.
| a. Capacity | Must provide capacity greater than the expected number of persons that may use them during a fire or emergency event.
| b. Step depth | Must be consistent in step depth and riser for the full length and height.
| c. Riser height | The maximum riser height is 180mm. Minimum riser height is 100mm. Minimum tread is 280mm.
| d. Slip hazard | The potential slip hazard on tread surface in wet, icy or snowy conditions must be considered in material selection.
| e. Thread marking | The marking of the tread nosing in a different colour or texture to assist sight-impaired people must be considered.
| f. Handrails width | Handrails must be provided to one side of the stair when the width is less than 1,500mm; handrails must be provided on each side of the stairs where stair width is between 1,500mm and 3,000mm wide; if the stair width is greater than 3,000mm wide, intermediate handrails must be provided to the stair to assist safe movement. The clear distance of the handrail from the wall or obstruction is to be between 50-75mm.
| g. Handrails location | Handrails to be well secured and able to withstand all normal usage forces without obvious deflection, located 865mm-965mm to top of rail above step height.
| h. Landings | Landings every 12 risers with a minimum length of 1,200mm between stairs EXCEPT if the external stair is a steel fire escape stair, it should comply with C5.PR 3.
C5.PR 3 | Internal steps | Internal stairways within buildings MUST comply with all of the requirements specified in the section.
| a. Width | Must not be less than the minimum widths for escape as noted in SECTION C4.PR 3.
| b. Step depth | Must be consistent in step depth and riser for the full length and height.
| c. Riser height | The maximum riser height is 180mm. Minimum riser height is 100mm. Minimum tread is 280mm.
| d. Slip hazard | The potential slip hazard on tread surface in wet, icy or snowy conditions must be considered.
| e. Handrails width | Hand rails must be provided to each side of the stairs where width is less than 2,400mm wide. If the width is greater than 2,400mm wide, intermediate hand rails must be provided to assist safe movement. The clear distance of the handrail from the wall or obstruction is to be between 50-75mm.
| f. Handrails location | Hand rails are to be well secured and able to withstand all normal usage forces without obvious deflection, located 865mm-965mm to top of rail above stair height.
| g. Landings | Landings every 16 risers with a minimum length of 1,200mm between stairs.
C5.PR 4 | Balustrade | Balustrade panels to balconies used as primary access MUST not be less than 1,000mm in height from floor level of balcony to top of panel. The infill between 150mm above floor level to 750mm above floor level MUST be either solid material or vertical bar, making it un-climbable for small children. Bar spacing to be maximum of 150mm centers. Balustrade panels below handrails to external stairs and internal stairs MUST contain infill as above.
C5.PR 5 | Ramps | Ramps MUST be provided for access to the main entrance/exit of a building for disabled persons, deliveries of goods, etc. Ramps MUST be used wherever possible inside the building to facilitate access to all parts of the building. For further guidelines and specific parameters stemming from this requirement, please see the relevant section.
| a. | Ensure that inaccessible services or building functional spaces that may be used by disabled persons are on the ground floor, or duplicated on the ground floor.
| b. | Ensure that toilet facilities are located in an accessible location.
| 1 | Minimum width of 915mm between handrails.
| 2 | Maximum slope of 1:12, or 8.3%.
| 3 | Horizontal landings at maximum of 8m length of ramp with landing a minimum of 1,525mm in length.
| 4 | Handrails to ramp sides at 865mm-965mm to top of rail above ramp.
| 5 | Threshold ramps where used for maximum of a single 150mm rise may have a steeper slope of maximum 1:8.
| 6 | Ramp surface finish must be considered for potential slip/slide hazard in wet, icy or snowy conditions.
C5.PR 6 | Door openings | Accessibility at door openings is critical for the effective access of wheelchairs. The design of all spaces which have wheelchair access MUST comply with the space requirements laid out in the section.
C5.PR 7 | Gender equality | Cultural and social norms regarding gender equality and access differ in the countries where UNOPS provides building infrastructure. The Design Solution MUST demonstrate that cultural and social norms have been considered while ensuring that women and men have equal access to public facilities.
C5.PR 8 | Equipment access | Equipment access for service, repair and replacement if necessary, has implications for circulation space, door opening widths, and general access to the building and roof. The DP MUST consider this aspect in the development of the design.
Health and amenity (C6)
C6.PR 1 | Lighting | Lighting for each building MUST comply with the requirements laid out in the relevant section.
| a. Daylight | Use daylight as a primary means of lighting in all habitable rooms during daylight hours, unless security, privacy or other technical reasons preclude it.
| b. Glazing impact | Consider the climatic conditions, orientation, size, insulation and shading of windows to limit the negative impacts of glazing. Whether it is climatically or culturally appropriate is a broad subject with many views, however the DP MUST consider the glazing solution for any building to avoid significant heating and/or cooling issues which may affect both the health of occupants and service costs for the building.
| c. Daylight penetration | Consider the maximum effective depth of daylight penetration into a building. A typical indication of maximum effective depth is 6-9m from the external wall. Please see factors to be considered in the relevant section.
| d. Artificial lighting | Consider the extent of supplementary artificial lighting for all internal rooms, or spaces unable to be lit by daylight. The level of artificial lighting shall be sufficient to enable the effective functional use of the room or space.
C6.PR 2 | Ventilation | Ventilation for each building MUST comply with the requirements laid out in the relevant section.
| a. Natural Ventilation | The minimum openable window area to the outdoors shall be 5% of the floor area in a room.In locations where adjoining rooms without openings to the outdoors use ‘borrowed’ ventilation from a naturally ventilated room the common wall shall have an opening of a minimum of 10% of the unventilated room floor area.
| b. Mechanical ventilation | In cold climates, where temperatures are lower than 5°C, ensure that all rooms containing bathtubs, showers, spas and other bathing facilities shall be mechanically ventilated.
| c. Cross ventilation | Enable cross ventilation where feasible and appropriate. This is particularly relevant in hot or humid climatic conditions and should be achieved with nominally equal areas of openable ventilation on opposite walls of the room or space.
| d. Other measures | Consideration should be given to other methods for natural ventilation such as stack or chimney design techniques to boost the impact of natural ventilation techniques where required.
C6.PR 3 | Concealed spaces | Every building that contains concealed sub floor spaces, attic spaces or voids within wall cavities MUST be designed to inhibit or eliminate moisture migration or condensation issues, in line with the requirements laid out in the relevant section.
| a. Temperature and dew points | Temperature variations and dew point locations relative to chosen building elements shall be assessed to avoid condensation in building cavities.
| b. Roof void space ventilation | Roof void space ventilation is to be implemented by openings at the bottom and top of sloped roofs to ensure convection air movement. All ventilation air movement MUST be located on the outer face of insulation to ensure the effectiveness of the insulation is not compromised.
| c. Sub-floor ventilation | Sub floor ventilation is required to be installed for voids between the underside of timber floor structures and the earth below. The vents shall be vermin proofed to prevent access into the crawl space and have an area of 0.7m2 per 100m2 of floor space. Minimum clearance for timber above ground is 300mm.
C6.PR 4 | Mechanical ventilation | Buildings or parts of buildings that require mechanical ventilation for exhaust MUST comply with the requirements laid out in the relevant section.
| a. Mechanical exhaust Rates | 1. Two air changes/hour for internal rooms or store rooms 2. Five air changes/hour for bathing facilities, domestic style kitchens and cleaners’ rooms 3. Specific trade related exhaust requirements to be commensurate with acceptable levels prescribed for use by local authorities or bodies such as WHO.
| b. Mechanical Exhaust Systems | Mechanical exhaust systems shall not discharge into roof void spaces or ceiling spaces. All exhaust shall discharge to the outdoors.
C6.PR 5 | Space heating | All habitable spaces within buildings MUST be provided with an acceptable method of space heating in cold climates. e heating system MUST be capable of sustaining a minimum temperature of 15 degrees C and preferably 18 degrees C at any location within the heated space during normal occupancy periods. The DP designing the spaces and building MUST consider the impact of extreme cold and provide insulation, air locks and other heat management design activities to minimize heat loss and fuel usage. All pipe work, tanks, valves, and other liquid-based circulation systems MUST be insulated and located appropriately to avoid freezing conditions.
C6.PR 6 | Air conditioning | Given the variability of conditions that affect power considerations, types of equipment, and spare parts availability, the DP should prepare a design solution that provides human comfort conditions within the provided matrix. Where there are opportunities to consider alternatives to full air conditioning, or reducing equipment size by improvements to the building design or its insulation, the DP MUST investigate these options prior to finalizing the design solution.
C6.PR 7 | Washroom facilities | The DP MUST ensure that adequate toilets, washing and bathing facilities areas are provided in all buildings or adjacent to the buildings, depending on cultural expectations, and employing a gender-based approach. For a table of minimum requirements for adequate washroom facilities, please refer to the table in the relevant section.
C6.PR 8 | Accessible toilets | The DP MUST provide at least one accessible toilet facility for persons with disabilities in all buildings. For further guidelines and specific parameters stemming from this requirement, please see the relevant section.
C6.PR 9 | Accessible kitchens | All dwelling units that are configured for accessibility for disabled persons MUST contain a kitchen facility suitable for use by a person in a wheelchair. Reach and clearance spaces, under bench knee spaces and similar operational constraints MUST be considered by the DP in the design of these facilities.
C6.PR 10 | Cleaners' sinks | Cleaners’ sinks MUST be used to ensure there are suitable facilities available for keeping the building clean and hygienic.
C6.PR 11 | Kitchen facilities | Tea-making facilities or kitchens MUST be separate rooms and contain sufficient cupboards, sink ventilation and water supply to enable the hygienic preparation of drinks and food appropriate to cultural norms. Cleaners’ rooms MUST not be used for tea-making or food preparation.
C6.PR 12 | First aid facilities | First Aid facilities should be considered for all buildings in the interests of emergency assistance for the occupants. If the building is located in a conflict zone, then the provision of a ‘sick’ room as an emergency first aid room MUST be included for all buildings with an area greater than 300m².
Services and Equipment (C7)
C7.PR 1 | Water supply system
| a. | The water supply system MUST deliver water which is safe for human consumption and other uses. Laboratory analysis and a treatment regime may be required to achieve the standard for safe drinking water as defined by WHO. Toilet flushing and similar non-drinking water applications may use lower qualities of water supply.
| b. | The DP MUST research all water supply options including rain water harvesting.
| c. | Water storage requirements MUST be determined on the basis of data collected about reliability of supply and estimated daily consumption.
| d. | Water requirements for fire fighting MUST be determined and a separate storage provided if the municipal supply is inadequate and/or intermittent.
| e. | Cold water reticulation MUST be designed so that adequate supply – a minimum of 5 l/min - is available at all discharge points. The possibility of frost damage MUST be considered and precautions taken to avoid frost damage.
| f. | Hot water reticulation: the same observations apply as for cold water, but insulation is required to avoid heat loss.
| g. | The design of the water heating and pipe system MUST be such as to prevent incubation of bacteria colonies, legionella in particular.
| h. | The method of heating water, both for sanitary purposes and for heating MUST be considered carefully by the designer. Centralised heating MUST be compared with de-centralised heating in terms of initial cost and operating cost.
C7.PR 2 | Sewage and waste water
| a. | Sewage and waste water potentially presents the most serious threat to health in any project. The DP MUST consider all available technologies to determine the most environmentally sustainable option given the particular context for the project.
| b. | Waste water from kitchens MUST pass through a grease trap before being discharged into the general waste water system.
| c. | Sewage systems, collection pipe work, manholes and treatment facilities MUST be designed with great attention to detail to ensure that any potential health hazard is mitigated. In particular possible groundwater contamination and infiltration into drinking water sources must be avoided.
| d. | Neutralising tanks and plaster traps MUST be considered for waste systems for health clinics and hospitals and only deselected with good reason. Additionally, disposal systems for medical waste MUST be considered to ensure that any potential health hazard is mitigated.
| e. | The DP MUST confirm the capacity of the municipal system with the relevant authority.
C7.PR 3 | Stormwater management
| a. | Stormwater systems MUST be designed so that they safely dispose of stormwater without causing scour, flooding or contamination.
| b. | Water from roof drainage should, where practical, be harvested for use in the water supply to the infrastructure project or for site irrigation.
| c. | Water from hardened surfaces, parking and roads MUST be led through gross solid traps, silt and oil traps before either being stored for re-use in reservoirs or discharged safely into either a municipal stormwater drainage system or a waterway.
| d. | The storm drains MUST be designed for normal rainfall parameters determined from meteorological data. Design MUST be resilient against extreme situations to prevent serious failure.
C7.PR 4 | Electrical systems
| a. | All electrical installations MUST result in a high degree of life safety and building safety for the project. The lifespan of the project should be considered in the design of electric installations. In the case that no such codes exist, see section B3.
| b. | All earthing/grounding devices, including lightning rods, MUST be identified on electrical documentation, as incorrectly executed earthing may result in failure of safety devices and cause a fire and/or loss of life.
| c. | The designer MUST research the local situation of power generation and distribution and establish to the greatest extent possible the reliability and capacity of supply.
| f. | When choosing standby power diesel generators the following MUST be considered: availability of competent maintenance service; availability of spare parts; reliability of operation; fuel availability and consumption.
C7.PR 5 | Comms and IT Systems | The IT requirements for server rooms, patch panel locations, PABX units MUST be defined, in cooperation with the end-user, in order to enable an acceptable level of security, operation and capability for the facility.
C7.PR 6 | Security services | The DP MUST identify in the design brief and assist with provision of any specialist services infrastructure related to security needs for the operation of the building.
C7.PR 7 | Evidence of research | The DP MUST provide evidence of research in consideration of the choice of equipment to meet C7-TO 2 and C7-FS 2 for complex equipment design solutions. These choices are critical to the future performance and effectiveness of the design outcome.
| a. | Ventilation fans, filters, exhaust hoods, make up air supply systems
| b. | Heating equipment such as boilers, burners, duct heaters, radiant heat systems
| c. | Water pumps for distribution and/or pressurisation to sanitary facilities or for heating systems, fire hydrant/hose reel systems
| d. | Air conditioning systems comprising air, ground or water based split systems, packaged systems, conventional chiller/evaporator centralised systems, VRV and other technologically advanced systems
C7.PR 8 | Testing of equipment | In the design documentation, prior to the handover of the building to users, the DP MUST:
| a. | Clearly identify those items of equipment to be tested and commissioned.
| b. | Clearly identify the need for maintenance manuals for such equipment.
| c. | Clearly identify any necessary training of occupants in the use of the equipment.
Security (C8)
C8.PR 1 | Security levels | The DP MUST design security elements and systems that are appropriate to the level or type of threat that can be reasonably anticipated.
C8.PR 2 | Codes | National codes and standards MUST be used for the design of security elements where such codes and standards exist. In the absence of these, applicable international codes should be used. Refer to SECTION B2 for further guidance.
C8.PR 3 | UN Building and compounds | United Nations Department of Safety and Security MOSS (Minimum Operating Security Standards) and MORSS (Minimum Operating Residential Security Standards) MUST be used for the design of all infrastructure for all UN buildings and compounds.
C8.PR 4 | Atypical security considerations | Some atypical security considerations may apply for other types of buildings in exceptional circumstances, and these MUST be designed to an appropriate standard to mitigate the particular threat.
C8.PR 5 | Physical security | All three main components to physical security (delay, detection, and apprehension) are required for a functional security system. The DP MUST design all Delay, Detection and Apprehension and other physical aspects of security systems to meet the security requirement. Specialist consultants may be required for major projects, in which case the DP MUST liaise with the consultant to ensure all relevant content is provided in the design documentation.
C8.PR 6 | Design considerations | Issues that MUST be considered in the design will depend on the level of threat, which may include Blast film, window bars, bunkers and safe rooms, blast walls, etc. For further guidance and specific requirements that MUST be met under certain security circumstances, consult the relevant section.
C8.PR 7 | Access control | Access Control MUST be designed to prevent unauthorized access to the building or compound, and to intercept contraband (weapons, explosives, etc.), with the minimum impact to traffic flow through the access.
C8.PR 8 | Exit control | Exit control MUST be considered. Exit searches should focus on theft or unauthorised removal of vehicles, equipment, classified material, etc.
Green technology (C9)
C9.PR 1 | Design elements | Green technologies MUST be considered by the DP in different design elements, such as: site location planning; selection of environmentally preferable materials; minimize greenhouse gas emissions; minimize use of energy and supply with renewable sources; water use; sewage and graywater use; solid waste handling; indoor air quality, including thermal comfort, lighting quality and type of fitting; building commissioning, its operation and maintenance; and mitigation of greenhouse gases.
C9.PR 2 | Building orientation and shape | DPs MUST consider building orientation and shape to reduce energy consumption and promote natural light and ventilation whenever possible.
Climate change adaptation and disaster risk reduction (C10)
C10.PR 1 | Impact of natural hazards | The DP MUST consider principles and good practices in the design, thinking beyond codes and standards, to design infrastructure that reduces the impact that failure due to natural hazard could have for the use of infrastructure.
C10.PR 2 | Climate change | The DP MUST design the facility with recognition of the increased impacts of climate change. The DP MUSt identify all measures taken to consider these principles and practices in the design of infrastructure.
C10.PR 3 | Safe health facilities | When designing health facilities, Design Practitioner MUST incorporate specific measures for the services of the building to remain accessible and functional at maximum capacity and within the same infrastructure immediately following a natural disaster, in line with WHO’s “Hospitals safe from disasters’ programme”.
C10.PR 4 | Safe schools | When designing schools, the Design Practitioner MUST incorporate specific measures for the services of the building to remain accessible and functional at maximum capacity and within the same infrastructure immediately following a disaster, in line with the Guidance Notes on Safer School Construction developed by the Inter-Agency Network for Education in Emergencies and the Global Facility for Disaster Reduction and Recovery.

## Roads
DESIGN REVIEW CHECKLIST FOR ROADS |  |  |  |  | Project ID (OneUNOPS): | 00000
The following checklist is provided to help review the safety, functionality, and sustainability of UNOPS infrastructure projects. It is derived from the protocols, objectives and requirements provided in the UNOPS Infrastructure Design Planning Manual for Buildings, which lays out the minimum requirements for UNOPS building infrastructure. For design reviewers: This checklist provides a convenient tool by which to assess the design against the minimum requirements of the Design Planning Manual for Buildings. It is to be used in conjunction with the DP Manual. However, the reviewer's responsibility to ensure that the proposed design meets the spirit and intent of the DP Manual extends beyond the strict limits of this checklist. Additionally, when aspects of the proposed design do not meet the minimum requirements, it is not sufficient to merely observe a failure to comply. Whenever possible, the reviewer should provide guidance or suggestions on how to address the issue in an appropriate way. |  |  |  |  | Project name:
Project manager:
Basic project information:
For project managers and design practitioners: For each required item, you will find a color-coded response in the comments box: • Comments marked green meet the minimum requirements of the Design Planning Manual, or these requirements have been deemed not applicable for the proposed infrastructure/project. • Comments marked orange require your attention to meet the specified requirements (or provide additional information as to how the requirement was met). • Comments marked light green have been provisionally accepted but require further consideration or documentation. |  |  |  |  | Insert general comments here. Please mark your initials and the date of the comment.
Code | Protocol | Clause | Approval (drop-down) | Comments INSERT DATE. INSERT UNIQUE ID.
SECTION C: TECHNICAL OBJECTIVES, FUNCTIONAL STATEMENTS AND PERFORMANCE REQUIREMENTS
Site Considerations (C1)
C1.PR 1 | Rights of Way/ Rights of Use | The DP MUST investigate existing Rights of Way, both formal and informal, where these cross all or part of the Site. Positions of such rights of way and rights of use MUST be marked on the topographic survey drawings, and positions pegged on site.
C1.PR 2 | Displacement of People | Where relevant, DPs MUST consider design solutions that enable continued use of the site. If this is not possible, the PM should make recommendations to the government authorities so that affected people are allocated suitable replacement land and/or acceptable alternative compensation |  | `
C1.PR 3 | Bio-Diversity | DPs MUST make enquiries with relevant authorities such as national or international conservation bodies regarding the likelihood of any significant bio-diversity issues arising as a result of the infrastructure project, unless this process has been completed as part of an existing environmental assessment. Should site investigations show that bio-diversity issues exist, the DP MUST report this to the PM, so that UNOPS can bring the issue to the donor and other partners and stakeholders, including national conversation bodies, before any major design work is carried out.
C1.PR 4 | Cultural Heritage | Should investigations show that cultural heritage issues exist, DPs MUST report this to the PM, so that UNOPS can bring the issue to the Direct Partner / Donor / Government before any major design work is carried out. Should the government have any requirements regarding steps to be taken to protect culturally sensitive buildings or areas, such steps should be clearly stated in the approval documents from the government. The DP MUST ensure these are clearly identified and adhered to in the design documents.
C1.PR 5 | Archaeological Significance | Should investigations show that the Site is on land of any archaeological significance, DPs MUST report this to the PM, so that UNOPS can bring the issue to the Direct Partner / Donor / Government before any major design work is carried out. If any archaeological issues are not identified at an early stage, this could result in major delays and redesign costs.
C1.PR 6 | Site Environmental Assessment | The DP MUST verify with the UNOPS PM whether any specific environmental remediation or control measures are required in the design documentation The PM, with the assistance of the DP, MUST identify any problems with the site and should allow for this in construction estimates. Such issues should be brought to the attention of all stakeholders as early as possible, before any major design work is carried out. Costs of environmental remediation could be high, and could affect the time schedule.
C1.PR 7 | Seismic considerations | The DP MUST check earthquake risks and, wherever possible, design the road, bridge or other affected infrastructure to reduce the risks of failure during an earthquake event. Earthquake Density Maps can be downloaded from http://earthquake.usgs.gov/earthquakes/region.php.
C1.PR 8 | Climatic considerations | The DP MUST research and identify the most suitable climate information for use in the design of the infrastructure element.
C1.PR 9 | Demining | The DP and/or other design or survey related personnel MUST not enter the site area until a clearance certificate has been issued and approval for access provided by the PM. The DP MUST document any areas that are off limits for the contractor due to demining issues. The PM and DP must be aware that a demining certificate does not guarantee that a site is clear of all risk. If the design requires significant bulk excavation or deep trenches there may always be risks of finding further UXO. The DP MUST include statements and instructions in the specification regarding these potential risks.
C1.PR 10 | Site Ownership | Where possible, the Direct Partner, Donor or Government MUST provide an official deed / document showing ownership, signed and stamped by the relevant authorities. If possible, UNOPS should request to view the original of this document.
C1.PR 11 | Technical Surveys/ Reports | DPs MUST obtain all technical surveys necessary to complete the design of the infrastructure. This could include, but are not limited to, environmental assessments, topographical surveys, geotechnical surveys and rainfall and drainage report.
C1.PR 12 | Site Clearing | The DP MUST identify the full extent of any site clearing in the documents, if it forms part of the construction contract. Any site clearing MUST comply with the previously identified requirements from C1.PR 3 to C1.PR 6.
C1.PR 13 | Neighbouring buildings | The DP MUST investigate the potential for neighbouring buildings and structures to be affected by the infrastructure works and take steps to eliminate any negative impacts.
C1.PR 14 | Substancial relocation of materials | The PM, with the aid of the DP, MUST identify the full extent of any earthworks and establish plans for and responsibility for the earthworks. Any environmental issues arising from the earthworks MUST be documented and mitigated. The PM, with the aid of the DP, MUST identify the full extent of any demolition works and establish ownership and responsibility for the demolished materials. The DP MUST ensure that the demolition does not impact any other site infrastructure or adjacent infrastructure. If specific equipment is to be reused, the PM must ensure that ownership is determined. The DP MUST determine the suitability of the equipment before the design is completed.
C1.PR 15 | Site Remediation | The DP MUST specify the site remediation measures of all site areas, if necessary.
Materials Selection (C2)
C2.PR 1 | Fitness for purpose | The choice of building elements and materials MUST take into consideration that the materials fi the requirements as defined in C2.PR2 to C2.PR4.
C2.PR 2 | Local sources | All selection of building materials MUST be carried out on the basis of professional judgement of choices between locally available systems and materials, and systems that require either importation or the establishment or enhancement of a manufacturing facility
C2.PR 3 | Life cycle | Other than the services and equipment, building elements MUST be envisaged to have the required lifetime for the infrastructure project, an acceptable life cycle cost, and which can be recycled safely at the end of their useful life, where feasible.
C2.PR 4 | Hazardous elements and materials | Elements and materials with known hazardous content MUST not be used. Appropriate precautionary measures are required for materials that may be hazardous only during construction activities.
C2.PR 5 | Renewable materials | Preference may be given to elements with material content from renewable sources and lower embodied energy.
C2.PR 6 | Composites | Composite elements should not be used where avoidable, due to the difficulty in recycling such materials.
C2.PR 7 | Supplier social responsibility | Preference may be given to suppliers of building components or materials that have adopted a corporate social responsibility policy which adheres to the ten principles of the Global Compact[2] or are prepared to commence a programme of adopting such a policy into their corporate strategy.
C2.PR 8 | Cost and functionality | Unnecessarily expensive elements and materials should be avoided and the DP should research alternatives with lower cost where possible.
C2.PR 9 | Fire resistance | Fire resistance MUST be considered with reference to SECTION C4, including the contribution of materials to the spread of fire. Fire doors, walls and stops MUST be incorporated in the design where appropriate.
Temporary Works & Diversions (C3)
C3.PR 1 | Provision and review of temporary works | The PM MUST ensure that provisions for the design of temporary works are a contractual responsibility of the DP or, more often, the responsible contractor. Significant temporary works that have structural implications MUST be jointly reviewed by the PM, the DP, and IPMG.
C3.PR 2 | Codes | The design of temporary works MUST be carried out with recognized design codes, agreed in advance with relevant stakeholders.
C3.PR 3 | Localized failure | Temporary works MUST be designed in such a way that a local failure does not cause progressive failure of the whole structure. Sufficient time MUST be ensured for the evacuation of any workers so that no lives are lost.
C3.PR 4 | Earthquake design | Refer to C1.PR 8. Like permanent works, temporary works MUST be designed for earthquakes.
C3.PR 5 | Consideration of local circumstances | The design of temporary works MUST consider and incorporate life safety measures specific to the local circumstances.
C3.PR 6 | False work and form work | The temporary works design MUST include construction details of false work and form work.
C3.PR 7 | Structural steel elements | Structural steel elements, if used, MUST be sufficiently detailed to provide criteria of expected performance.
C3.PR 8 | Diversions | If relevant, diversions MUST be considered in the design of transport infrastructure and designed to minimize life safety risks.
Climate change and resilient infrastructure (C4)
C4.PR 1 | Impact of natural hazards | The DP MUST consider principles and good practices in the design, thinking beyond codes and standards, to design infrastructure that reduces the impact that failure due to natural hazard could have for the use of infrastructure. The DP must identify all measures taken to consider these principles and practices in the design of infrastructure.
C4.PR 2 | Climate change | The DP MUST design the facility with recognition of the increased impacts of climate change. The DP must identify all measures taken to consider these principles and practices in the design of infrastructure.
C4.PR 3 | Critical infrastructure | When designing any transport infrastructure, the DP MUST consider if such infrastructure is vital for the delivery of support and emergency aid in the case of a disaster.
C4.PR 4 | Earthquake design | If in a seismic zone, when choosing a structural system, the designer and engineer, MUST give consideration to the strengths and weaknesses of different construction methods. Special attention to connection detailing and design for seismic forces/accelerations is essential. The designer MUST also give consideration to the use of energy absorbing design features, which are less costly when measured against the life-cycle cost of a project.
SECTION D: SPECIFIC PERFORMANCE REQUIRIMENTS FOR ROADS
Preparatory Surveys (D1)
D1.PR 1 | Road Classification | The function and category of the road—trunk/arterial; primary/collector; secondary/distributor; tertiary/access; or other—MUST be identified and the implications incorporated in the design.
D1.PR 2 | Terrain classification | The terrain classification in the vicinity of the proposed road—flat, rolling, mountainous, escarpment, or other—MUST be identified and the implications for the road incorporated in the design.
D1.PR 3 | Drainage and water crossing survey | The DP MUST research and identify the drainage and water crossing issues to resolve in the design of the road.
D1.PR 4 | Borrow pit and/or quarry surveys | The DP MUST research and identify the source and volume of gravel required for the construction work as it may affect the proposed design of the road.
D1.PR 5 | Traffic surveys | The DP MUST use traffic surveys and projections of future traffic in the proposed design of the road.
D1.PR 6 | Load surveys | The DP MUST use load category surveys and projections of future traffic load in the proposed design of the road. A study of load categories should include: Axle loads of all heavy vehicles whether empty or loaded, Vehicle categories and Loading in each direction of the road.
Geotechnical Investigations (D2)
D2.PR 1 | Principal requirements for quality of road materials | The DP MUST consider the least intensive and most economical road material options available, consistent with other design requirements, for the design of the road pavement.
D2.PR 2 | Problem soils and materials | If confronted by liquefaction or low-strength soils, expansive soils such as black cotton soil, collapsible sands, dispersive sands, organic soils, or saline soils, the DP MUST consider the impact of these soils and their potential remediation methods in the design or rehabilitation of road infrastructure.
D2.PR 3 | Sub-grade moisture contect variation | The DP MUST consider the effective management of moisture of sub-grades in wet climates.
D2.PR 4 | Sub-grade design strength | The DP MUST consider the sub grade design strength in assessing the optimum pavement design solution.
D2.PR 5 | Side slope stabilization | The DP MUST consider side slope stability in the design of new roads and, where appropriate, assess and remediate existing conditions to ensure the safety of users in the design solution.
D2.PR 6 | Mountainous terrain design considerations | If relevant, the design solution MUST address the broad range of issues presented by road construction in mountainous areas.
Hydrological investigations and Flood Risk Assessments (D3)
D3.PR 1 | Rainfall | The DP MUST consider the impact of rainfall on the road and catchment zone for the design or upgrade of road infrastructure.
D3.PR 2 | Size and configuration of the catchment area | The DP MUST consider the size and configuration of the catchment zone to determine the maximum peak flow rate for the design or upgrade of road infrastructure.
D3.PR 3 | All-weather access | The DP MUST clarify the need for all weather access and design the road accordingly.
D3.PR 4 | Land use characteristics | The DP MUST consider the environmental impact on wetlands and the potential flooding impacts from wetlands in the design of a road.
D3.PR 5 | Maximum peak flow | The DP MUST identify the maximum peak flow rate and effective height of any flooding due to the potential flooding impacts on the design of the road.
D3.PR 6 | Flood return period | The DP MUST verify the flood return periods required for the road and associated infrastructure and use this data to inform the design of the road and drainage structures.
Pavement Design (D4)
D4.PR 1 | Pavement design process | The DP MUST develop the design of the road pavement in consideration of design standards, the function and lifetime of the road, traffic type, loads, and growth, construction materials, structural design, and cost analysis.
D4.PR 2 | Sub-grade strength of homogenous sections | The DP MUST consider the results of sub-grade strength tests and determine whether strengthening would benefit the design of the road pavement. Refer to Section D2. PR 5 for the process of establishing sub grade strength
D4.PR 3 | Road material testing | The DP MUST consider testing methods and determine suitable testing procedures to enable incorporation of test results in pavement design.
D4.PR 4 | Design traffic classification | The expected traffic load of the road MUST be determined and considered in the design of the pavement.
Geometric Design (D5)
D5.PR 1 | Traffic types and volume | The safety of all road users MUST be considered in the design process, taking into account foreseeable changes in traffic flows and loads and with recognition of the need to balance costs.
D5.PR 2 | Traffic speed | The DP MUST consider driver behaviour to establish acceptable design speed standards for use in development of the road design.
D5.PR 3 | Sight distance | The DP MUST consider sight distances in the design of the road and should adopt values with underlying assumptions that are most appropriate to the project.
D5.PR 4 | Topography | The DP MUST incorporate considerations of topography into the road design and adopt a fit-for-purpose solution with regard to the project context.
D5.PR 5 | Cross-sectional dimensions | The DP MUST clearly identify the cross-sectional dimensions and all associated impacts on the geometric design.
D5.PR 6 | Vertical alignment | The DP MUST determine the design parameter values that are most suited to the local terrain and road function.
D5.PR 7 | Horizontal alignment | The DP MUST determine which of the design parameter values are most suited to the local terrain and road function.
D5.PR 8 | Parking facilities, lay-bys, and passing lanes | The DP MUST consider the integration of safe parking and overtaking lanes in consultation with the needs of local inhabitants, traffic conditions and road function.
Drainage Design (D6)
D6.PR 1 | Selection of drainage structure | The DP MUST consider the type, size, complexity and various elements of drainage structures (in combination with vehicle loads) to avoid significant damage to or structural failure of the road infrastructure.
D6.PR 2 | Social and economic dimensions of drainage | The DP MUST consider the optimisation of benefits in the design of drainage structures to leverage both economic and social dimensions for the road infrastructure.
Road Safety (D7)
D7.PR 1 | Road markings and road signs | The DP MUST identify and integrate a range of signs and road markings consistent with the needs of local conditions and the road function.
D7.PR 2 | Intersection safety | The DP MUST consider the design implications of multiple traffic flows at intersections and the possible options to reduce crash severity, such as the use of roundabouts.
D7.PR 3 | Roadside furniture | The DP MUST consider the safety of road users and pedestrians with any roadside obstacles and in the design of roadside furniture and its placement.

## Sheet3 (hidden)
Drop down options
Accepted
Not compliant
Provisionally Accepted
N/A

## Sheet2 (hidden)
Drop down options
Yes
N/A