## Feuil1
Projet d'Appui à l'Office National de la Famille et de la Population pour la Gestion d'une Subvention du Global Fund
BILLS OF QUANTITIES
Project title: Design, supply, installation, testing, commissioning and training of Pressure Swing Adsorption (PSA) technology based Oxygen generating plant in Djerba Regional Hospitals in TUNISIA
SECTION No. | ITEM No | Oxygen PSA Generator supply, delivery, installation, commissioning and training | UNIT | QTY | UNIT PRICE (insert currency) | TOTAL (insert currency)
DESIGNATION
| 1 | Section 1: Oxygen PSA Generator Main Unit supply & Installation
A compact structure PSA Oxygen Plant is to be installed to supply uninterrupted high-quality medical oxygen through central medical gas pipeline system to the hospital facility. The plant should consist of at least: Power supply, Screw type air compressor, air dryer, filters & Filtration system (micron, bacteria etc.), air tank, oxygen generator, oxygen buffer tank, Emergency bottles (Back up), bottle filling system, medical gas system monitoring and analyzer, regulation and alarm system, pressure transducers, flowmeters, valves, controls, distribution network (piping and accessories) and any other component needed to make the system fully functional. The Oxygen Generator (OG) shall operate on (PSA) Pressure Swing Adsorption principle. The OG should have at least the following features: Max/peak oxygen flow: 60 Nm3/h Continuous oxygen flow: 50 Nm3/h +/- 10% @ 4-6 Bar outlet pressure (noting that the pressure reaching the oxygen outlets inside the hospital should not be less than 4 bar) Oxygen Purity should be at least 93±3%. Compact structure- ·Power supply AC 400V, 50Hz 3-phase, Less than 80 kW consumption. Installation must include a self-switching Manifold meeting ISO standards and designed with regulators tested at a high pressure, connected to two different sources of supply primary and secondary source of oxygen (one from the new PSA and the other of the hospital's old PSA). The switch mounted on the control panel allows switching between the two sources.
| 1.1 | Supply, Delivery & on-site Installation and commissioning at Djerba Hospital | No | 1 |  | 0
| 1.3 | Piping and accessories
Ø12/14 Copper tube. High quality and in full compliance with standard EN 13348 “copper tube for medical gases” and standard NF EN 7396-1 relating to the “calculation of medical gas distribution installations”. Features: - No welding - Smooth, clean and dry inner wall - Ends sealed until installation to avoid any risk of contamination by external impurities during storage or transport - Gas tight - Limited residual impurity content
| 1.3.1 | Supply, Delivery & Installation at Djerba Hospital | m | 20 |  | 0
| 1.4 | Bottle filling system self-switching Manifold and Medical Oxygen Cylinders supply, installation and commissioning
| 1.4.1 | Medical cylinders, 46.7L, ISO 9809
| 1.4.1.1 | Supply, Delivery & Installation at Djerba Hospital | No | 10 |  | 0
| 1.4.2 | Bottle filling system supply, installation and commissioning
SEMI AUTOMATIC MANIFOLD SYSTEM: Norm: ISO, Maximum flow: 50 Nm3/h +/- 10% @ 4-6 Bar, Medical gas: O2, Cylinder connection type: Stainless Steel pigtails, Cylinder connection standard: BS, Equiped with Alarm panel
| 1.4.2.1 | Filling Ramps for Djerba Hospital site | No | 2 |  | 0
| 1.4.2.2 | Pigtails for Djerba Hospital site | No | 10 |  | 0
| 1.4.3 | Self-switching Manifold
A self-switching Manifold meeting ISO standards and designed with regulators tested at a high pressure, connected to two different sources of supply primary and secondary source of oxygen (one from the new PSA and the other of the hospital's old PSA). The switch mounted on the control panel allows switching between the two sources.
| 1.4.3.1 | Self-switching Manifold for Djerba Hospital site | No | 1 |  | 0
| 1.4 | Power protection equipment supply, on-site installation and commissioning
The main power supply (80KVA) will be from the main power supply of the sector (there is 300 kVA available as residual power versus 80 kVA necessary for the plant). This main 80KVA power should be through MCCB. The whole system (Main and Control) shall be supplied with an Automatic Voltage Stabilizer (AVS) (3phase, 380 to 400V +/- 5%, 50Hz, minimum 80 KVA) to stabilize the voltage supplied to the system (voltage surges, fluctuations, and drops). Standby generator (an emergency power supply) (3phase, 380 to 400V +/- 5%, 50Hz, minimum 80 KVA) equipped with an Auto Transfer Switch to support the power supply of the PSA installation offered in case of the primary power source failure. - UPS- Uninterruptible Power Supply- (220 VAC ± 5% - 1 phase / 50 Hz, max. 3KVA) with an autonomy of Thirty Minutes, complete including protection, inverter and batteries) for Control system operations. Electrical Interconnection: Industrial Disconnector Switch or Industrial Plug of adequate rating. Adequate grounding must be provided for each component of the circuit as described in the document ''Configuration du circuit d'Alimentation électrique''
| 1.4.1 | Automatic Voltage Stabilizer (AVS) (3phase, 380 to 400V +/- 5%, 50Hz, 80 KVA)
| 1.4.1.1 | Supply, Delivery & Installation at Djerba Hospital | No | 1 |  | 0
| 1.4.2 | UPS- Uninterruptible Power Supply- (220 VAC ± 5% - 1 phase / 50 Hz, max. 3KVA)
| 1.4.2.1 | Supply, Delivery & Installation at Djerba Hospital | No | 1 |  | 0
| 1.5 | Standby generator (an emergency power supply) (3phase, 380 to 400V +/- 5%, 50Hz, 60 KVA) equipped with an Auto Transfer Switch (3 Phase, 380V to 400V, 150A, 45 to 65Hz, 10mS)
| 1.5.1 | Supply, Delivery & Installation at Djerba Hospital | No | 1 |  | 0
| 1.6 | Hospital MCCB: 3 Phase, 380V to 400V, 100A, 20kA
| 1.6.1 | Supply, Delivery & Installation at Djerba Hospital | No | 1 |  | 0
| 1.7 | Power distribution Board (in PSA Plant Room): 3Phase, 100A, 20kA
| 1.7.1 | Supply, Delivery & Installation at Djerba Hospital | No | 1 |  | 0
| 1.8 | Grounding cables in copper and necessary accessories for each component of the circuit (see Document ''Configuration du circuit d'Alimentation électrique'': 35mm2, 5 ohm (max for grounding value)
| 1.8.1 | Supply, Delivery at Djerba Hospital | m | 20 |  | 0
| 1.9.2 | Installation at Djerba Hospital | No | 1 |  | 0
| 1.9 | Three Phase Power Cable (5x) made in copper, 35mm2 as shown in document ''Configuration du circuit d'Alimentation électrique''
| 1.9.1 | Supply, Delivery at Djerba Hospital | m | 100 |  | 0
| 1.9.2 | Installation at Djerba Hospital | No | 1 |  | 0
| 1.10 | Single phase Power Cable (3x) made in copper, 35mm2 as shown in document ''Configuration du circuit d'Alimentation électrique''
| 1.10.1 | Supply, Delivery at Djerba Hospital | m | 10 |  | 0
| 1.10.2 | Installation at Djerba Hospital | No | 1 |  | 0
| 1.11 | Technical staff Training
Training of the local technical team (3 techncians) on the use and maintenance of the equipment (Maintenance level 2 according to the maintenance levels of the AFNOR standard).
| 1.11.1 | Technical training for Djerba Hospital local team | No | 3 |  | 0
| 1.12 | WARRANTY
2 years from installation and commissioning
| 1.12.1 | Preventive and Curative maintenance, parts and labor included | Year | 2 |  | 0
| 1.13 | Maintenance kits
Maintenance kit required for an operation period of 2 years Tool kit for oxygen plant maintenance
| 1.13.1 | Supply and Delivery at Djerba Hospital | No | 1 |  | 0
|  | Total price, all inclusive |  |  |  | 0
Bidder name:
Authorized representative full name & title:
Signature: