Terms of Reference

Design, Procure and Install Solar PV Systems and Appliances for

Selected Demonstration Sites in Ethiopia

I. Introduction

Upon the partnership with governments of China and Ethiopia, UNDP is implementing the project, entitled “Biogas, Biomass and Solar Trilateral Cooperation- Transitioning to Sustainable Energy Uses in the Agro-Industry Sri-Lanka-China-Ethiopia Project” with the aim to address sustainable development challenges related to international cooperation, access to energy for improved service delivery and sustainable integrated farming practices for Ethiopia and to support GHG emission reduction national targets through trial and demonstration of the potential of biogas and solar in the agro-industry sector for Sri Lanka.

The Project in Ethiopia takes a point of departure in the need for renewable energy technology (RET) dissemination and scale-up for Ethiopia climate resilient growth and supports access to energy and sustainable resources consumption through trial and demonstration of biogas and solar energy for productive uses. The Project is implemented under a South-South Cooperation framework and as such presents itself as a learning platform for both China and Ethiopia to engage and cooperate at the international level in renewable energy technology and skills transfer.

The Project is executed by UNDP country offices of Ethiopia and China and implemented in a joint effort of the Ministry of Water and Energy of Ethiopia (MoWE), Ministry of Science and Technology of China- Administrative Center for China’s Agenda 21 (MOST-ACCA 21), and China Agricultural University (CAU). Project interventions include developing capacity of stakeholders in the energy sector to assess the potential of RET in meeting energy needs in productive sectors such as public service delivery and the agro-industry; hearing Chinese knowledge and experience in biogas and solar energy for productive uses; determining suitable business models through South-South knowledge and experience sharing platforms; providing support to Chinese institutions on carrying relevant capacity development in South partner countries.

The Project is providing technical and financial support to implement the activities under Outcome 1, which is to build capacity for RET transfer through demonstration of biogas and solar for productive uses. With the intention of implementing this outcome, the project has selected and endorsed 4 demonstration sites through calling for Expression of Interests (EOIs) to design, procure and install solar PV systems in Amhara, Harari and SNNPR regions in Ethiopia. Following that, energy need assessment and feasibility study have been carried out at the selected demonstrations sites.

Therefore, this TOR is prepared to design, supply, and install 4 sets of solar PV systems and appliances for selected demonstration sites in Amhara, Harari and SNNPR regions in Ethiopia.

II. Objectives

As included in the fiscal year 2021/2022 annual work plan of the project, the objective of this assignment is to design, procure 4 sets of solar PV systems, and related aftersales services to establish 4 solar PV demonstration sites in Amhara, Harari and SNNPR regions in Ethiopia.

III. The Scope of Work

1. Design, and planning

The selected bidder(s) is required to provide the design and planning works for the realization of solar PV demonstration construction, including but not limited to:

- Complete a report of project working plan specifying all the steps that will be carried out to perform the project (from design work to After-sales services) with the corresponding timeline and who will be responsible for each step (vendor, local partner, or both).

- Perform a detailed engineering on the design to acquire all necessary information for preparation of design documentation and discuss technical issues with representatives of all relevant stakeholders.

- Provide the technical design and drawings, including but not limited to civil construction drawings, physical layout drawings, functional drawings, single-line diagrams (SLDs), structural calculation notes, shading loss calculation, cable and protection sizing calculations, all technical datasheets and other manufacturer’s technical documentation.

- All planning and permitting works required for the realization of the project.

Submission of the following documents:

- Report of project working plan with time schedule and Gantt chart for the execution of the total works

- Technical design report including system design drawings to be approved by UNDP before start of works

- Bill of Quantities (BOQ) per site

- Social-environmental assessment and risk management plan

- As-built drawings and technical documentation (Including catalogues, brand names, model numbers of all equipment and materials installed in the Project, etc.) in English.

2. Supply of 4 sets of solar PV systems based on technical specification Section 5a.

3. Provide manual, telecalls, or video tutorials for the installation, maintenance, and operation of the solar PV systems.

4. Provide the following services (installation, testing/commissioning, and training) for the solar PV systems.

4.1 Installation services

Upon delivery of the systems to the destination, the selected bidder(s) will be required to undertake the site preparation (clearing, pruning, excavation, etc.) and   complete the installation at the solar PV demonstration sites.

4.2 Testing/commissioning services

After the completion process for installation, the selected bidder(s) will be required to test the function of the solar PV systems. All tests should be conducted in accordance with the descriptions below.

- On-site acceptance test: all individual components and the whole assembly of the product will be subjected to the relevant national standards, industrial standards and enterprise standards for type test, delivery test and on-site handover test. All part of the product should provide the type test and delivery test report of the products within the scope of supply.

- On-site handover test: the relevant government authorities/ end users should organize and implement the on-site handover test. The bidder(s) will send personnel to participate in the test to provide technical support and on-site cooperation; If the end users have special requirements, end users can negotiate with the bidder(s).

- Special test: if the end users have special requirements for product verification, special test can be carried out. The content of special test will be determined by the end user and the bidder(s) through negotiation. The test can be carried out in the type test, factory test or field handover test.

In addition, the tests needed to be carried out by the engineers deployed by the selected bidder (s) with consultation with relevant government authorities/ end users in Ethiopia.

The inspection and testing of the equipment on site serve the purpose of demonstrating that particular equipment is capable of conforming to the relevant general requirements, and the purpose of providing there is no deviation from the operating instructions.

Note: The end user/the focal point in the receiving unit will facilitate the testing step and provide the testing result as one of the supporting documents for releasing payment.

4.3 Training services

To provide training material (manual and video clips in English) and in-person/on-site training for the targeted group (no less than 2 persons in each demonstration sites) on how to operate the system and do regular checks or maintenance.

Number of trainees in each demonstrate site: no less than 2 persons

Duration of training: 6 hours per each location

The bidder (s) shall provide training for technical, operational and maintenance staff in each site as indicated.

The training shall be carried out in English by experienced engineers/trainers with not less than 5 years working experience and 2 years working experience with the delivered kind of equipment. The CV of the engineer/trainer must be provided for acceptance by UNDP in consultation with relevant departments in Ethiopia and the Joint Technical Committee in advance. If the engineer/trainer cannot communicate and carry out the required training sessions in English, the selected bidder (s) must deploy a translator to be able to deliver the trainings in English. Any cost related must be covered by the bidder(s).

4.4 Warranty, Maintenance services and repair services

The selected bidder(s) must provide maintenance and repair support services which include:

- Clear written instruction on conducting maintenance and repair services need to be provided by the bidder(s). The selected bidder need to provide a warranty period of:  a) 15 years Warranty for the Solar Module; b) 3years for the   storage battery and c) 2 Years for Off-grid inverter . However, the bidder needs to provide warranty for a minimum period of two (2) years after the sale of the equipment (except for Solar Module, Storage Battery and Off grid Inverter. Please see below.), other than consumables, will be free from defects in material and workmanship.

- Spare parts should include installation and debugging spare parts and equipment operation spare parts. Spare parts should be new products with the same model and process as the products. The bidder(s) shall provide spare parts free of charge, including wearing parts for a minimum period of one year (1) after the qualified operation.

- Technical support must be available for a minimum period of one (1) year. The bidders need to have service centers or authorized partnering agents in Ethiopia for providing in-country or on-site support and provide detailed information and agreement for the services. The bidder(s) must provide on-site technical support on how to identify different types of errors and how to solve said errors or malfunctions for a minimum period of one (1) year.

- The on-site support must provide solutions to effectively resolve the issue, share preventive advice to avoid similar issues in the future, and promote sustainable operation and maintenance of the system. The provided on-site support must ensure achieving the optimal benefits and functions of the supplied equipment and associated services in its lifecycle, to maximize the benefits to relevant end users as the common good. After the warranty period, any cost related to the technical support will be separately discussed with the selected bidder(s) once there is a need.

IV. Required Deliverables

Delivery of Solar PV Systems and Appliances and installation need to be completed within 3 months (90 days).  The following presents the list of required deliverables.

| Deliverable 1 | Detailed system design, technical report, and drawings of 4 solar PV systems in target locations; Report of project working plan with time schedule and Gantt chart for the execution of the total works; Bill of Quantities (BOQ) per site; Social-environmental assessment and risk management plan; As-built drawings and technical documentation (Including catalogues, brand names, model numbers of all equipment and materials installed in the Project, etc.) in English. |
| --- | --- |
| Deliverable 2 | On-site supply and delivery of 4 sets of solar PV systems with all components needed for its operation |
| Deliverable 3 | Provision of manual, telecalls, or video tutorials for the installation, maintenance, and operation of the solar PV systems |
| Deliverable 4 | Timely installation, construction, testing/commissioning and well-performing solar PV systems in selected target locations |
| Deliverable 5 | In-person/on-site training on operation and maintenance of the installed equipment, as well as provision of training manuals |
| Deliverable 5 | The selected bidder need to provide a warranty period of: a) 15 years Warranty for the Solar Module; b) 3years for the storage battery and c) 2 Years for Off-grid inverter . However, the bidder needs to provide warrants for a minimum period of two (2) years after the sale of the equipment (except for Solar Module, Storage Battery, and Off grid ) and a minimum period of one year for warranty on spare parts, labor, and technical support. |

Details and Specifications of the Solar PV Systems

1. PV System for Newase Primary and Junior Secondary School in Wolaita Sodo town, SNNPR region

- Newase Primary and Junior Secondary School was established in 2004 E.C, which is Located in Boloso Sore Woreda of Wolaita Zone, about 35 km far from Sodo city and about 370 km from Addis Ababa (Latitude7.09, Longitude:37.71). It is a Primary and secondary school (1-8 grade). Currently, the school has 1067 students, and among these, 40 of them are disabled. There are 10 classrooms, 1 library, 1 laboratory, 2 offices (director and staff offices), and one center for disabled students. The plan of the site can be seen below in Figure 1, Figure 2 and Figure 3.

Figure 1 – Back site area for demonstration

| Kebele | Woreda | Place of the school | Area (back site) | Owner | Purpose |
| --- | --- | --- | --- | --- | --- |
| Basa gofera Boloso Sore | Boloso Sore | Newase school | 3900km2 (50m*78m) | Newase school | Solar Demonstration site |

Figure 2 – Back site1, 2, 3 images

Figure 3 – Director Office, Classrooms images

- The school received Desktops, laptops, LCD projectors, LED TVs, and tape recorders from the regional education office and other donors. But the school doesn’t use these all appliances due to the lack of electricity. The energy demand of Newase primary and secondary school from solar PV system is shown below.

| Items | Quantity | Wattage(W/unit) | ON time per day | Wh/unit | Wh/day |
| --- | --- | --- | --- | --- | --- |
| Bulb | 47 | 25 | 4 | 100 | 4,700 |
| LCD TV | 2 | 55 | 4 | 220 | 440 |
| Desk top computer | 21 | 200 | 4 | 800 | 16,800 |
| Printer | 1 | 120 | 4 | 480 | 480 |
| Photocopy machine | 1 | 180 | 4 | 720 | 720 |
| UPS | 1 | 900 | 4 | 3,600 | 3,600 |
| Total |  |  |  | 5,920 | 26,740 |

- The details of systems and specifications are described below as follows:

| No. | Items | Specification | Unit | Quantity |
| --- | --- | --- | --- | --- |
| 1 | Solar module | Category: Single-crystal silicon, Grade A Power: 335w - 455w Rated voltage: 40- 42V Rated current: 10 A – 11 A Module efficiency: about 20.5% - 21.4% | No. | 20 |
| 2 | PV module bracket | Hot dip galvanized photovoltaic bracket; C41*62 hot dip galvanized steel; Matching hot dip galvanized screws and nuts. Life span more than 25 years. Note: Bidder can clearly specify based on site conditions in destinations and must be compatible with all relevant proposed equipment. | Set | 1 |
| 3 | MPPT | Operating voltage: 96V Operating current: 100A Charging mode: MPPT Display mode: LCD | No. | 1 |
| 4 | Off-grid inverter | Rated power: 10KW Input voltage: DC96V Output voltage: AC220V Wave type: pure sine wave | No. | 1 |
| 5 | Valve-controlled, lead acid, maintenance-free colloid storage battery (life cycle: 6 years) | Rated voltage: DC12V，250Ah | No. | 32 |
| 6 | Control cabinet and accessories (Outdoor control box, short circuit protection, over voltage and over current protection, lightning protection, temperature detection) | Bidder to clearly specify based on site conditions in destinations, and must be compatible with all relevant proposed equipment | Set | 1 |
| 7 | Auxiliary material, e.g., Cables |  | Set | 1 |
| 8 | Batteries bracket |  | Set | 2 |
| 9 | Photovoltaic bus box (3 in 1 out) |  | Set | 2 |
| Installation: The installation is to provide by the Supplier, hence, all the required accessories and other works related with the installations of the Solar PV System should be indicated in the technical proposal and financial offer. |  |  |  |  |

2. PV System for Harari Education Bureau (Kara Primary School) in Harari Region

- Kara Primary School (Latitude 9.370, Longitude 42.236) is one of the two primary schools selected by Harari Education Bureau in the Erer woreda among eight schools that is not electrified. The school is located in Shenkor Woreda, Harari regional state of Ethiopia.

Figure 4 – Kara Primary School Building image

- The Solar Panels are suggested to be located on the roof of the building. The plan of the roof can be seen below in Figure 5.

Figure 5 – Roof design drawings

- Since there is no overhead transmission line in the school area, there is no electricity/ energy source and no electric energy expense. The electricity needs of the school is shown below.

| No. | Appliances | Powe (W) | No. of Appliances | Daily use(hrs.) | Daily Energy (Wh/d) |
| --- | --- | --- | --- | --- | --- |
| 1 | Desktop computer | 200 | 25 | 4 | 20,000 |
| 2 | Led bulb | 8.5 | 75 | 6.5 | 4,144 |
| 3 | Amplifier | 150 | 1 | 2 | 300 |
| 4 | Laser jet Pro M102a Printer | 380 | 1 | 2 | 760 |
| 5 | LCD TV for laboratory | 150 | 2 | 4 | 1,200 |
| 6 | A satellite dish receiver-SUPER MAX | 60 | 1 | 5.6 | 336 |
| Total |  |  |  |  | 26,740 |

- The details of systems and specifications are described below as follows:

| No. | Items | Specification | Unit | Quantity |
| --- | --- | --- | --- | --- |
| 1 | Solar module | Category: Single-crystal silicon, Grade A Power: 335w - 455w Rated voltage: 40- 42V Rated current: 10 A – 11 A Module efficiency: about 20.5% - 21.4% | No. | 20 |
| 2 | PV module bracket | Hot dip galvanized photovoltaic bracket; C41*62 hot dip galvanized steel; Matching hot dip galvanized screws and nuts. Life span more than 25 years. Note: Bidder can clearly specify based on site conditions in destinations and must be compatible with all relevant proposed equipment. | Set | 1 |
| 3 | MPPT | Operating voltage: 96V Operating current: 100A Charging mode: MPPT Display mode: LCD | No. | 1 |
| 4 | Off-grid inverter | Rated power: 10KW Input voltage: DC96V Output voltage: AC220V Wave type: pure sine wave | No. | 1 |
| 5 | Valve-controlled, lead acid, maintenance-free colloid storage battery (life cycle: 6 years) | Rated voltage: DC12V，250Ah | No. | 32 |
| 6 | Control cabinet and accessories (Outdoor control box, short circuit protection, over voltage and over current protection, lightning protection, temperature detection) | Bidder to clearly specify based on site conditions in destinations, and must be compatible with all relevant proposed equipment | Set | 1 |
| 7 | Auxiliary material, e.g., Cables |  | Set | 1 |
| 8 | Batteries bracket |  | Set | 2 |
| 9 | Photovoltaic bus box (3 in 1 out) |  | No. | 2 |
| 10 | Installation: The installation is to provide by the Supplier, hence, all the required accessories and other works related with the installations of the Solar PV System should be indicated in the technical proposal and financial offer. |  |  |  |

3. PV System for Harai Education Bureau (Semire Primary School) in Harari region

- Semire Primary School (Latitude 9.334, Longitude 42.195) is one of the primary schools selected by Harari Education Bureau in the Erer woreda among eight schools that is not electrified. The school is located in Shenkor Woreda, Harari regional state of Ethiopia.

Figure 6 – Semire Primary School Building image

- The Solar Panels are suggested to be located on the roof of the building. The plan of the roof can be seen below in Figure 7.

Figure 7 – Roof design drawings

- Since there is no overhead transmission line in the school area, there is no electricity/ energy source and no electric energy expense. The electricity needs of the school is shown below.

| No. | Appliances | Powe (W) | No. of Appliances | Daily use(hrs.) | Daily Energy (Wh/d) |
| --- | --- | --- | --- | --- | --- |
| 1 | Desktop computer | 200 | 25 | 4 | 20,000 |
| 2 | Led bulb | 8.5 | 75 | 6.5 | 4,144 |
| 3 | Amplifier | 150 | 1 | 2 | 300 |
| 4 | Laser jet Pro M102a Printer | 380 | 1 | 2 | 760 |
| 5 | LCD TV for laboratory | 150 | 2 | 4 | 1,200 |
| 6 | A satellite dish receiver-SUPER MAX | 60 | 1 | 5.6 | 336 |
| Total |  |  |  |  | 26,740 |

- The details of systems and specifications are described below as follows:

| No. | Items | Specification | Unit | Quantity |
| --- | --- | --- | --- | --- |
| 1 | Solar module | Category: Single-crystal silicon, Grade A Power: 335w - 455w Rated voltage: 40- 42V Rated current: 10 A – 11 A Module efficiency: about 20.5% - 21.4% | No. | 20 |
| 2 | PV module bracket | Hot dip galvanized photovoltaic bracket; C41*62 hot dip galvanized steel; Matching hot dip galvanized screws and nuts. Life span more than 25 years. Note: Bidder can clearly specify based on site conditions in destinations and must be compatible with all relevant proposed equipment. | Set | 1 |
| 3 | MPPT | Operating voltage: 96V Operating current: 100A Charging mode: MPPT Display mode: LCD | No. | 1 |
| 4 | Off-grid inverter | Rated power: 10KW Input voltage: DC96V Output voltage: AC220V Wave type: pure sine wave | No. | 1 |
| 5 | Valve-controlled, lead acid, maintenance-free colloid storage battery (life cycle: 6 years) | Rated voltage: DC12V，250Ah | No. | 32 |
| 6 | Control cabinet and accessories (Outdoor control box, short circuit protection, over voltage and over current protection, lightning protection, temperature detection) | Bidder to clearly specify based on site conditions in destinations, and must be compatible with all relevant proposed equipment | Set | 1 |
| 7 | Auxiliary material, e.g., Cables |  | Set | 1 |
| 8 | Batteries bracket |  | Set | 2 |
| 9 | Photovoltaic bus box (3 in 1 out) |  | No. | 2 |
| 10 | Installation: The installation is to provide by the Supplier, hence, all the required accessories and other works related with the installations of the Solar PV System should be indicated in the technical proposal and financial offer. |  |  |  |

4. PV System for Amhara Water Irrigation and Energy Development Bureau in Amhara Region

- Amhara Water Irrigation and Energy Development Bureau is located in Ambassel worda (Tisabalima), Amhara National Regional State North Wollo zone of Ethiopia. Its geographical location (GPS) is longitude 39.751and its latitude is 11.566. Groundwater well Irrigation project is located in ANRS North Wollo zone. The site is 56km from Woldia zonal capital, 26km from Woreda, Mersa town. 1km of the road is accessed on foot. The irrigated area is 54 ha. It has a grid system nearby 3.6km from the project site. The distribution line voltage level is 15kV, but this high-tension power is not efficient enough to run a 75kw electrical motor. The electrical line installed from nearby the substation is about 56km. There is suitable place (1000m2) around the powerhouse.

Figure 8 –The areas around the powerhouse and water well images

- The details of systems and specifications are described below as follows:

| No. | Items | Specification | Unit | Quantity |
| --- | --- | --- | --- | --- |
| 1 | Solar module | Category: Single-crystal silicon, Grade A Power: 335w - 455w Rated voltage: 40- 42V Rated current: 10 A – 11 A Module efficiency: about 20.5% - 21.4% | No. | 322 |
| 2 | PV module bracket | Hot dip galvanized photovoltaic bracket; C41*62 hot dip galvanized steel; Matching hot dip galvanized screws and nuts. Life span more than 25 years. Note: Bidder can clearly specify based on site conditions in destinations and must be compatible with all relevant proposed equipment. | Set | 1 |
| 3 | Pump | 90-96kW, 380V, Total head>90m | No. | 1 |
| 4 | Specific solar pump inverter | 110KW, 380V, Max efficiency 97% | No. | 1 |
| 5 | Control cabinet and accessories (Outdoor control box) | Bidder to clearly specify based on site conditions in destinations, and must be compatible with all relevant proposed equipment | Set | 1 |
| 6 | Auxiliary material, e.g., Cables |  | Set | 1 |