## Clarification
Clarification Round 2
UNDP- ETH-00014 : Supply and Installation of Solar PV Systems and Appliances for Selected Demonstration Sites in Ethiopia
Request no. | Date | Document reference (specify paragraph / section / article) | Clarifications | Date | Client Response | Status
1 | 2022-10-18 | Terms of Reference - TOR (Page-6) PV System for Newase Primary and Junior Secondary School in Wolaita Sodo town, SNNPR region | As per the given data and pictures it is not clarify either it is roof mounted system or ground mounted system? Please share the kmz file or the exact coordinates of the site for our review to check the available space and the trees shadows. |  | The Solar PV systems will be installed on the ground for Newase Primary and Junior Secondary School in Wolaita Sodo town, and please follow the specificiatons in the TOR.
2 | 2022-10-18 | Terms of Reference - TOR (Page-6) PV System for Newase Primary and Junior Secondary School in Wolaita Sodo town, SNNPR region | Please confirm if the Secuirty Fence is required for the ground mounted PV System or not? If required, please share the specifications of Fence. |  | Please refer to the specifications given in the TOR.
3 | 2022-10-18 | Terms of Reference - TOR (Page-6) PV System for Newase Primary and Junior Secondary School in Wolaita Sodo town, SNNPR region | If the system is roof mounted kindly provide the height of building? Termination point, inverter and battery location is not given in provided data so kindly provide the the location of termination point, inverter and battery? |  | The Solar PV systems will be installed on the ground for Newase Primary and Junior Secondary School in Wolaita Sodo town, and please follow the specificiatons in the TOR.
4 | 2022-10-18 | Terms of Reference - TOR (Page-6) PV System for Newase Primary and Junior Secondary School in Wolaita Sodo town, SNNPR region | If the system is ground mounted kindly provide the termination point, inverter and battery location? Also provide the distance from PV Area to termination point? |  | Termination point, inverter and battery location is on the ground, and the exactly position should be set down when intalling on the spot. Distance between PV Area to termination point is approximately 30 meters.
5 | 2022-10-18 | Terms of Reference - TOR (Page-10) PV System for Harari Education Bureau (Kara Primary School) in Harari Region | The building height is not given in provided data so kindly provide the height of building? Termination point, inverter and battery location is not given in provided data so kindly provide the the location of termination point, inverter and battery? |  | The building height for Kara primary school is 10.2 meter. Termination point, inverter and battery location is on the ground, and the exactly position should be set down when intalling on the spot.
6 | 2022-10-18 | Terms of Reference - TOR (Page-14) PV System for Harai Education Bureau (Semire Primary School) in Harari region | The building height is not given in provided data so kindly provide the height of building? Termination point, inverter and battery location is not given in provided data so kindly provide the the location of termination point, inverter and battery? |  | The building height for Semire school is 7.4 meter. Termination point, inverter and battery location is on the ground, and the exactly position should be set down when intalling on the spot.
7 | 2022-10-18 | Terms of Reference - TOR (General School Sites 1-3) | The rating of PV modules is mentioned as 335w - 455w which corresponds to the DC system of 6.7kW to 9.1kW. Please confirm the DC capacity of the system which is required. |  | The DC capacity of the system should be 6.7kVA to 9.1kA KVA and KW are not exactly the same but related.
8 | 2022-10-18 | Terms of Reference - TOR (Page-17) PV System for Amhara Water Irrigation and Energy Development Bureau in Amhara Region | Area is not clearly marked for PV System? Distance from PV Area to Inverter location is also not clarify? It is also not clarify either it is VFD Pump system or On grid system? |  | Inverter shoule be located near the well, and it could be found on spot. This is an off-grid system.
9 | 2022-10-18 | Terms of Reference - TOR (General All Sites 1-4) | Please specify whether the equipment room/space for inverters and batteries shall be provided witihin the buildings or the construction of room is in the scope of the Bidder. |  | There is room/space available for the mentioned components, inverter, battery etc..
10 | 2022-10-18 | Terms of Reference - TOR (General School Sites 1-3) | Please inform whether any structural integrity assessment has been carried out for the rooftops of schools by any Civil Consultant for confirmation of building suitability for Civil works. Kindly share the report. For the purpose of clarity, any reinforcement works for the building rooftops shall be excluded from the scope of Bidder. Please confirm. |  | There is no integrety assessment done on the roofs, but the selected insitution confirmed that the roofs are capable of carrying the solar panels.
11 | 2022-10-18 | Terms of Reference - TOR (General School Sites 1-3) | Please confirm if any arrangements of water piping and pumping is required for cleaning of PV modules on the rooftops or it will be managed through existing facilities by the end user itself. |  | It will be managed by the end users based on the intructions given by the company.
12 | 2022-10-18 | Terms of Reference - TOR (General School Sites 1-3) | Please provide the details of Distribution Boards in the buildings. It is assumed that the solar power connection shall be made to the main Distribution board and the remaining internal wiring and distribution shall be used as per existing situation. Please confirm. |  | The selected room for distribution boards will be avail during the installation.
13 | 2022-10-18 | Terms of Reference - TOR (General School Sites 1-3) | Please confirm if the access ladder to the rooftops of schools is available or bidder has to consider the provision of access ladder in its scope. |  | The bidder should faciliate the equipment and tools for installatiion
14 | 2022-10-18 | Terms of Reference - TOR (Page-17) PV System for Amhara Water Irrigation and Energy Development Bureau in Amhara Region | Please share the details of 1000m2 area available for installation of Solar Modules for the PV System for Amhara Water Irrigation and Energy Development Bureau in Amhara Region site. The KMZ file shall be required to assess the earthworks requirement for ground monuted PV system. |  | There is a flat area for installation. There is possiblity to choose any spot wihtin 1000m2 areas.
15 | 2022-10-18 | Terms of Reference - TOR (Page-17) PV System for Amhara Water Irrigation and Energy Development Bureau in Amhara Region | Please confirm if the Secuirty Fence is required for the ground mounted PV System or not? If required, please share the specifications of Fence. |  | Please follow the specifications provided in the TOR.
17 | 2022-10-18 | Terms of Reference - TOR (Page-17) PV System for Amhara Water Irrigation and Energy Development Bureau in Amhara Region | The rating of PV modules is mentioned as 335w - 455w which corresponds to the DC system of 107,87kW to 146.5kW. Please confirm the DC capacity of the system which is required. |  | The DC capacity of the system should be 107.87kVA to 146.5kVA
18 | 2022-10-18 | Terms of Reference - TOR (General All Sites 1-4) | The PV modules of 335w-455w may not be available at the time of project execution, please confirm if we can use higher capacity PV modules i.e. 540W +. |  | No, there is a whole design, and the larger modules can't match the MPPT charger and the interter. If there is only the 540W module available, there should be a new desigh for the system.
19 | 2022-10-18 | Invitation to Bidder-ITB (General Condition of Contract 2.2.1) | If the short word GTCs for "General Condition of Contract" is wrong?I assumed GCC correctly. In addition, there is no attachment for"General Condition of Contract" in the Portal on the UNDP web. As we understand, is that "Section 2_General instructions to Bidders" right for "General Condition of Contract"?, please confirm it. |  | Yes: GTC stands for General Terms and Conditions. We have attached the GTC and In section 2, in additions to the General instruction to bidders, we have attached bid data sheet. In fact, bid data sheet was attached in section 1, sub section 1.2