## Solar pump
SOLAR PUMP and INSTALLATION
ITEM |  | DESCRIPTION | UNIT | QNT | RATE (SLE) | AMOUNT (SLE)
1 | Material Number | SUPPLY AND INSTALLATION OF 1.4 KWP SOLAR PUMP
1.1 | SL010619 | Supply a solar-powered submersible water pump capable of delivering 20 m3/day - against a total dynamic head of 100 m coupled to a 1.4KWP motor; type SQF 2.5-2. pump with built-in non-return valve; Stainless steel pump casing; Maximum ambient pressure: 15 bar; Pump outlet dia. 1 1/4"; Rated current: 8.4 ; Motor Rated speed: 3600 rpm; Mains frequency: 50 / 60 Hz; Rated voltage: 1 x VDC 30-300 V; | LS | 29
1.2 | SL010619 | Supply a control unit CU 200, enables connection of a level switch; incorporates cable entries for -power supply connection,-pump connection, earth connection, level switch connection. the control unit should have idicator for system monitoring and alarm indicator, pump runing, input power and other accessories all enclosed in weather proof steel enclosure and capable to run a 1.4 kW motor. | LS | 29
1.3 | SL011347 | Supply solar panel modules of 300 W minimum, of min 35.5vdc, arrayed will be determine dased on the borehole depth | No | 348
1.4 | SL009533 | 3 X 6 Sq mm submersible cable toxic-free, each length is 130m with no Joint. | Set | 29
1.5 | SL010619 | FLOAT Electrical water tank level switch with 0.5 sq. mm 2 core cable of length 50m | No | 29
1.6 | SL010619 | Head plate, dia 200mm thickness 3mm, stainless steel, pre-drilled and threaded 1''1/4 Elbow 90° galvanised iron | No | 29
1.7 | SL012395 | Stainless steel wire cables diameter : 4mm which can Resistance : 990kg in rolls of 100m | No | 10
1.8 | SL006575 | Supply steel structure for mounting solar modules 4.0m high from the natural ground level by means of 6No. 5mm thick 100mm diameter stainless steel pipes. Properly align the solar modules parallel to the equator, nearly flat but tilted at 90 to the North facing south and able to capture the sun’s irradiation while on the Cancer, Equator, and Capricorn Tropics. 75mm x 50mm X 2mm thick box pipe for the mainframe and braces 50mm x 50mm x 2mm thick. | LS | 29
1.9 | SL006174 | Lighting protection combiner box: The PV array lightning protection box has the following characteristics： （1）meet the requirements of outdoor installation, protection class IP65, with anti-UV, anti-acid, anti-alkali, moisture, mildew, rodent control, and other functions； （2）access 4-way PV array, each with 15A, 1000Vdc fuse (replaceable other grades）； （3）Equipped with a special high-voltage lightning protection device, lightning protection function with cathode and anode ； （4）Use quadruple PV dedicated circuit breaker with positive and negative in series; Items inside the box 1. Negative convergence copper busbar 2. 4-way detection unit 3. DC MCB 4. Dc positive Convergence output 5. Dc negative Convergence output 6. Ground output point 7. Lightning protection device 8. Positive convergence copper 9. DC positive fuse holder and fuse (each input in series with a fuse) up to 4 ways 10. DC negative fuse holder and fuse (each input in series with a fuse) up to 4 road | No | 29
1.1 | SL013296 | Earth Rod: Solid Copper Earth Rods, minimum 2.4 m length, the diameter of earth rod of 12.7 mm, and unit weight 2.36Kg | No. | 58
1.11 | SL013297 | Earth cable:16mm Copper Ground Wire | M | 725
1.12 |  | 1 1/4" Diameter HDPE pipes PE-100, in roll of 100m | M | 2900
1.14 |  | Enclosure, Multipurpose, material Polycarbonate,size0 300 mm, 250 mm, 150 mm, IP65, and a DC disconnect switch 25A | No. | 29
1.13 |  | Installation of the system with two years warranty for equipment and installation. During the installation, training will be done for the two pump operators from each community. The cost should include all missing items for the installation. | No. | 29
TOTAL FOR 29 SOLAR PUMPS