## 1. 30 kVA PV 10% Roof
Bidder name:
Make and model:
Lot 1. 30 kVA PV 10% Sloped Roof or Gen set mount.
HYBRID PV SOLAR/DIESEL GENERATOR SET SPECS | UNOPS REQUIREMENTS | Bidder: Compliant/Non-compliant to UNOPS requirements? Please mark YES/NO in this coloumn. Not indicating YES/NO in this column may render your bid non-compliant. | Bidders are required to provide information in this column on the specifications of their bid to demonstrate compliance to set specifications. Not providing specifications under this column may render your bid non-compliant.
Complete Hybrid PV solar/diesel generator set for autonomous operation, including PV solar power array, battery package, inverter and charge controller. Diesel engine, alternator, control panel with monitoring gauges/indicators, starting equipment, fuel tank as well as other accessories. Charger to charge battery package by diesel gen set and PV solar system interface between diesel gen set and PV solar power unit for a smooth operation for the two energy sources in conjunction, automatically without any manual intervention. Factory test certificates must be included and must be in accordance to internationally recognised standards. Suitable for tropical conditions. | Comply and state → | Yes / No
KEY DATA
Make | Please state →
Model | Please state →
Country of origin | Please state →
DIESEL GEN SET
Rated power output, min. 30 kVA | Comply and state → | Yes / No
Power factor: 0.8 | Comply and state → | Yes / No
Rated power output, 24 kW, min. | Comply and state → | Yes / No
Voltage, 220/230/240 and 380/400 V | Comply and state → | Yes / No
Phase: 1 and 3 | Comply and state → | Yes / No
AC frequency, 50/60 Hz | Comply and state → | Yes / No
Speed: rpm 1500 or 3000 or other | Please state →
Prime power according to ISO 8528 or equivalent, i.e. power available at variable load with no limitations on hours of operation and capable of min. 10% overload for min. 1 hour in any 12 hours. | Comply and state → | Yes / No
Prime rating of min. the stated output rating at Normal Temperature and Pressure conditions (NTP). Please state | Comply and state → | Yes / No
Derating information (temperature, altitude and humidity), please state | Please state →
Engine
Make | Please state →
Model | Please state →
Engine power output, kW at rpm: | Please state →
Fuel: Diesel | Comply and state → | Yes / No
Cooling, liquid or air or combined, suitable for tropical conditions | Please state →
Speed governor, state type | Please state →
Exhaust with suitable piping and residential silencer | Comply and state → | Yes / No
Noise level, dB(A) at 1 m (silencer fitted) | Please state →
Fuel consumption at 75% load: L/hour | Please state →
CO2 emissions at 75% load: g/hour | Please state →
Mounted on anti-vibration mounts | Comply and state → | Yes / No
ENVIRONMENTAL
EU Non-road emissions regulations schedule, e.g. EU STAGE II, III A, III B, IV. US Non-road and stationary emissions regulations to Tier 1,2,3,4 or equivalent. Please state. | Comply and state → | Yes / No
Alternator
Make: | Please state →
Model: | Please state →
Brushless type | Comply and state → | Yes / No
Cooling, liquid, air, other | Please state →
Protection class min. IP 23 | Comply and state → | Yes / No
Suitable AC power outlets protected by circuit breaker (state type) | Comply and state → | Yes / No
Insulation to min. IEC 60085 - >155 ° C - (F) or equivalent | Comply and state → | Yes / No
Voltage regulator | Comply and state → | Yes / No
Standard accessories
Fuel tank. Integrated or separate, suitable for continuous operation of min. 8 hours at rated capacity. State capacity, litres. Fuel level gauge. Including all necessary pipework, connections etc. Possibility for connection to external tank. | Comply and state→ | Yes / No
Low oil pressure protection, automatic shut down | Comply and state → | Yes / No
Over heating protection | Comply and state → | Yes / No
Overload protection | Comply and state → | Yes / No
Emergency stop | Comply and state → | Yes / No
Electric starter with key and battery | Comply and state → | Yes / No
Min. Voltmeter, ammeter, hour meter, Hz meter, water temp gauge/indicator (where applicable) | Comply and state → | Yes / No
Earthing/grounding facility | Comply and state → | Yes / No
PV SOLAR POWER SYSTEM STANDARD ARRAY NOMINAL MIN. 2.4 kWp. Battery pack 24 kWh. For Sloped Roof or Gen set mount.
PV solar array
Make and model: | Please state →
Array kWp, min 10% of diesel generator set max output which is 30 kVA/24 kW, hence = 2.4kWp min. | Comply and state→ | Yes / No
PV panels, total surface covering, m2 | Please state →
Nominal power output each panel, kWp | Please state →
Isc array, A (Amp) | Please state →
Certifications: Any one or more of IEC61215, UL1703 or equivalent | Comply and state → | Yes / No
Charge controller
Make and model: | Please state →
Type: MTTP | Comply and state → | Yes / No
Certifications. Any one or more of EN60730-1/2-11, 55022, 61000-4-27374/5/6 or equivalent | Comply and state→ | Yes / No
Capacity: Isc array +20%, min. | Comply and state→ | Yes / No
Inverter
Make and model: | Please state →
Capacity, A (Amp): Min. equivalent to max load | Comply and state→ | Yes / No
Pure sine curve | Comply and state → | Yes / No
Certifications: Any one or more of EN50178, 62040, 60950, 61000-2/3/6, EN60529, 50438 or equivalent | Comply and state → | Yes / No
Battery package
Make and model: | Please state →
Capacity: Min. equivalent to hybrid diesel gen set full load - 24 kW - for 1 hour = 24 kWh. | Comply and state→ | Yes / No
Battery type: LiFePo4 | Comply and state→ | Yes / No
Certifications,: Any one or more of UL1642, IEC62133, 61000-6-3 or equivalent | Comply and state→ | Yes / No
PV panel racks, brackets, cables, fittings etc.
PV panels racks for sloped roof mount included for all included PV panels, if not attached to the Hybrid Gen set system itself (permanently or fold-out system etc). | Comply and state→ | Yes / No
All cables, junctions, contacts, breakers, earthing spears, fittings, screws, nut and bots etc included | Comply and state → | Yes / No
Installation
The system must be plug and play. Inverter, charge controller, battery package, battery charger must be pre-installed and wired either inside one common Hybrid system cage or in a separate cabinet, in order to easily connect the PV array and the local installation. All cables for establishing the PV array must be readily available with pre-installed connections and clearly marked in a way that no mistakes can occur. | Comply and state → | Yes / No
Other
Lifting points for handling | Comply and state → | Yes / No
Installation instructions, drawings, photos, brochures etc. English/French/Spanish | Comply and state → | Yes / No
Operators and maintenance manual, English/French/Spanish | Comply and state → | Yes / No
Tool kit | Comply and state → | Yes / No
Basic maintenance kit, engine: Min. 4 x oil filters, 2 x air filters, 2 x fuel filters | Comply and state → | Yes / No
Dimensions, L x W x H, mm | Please state →
Weight, dry, entire hybrid system incl. Battery package and all PV panels, cables, brackets etc etc.: kg: | Please state →
WARRANTY
Diesel Generator set: 2 years/2500 hours of operation which ever occur first. PV panels: Min. 10 years. Min. 90% performance guarantee at 10 years. Min. 80% performance guarantee at 20 years. Battery package: Min. 5 years. Inverter/charge controller/charger: Min. 4 years. Other equipment: Min. 2 years | Comply and state → | Yes / No
Sustainability
The bidder must demonstrate that its organisation has an environmental management system in place which as a minimum shall submit at least one or more of the following : the environmental policy principles of the organisation; the management measures and procedures taken or that will be taken to assess, monitor, measure and mitigate environmental impacts of the business processes/products associated with the execution of the contract; how attention is paid to the awareness and training/competency of employee(s) and supplier(s) with regard to dealing with the environmental aspects relevant to this bid; and that compliance with the environmental legislation applicable to the required performance(s) is guaranteed, ISO 14001 certificate, EMAS or an equivalent certificate | Comply and state → | Yes / No
The bidder shall provide documentation which outlines their approach to ensuring equal opportunity, diversity and inclusion within their organisation (e.g. equal pay policy, parental leave, ratio of females/males employees, % of female in management positions, grievances disaggregated by gender, transparency of promotion criteria, sexual harassment policies) | Comply and state → | Yes / No
Mandatory Options
Diesel engine spare parts & maintenance kit for min. 2500 hours of operation | Mandatory | enter prices on Form C: Price Schedule
Sound insolating and water proof canopy (max. 70 dB(A) at 7 m) | Mandatory | enter prices on Form C: Price Schedule
Work shop manual | Mandatory | enter prices on Form C: Price Schedule
Spare parts catalogue | Mandatory | enter prices on Form C: Price Schedule
60 Hz version of Generator set, please enter any surcharge to the std 50 Hz version offered above | Mandatory | enter prices on Form C: Price Schedule
Suggested Options
Heavy duty air filter for dusty conditions | Please provide price or state STD→ | Submit other option prices on a separate form
Heavy duty fuel filter/additional fuel filter in line with original | Please provide price or state STD→ | Submit other option prices on a separate form
Additional silencer, state dB(A) at 1 m and/or 7 m | Please provide price or state STD→ | Submit other option prices on a separate form
High chimney for exhaust, state height and materials | Please provide price or state STD→ | Submit other option prices on a separate form
(ATS) Automatic Transfer Switch | Please provide price or state STD→ | Submit other option prices on a separate form
Over speed protection | Please provide price or state STD→ | Submit other option prices on a separate form
Manual transfer switch | Please provide price or state STD→ | Submit other option prices on a separate form
External fuel tank with pipes including min.. 10 meter non-corrosive material and fittings, state volume of tank and material | Please provide price or state STD→ | Submit other option prices on a separate form
Slow moving trolley/trailer | Please provide price or state STD→ | Submit other option prices on a separate form
(AMF) Automatic Mains Failure Power generation set | Please provide price or state STD→ | Submit other option prices on a separate form
Automatic main circuit breaker | Please provide price or state STD→ | Submit other option prices on a separate form
Installation instructions and eventual. drawings, other languages | Please provide price or state STD→ | Submit other option prices on a separate form
Change over switch positions for: 1) Mains 2) Off 3) GENERATOR SET | Please provide price or state STD→ | Submit other option prices on a separate form
Automatic main circuit breaker | Please provide price or state STD→ | Submit other option prices on a separate form
Operators and maintenance manual, other languages | Please provide price or state STD→ | Submit other option prices on a separate form

## 2. 30 kVA PV 20% Roof
Bidder name:
Make and model:
Lot 2. 30 kVA PV 20% Sloped Roof or Gen set mount.
HYBRID PV SOLAR/DIESEL GENERATOR SET SPECS | UNOPS REQUIREMENTS | Bidder: Compliant/Non-compliant to UNOPS requirements? Please mark YES/NO in this coloumn. Not indicating YES/NO in this column may render your bid non-compliant. | Bidders are required to provide information in this column on the specifications of their bid to demonstrate compliance to set specifications. Not providing specifications under this column may render your bid non-compliant.
Complete Hybrid PV solar/diesel generator set for autonomous operation, including PV solar power array, battery package, inverter and charge controller. Diesel engine, alternator, control panel with monitoring gauges/indicators, starting equipment, fuel tank as well as other accessories. Charger to charge battery package by diesel gen set and PV solar system interface between diesel gen set and PV solar power unit for a smooth operation for the two energy sources in conjunction, automatically without any manual intervention. Factory test certificates must be included and must be in accordance to internationally recognised standards. Suitable for tropical conditions. | Comply and state → | Yes / No
KEY DATA
Make | Please state →
Model | Please state →
Country of origin | Please state →
DIESEL GEN SET
Rated power output, min. 30 kVA | Comply and state → | Yes / No
Power factor: 0.8 | Comply and state → | Yes / No
Rated power output, 24 kW, min. | Comply and state → | Yes / No
Voltage, 220/230/240 and 380/400 V | Comply and state → | Yes / No
Phase: 1 and 3 | Comply and state → | Yes / No
AC frequency, 50/60 Hz | Comply and state → | Yes / No
Speed: rpm 1500 or 3000 or other | Please state →
Prime power according to ISO 8528 or equivalent, i.e. power available at variable load with no limitations on hours of operation and capable of min. 10% overload for min. 1 hour in any 12 hours. | Comply and state → | Yes / No
Prime rating of min. the stated output rating at Normal Temperature and Pressure conditions (NTP). Please state | Comply and state → | Yes / No
Derating information (temperature, altitude and humidity), please state | Please state →
Engine
Make | Please state →
Model | Please state →
Engine power output, kW at rpm: | Please state →
Fuel: Diesel | Comply and state → | Yes / No
Cooling, liquid or air or combined, suitable for tropical conditions | Please state →
Speed governor, state type | Please state →
Exhaust with suitable piping and residential silencer | Comply and state → | Yes / No
Noise level, dB(A) at 1 m (silencer fitted) | Please state →
Fuel consumption at 75% load: L/hour | Please state →
CO2 emissions at 75% load: g/hour | Please state →
Mounted on anti-vibration mounts | Comply and state → | Yes / No
ENVIRONMENTAL
EU Non-road emissions regulations schedule, e.g. EU STAGE II, III A, III B, IV. US Non-road and stationary emissions regulations to Tier 1,2,3,4 or equivalent. Please state. | Comply and state → | Yes / No
Alternator
Make: | Please state →
Model: | Please state →
Brushless type | Comply and state → | Yes / No
Cooling, liquid, air, other | Please state →
Protection class min. IP 23 | Comply and state → | Yes / No
Suitable AC power outlets protected by circuit breaker (state type) | Comply and state → | Yes / No
Insulation to min. IEC 60085 - >155 ° C - (F) or equivalent | Comply and state → | Yes / No
Voltage regulator | Comply and state → | Yes / No
Standard accessories
Fuel tank. Integrated or separate, suitable for continuous operation of min. 8 hours at rated capacity. State capacity, litres. Fuel level gauge. Including all necessary pipework, connections etc. Possibility for connection to external tank. | Comply and state→ | Yes / No
Low oil pressure protection, automatic shut down | Comply and state → | Yes / No
Over heating protection | Comply and state → | Yes / No
Overload protection | Comply and state → | Yes / No
Emergency stop | Comply and state → | Yes / No
Electric starter with key and battery | Comply and state → | Yes / No
Min. Voltmeter, ammeter, hour meter, Hz meter, water temp gauge/indicator (where applicable) | Comply and state → | Yes / No
Earthing/grounding facility | Comply and state → | Yes / No
PV SOLAR POWER SYSTEM STANDARD ARRAY NOMINAL MIN. 4.8 kWp. Battery pack 24 kWh. For Sloped Roof or Gen set mount.
PV solar array
Make and model: | Please state →
Array kWp, min 20% of diesel generator set max output which is 30 kVA/24 kW, hence = 4.8 kWp min. | Comply and state→ | Yes / No
PV panels, total surface covering, m2 | Please state →
Nominal power output each panel, kWp | Please state →
Isc array, A (Amp) | Please state →
Certifications: Any one or more of IEC61215, UL1703 or equivalent | Comply and state → | Yes / No
Charge controller
Make and model: | Please state →
Type: MTTP | Comply and state → | Yes / No
Certifications. Any one or more of EN60730-1/2-11, 55022, 61000-4-27374/5/6 or equivalent | Comply and state→ | Yes / No
Capacity: Isc array +20%, min. | Comply and state→ | Yes / No
Inverter
Make and model: | Please state →
Capacity, A (Amp): Min. equivalent to max load | Comply and state→ | Yes / No
Pure sine curve | Comply and state → | Yes / No
Certifications: Any one or more of EN50178, 62040, 60950, 61000-2/3/6, EN60529, 50438 or equivalent | Comply and state → | Yes / No
Battery package
Make and model: | Please state →
Capacity: Min. equivalent to hybrid diesel gen set full load - 24 kW - for 1 hour = 24 kWh. | Comply and state→ | Yes / No
Battery type: LiFePo4 | Comply and state→ | Yes / No
Certifications,: Any one or more of UL1642, IEC62133, 61000-6-3 or equivalent | Comply and state→ | Yes / No
PV panel racks, brackets, cables, fittings etc.
PV panels racks for sloped roof mount included for all included PV panels, if not attached to the Hybrid Gen set system itself (permanently or fold-out system etc). | Comply and state→ | Yes / No
All cables, junctions, contacts, breakers, earthing spears, fittings, screws, nut and bots etc included | Comply and state → | Yes / No
Installation
The system must be plug and play. Inverter, charge controller, battery package, battery charger must be pre-installed and wired either inside one common Hybrid system cage or in a separate cabinet, in order to easily connect the PV array and the local installation. All cables for establishing the PV array must be readily available with pre-installed connections and clearly marked in a way that no mistakes can occur. | Comply and state → | Yes / No
Other
Lifting points for handling | Comply and state → | Yes / No
Installation instructions, drawings, photos, brochures etc. English/French/Spanish | Comply and state → | Yes / No
Operators and maintenance manual, English/French/Spanish | Comply and state → | Yes / No
Tool kit | Comply and state → | Yes / No
Basic maintenance kit, engine: Min. 4 x oil filters, 2 x air filters, 2 x fuel filters | Comply and state → | Yes / No
Dimensions, L x W x H, mm | Please state →
Weight, dry, entire hybrid system incl. Battery package and all PV panels, cables, brackets etc etc.: kg: | Please state →
WARRANTY
Diesel Generator set: 2 years/2500 hours of operation which ever occur first. PV panels: Min. 10 years. Min. 90% performance guarantee at 10 years. Min. 80% performance guarantee at 20 years. Battery package: Min. 5 years. Inverter/charge controller/charger: Min. 4 years. Other equipment: Min. 2 years | Comply and state → | Yes / No
Sustainability
The bidder must demonstrate that its organisation has an environmental management system in place which as a minimum shall submit at least one or more of the following : the environmental policy principles of the organisation; the management measures and procedures taken or that will be taken to assess, monitor, measure and mitigate environmental impacts of the business processes/products associated with the execution of the contract; how attention is paid to the awareness and training/competency of employee(s) and supplier(s) with regard to dealing with the environmental aspects relevant to this bid; and that compliance with the environmental legislation applicable to the required performance(s) is guaranteed, ISO 14001 certificate, EMAS or an equivalent certificate | Comply and state → | Yes / No
The bidder shall provide documentation which outlines their approach to ensuring equal opportunity, diversity and inclusion within their organisation (e.g. equal pay policy, parental leave, ratio of females/males employees, % of female in management positions, grievances disaggregated by gender, transparency of promotion criteria, sexual harassment policies) | Comply and state → | Yes / No
Mandatory Options
Diesel engine spare parts & maintenance kit for min. 2500 hours of operation | Mandatory | enter prices on Form C: Price Schedule
Sound insolating and water proof canopy (max. 70 dB(A) at 7 m) | Mandatory | enter prices on Form C: Price Schedule
Work shop manual | Mandatory | enter prices on Form C: Price Schedule
Spare parts catalogue | Mandatory | enter prices on Form C: Price Schedule
60 Hz version of Generator set, please enter any surcharge to the std 50 Hz version offered above | Mandatory | enter prices on Form C: Price Schedule
Suggested Options
Heavy duty air filter for dusty conditions | Please provide price or state STD→ | Submit other option prices on a separate form
Heavy duty fuel filter/additional fuel filter in line with original | Please provide price or state STD→ | Submit other option prices on a separate form
Additional silencer, state dB(A) at 1 m and/or 7 m | Please provide price or state STD→ | Submit other option prices on a separate form
High chimney for exhaust, state height and materials | Please provide price or state STD→ | Submit other option prices on a separate form
(ATS) Automatic Transfer Switch | Please provide price or state STD→ | Submit other option prices on a separate form
Over speed protection | Please provide price or state STD→ | Submit other option prices on a separate form
Manual transfer switch | Please provide price or state STD→ | Submit other option prices on a separate form
External fuel tank with pipes including min.. 10 meter non-corrosive material and fittings, state volume of tank and material | Please provide price or state STD→ | Submit other option prices on a separate form
Slow moving trolley/trailer | Please provide price or state STD→ | Submit other option prices on a separate form
(AMF) Automatic Mains Failure Power generation set | Please provide price or state STD→ | Submit other option prices on a separate form
Automatic main circuit breaker | Please provide price or state STD→ | Submit other option prices on a separate form
Installation instructions and eventual. drawings, other languages | Please provide price or state STD→ | Submit other option prices on a separate form
Change over switch positions for: 1) Mains 2) Off 3) GENERATOR SET | Please provide price or state STD→ | Submit other option prices on a separate form
Automatic main circuit breaker | Please provide price or state STD→ | Submit other option prices on a separate form
Operators and maintenance manual, other languages | Please provide price or state STD→ | Submit other option prices on a separate form
Operators and maintenance manual, other languages | Please provide price or state STD→ | Submit other option prices on a separate form

## 3. 30 kVA PV 40% Roof
Bidder name:
Make and model:
Lot 3. 30 kVA PV 40% Sloped Roof or Gen set mount.
HYBRID PV SOLAR/DIESEL GENERATOR SET SPECS | UNOPS REQUIREMENTS | Bidder: Compliant/Non-compliant to UNOPS requirements? Please mark YES/NO in this coloumn. Not indicating YES/NO in this column may render your bid non-compliant. | Bidders are required to provide information in this column on the specifications of their bid to demonstrate compliance to set specifications. Not providing specifications under this column may render your bid non-compliant.
Complete Hybrid PV solar/diesel generator set for autonomous operation, including PV solar power array, battery package, inverter and charge controller. Diesel engine, alternator, control panel with monitoring gauges/indicators, starting equipment, fuel tank as well as other accessories. Charger to charge battery package by diesel gen set and PV solar system interface between diesel gen set and PV solar power unit for a smooth operation for the two energy sources in conjunction, automatically without any manual intervention. Factory test certificates must be included and must be in accordance to internationally recognised standards. Suitable for tropical conditions. | Comply and state → | Yes / No
KEY DATA
Make | Please state →
Model | Please state →
Country of origin | Please state →
DIESEL GEN SET
Rated power output, min. 30 kVA | Comply and state → | Yes / No
Power factor: 0.8 | Comply and state → | Yes / No
Rated power output, 24 kW, min. | Comply and state → | Yes / No
Voltage, 220/230/240 and 380/400 V | Comply and state → | Yes / No
Phase: 1 and 3 | Comply and state → | Yes / No
AC frequency, 50/60 Hz | Comply and state → | Yes / No
Speed: rpm 1500 or 3000 or other | Please state →
Prime power according to ISO 8528 or equivalent, i.e. power available at variable load with no limitations on hours of operation and capable of min. 10% overload for min. 1 hour in any 12 hours. | Comply and state → | Yes / No
Prime rating of min. the stated output rating at Normal Temperature and Pressure conditions (NTP). Please state | Comply and state → | Yes / No
Derating information (temperature, altitude and humidity), please state | Please state →
Engine
Make | Please state →
Model | Please state →
Engine power output, kW at rpm: | Please state →
Fuel: Diesel | Comply and state → | Yes / No
Cooling, liquid or air or combined, suitable for tropical conditions | Please state →
Speed governor, state type | Please state →
Exhaust with suitable piping and residential silencer | Comply and state → | Yes / No
Noise level, dB(A) at 1 m (silencer fitted) | Please state →
Fuel consumption at 75% load: L/hour | Please state →
CO2 emissions at 75% load: g/hour | Please state →
Mounted on anti-vibration mounts | Comply and state → | Yes / No
ENVIRONMENTAL
EU Non-road emissions regulations schedule, e.g. EU STAGE II, III A, III B, IV. US Non-road and stationary emissions regulations to Tier 1,2,3,4 or equivalent. Please state. | Comply and state → | Yes / No
Alternator
Make: | Please state →
Model: | Please state →
Brushless type | Comply and state → | Yes / No
Cooling, liquid, air, other | Please state →
Protection class min. IP 23 | Comply and state → | Yes / No
Suitable AC power outlets protected by circuit breaker (state type) | Comply and state → | Yes / No
Insulation to min. IEC 60085 - >155 ° C - (F) or equivalent | Comply and state → | Yes / No
Voltage regulator | Comply and state → | Yes / No
Standard accessories
Fuel tank. Integrated or separate, suitable for continuous operation of min. 8 hours at rated capacity. State capacity, litres. Fuel level gauge. Including all necessary pipework, connections etc. Possibility for connection to external tank. | Comply and state→ | Yes / No
Low oil pressure protection, automatic shut down | Comply and state → | Yes / No
Over heating protection | Comply and state → | Yes / No
Overload protection | Comply and state → | Yes / No
Emergency stop | Comply and state → | Yes / No
Electric starter with key and battery | Comply and state → | Yes / No
Min. Voltmeter, ammeter, hour meter, Hz meter, water temp gauge/indicator (where applicable) | Comply and state → | Yes / No
Earthing/grounding facility | Comply and state → | Yes / No
PV SOLAR POWER SYSTEM STANDARD ARRAY NOMINAL MIN. 9.6 kWp. Battery pack 24 kWh. For Sloped Roof or Gen set mount.
PV solar array
Make and model: | Please state →
Array kWp, min 40% of diesel generator set max output which is 30 kVA/24 kW, hence = 9.6 kWp min. | Comply and state→ | Yes / No
PV panels, total surface covering, m2 | Please state →
Nominal power output each panel, kWp | Please state →
Isc array, A (Amp) | Please state →
Certifications: Any one or more of IEC61215, UL1703 or equivalent | Comply and state → | Yes / No
Charge controller
Make and model: | Please state →
Type: MTTP | Comply and state → | Yes / No
Certifications. Any one or more of EN60730-1/2-11, 55022, 61000-4-27374/5/6 or equivalent | Comply and state→ | Yes / No
Capacity: Isc array +20%, min. | Comply and state→ | Yes / No
Inverter
Make and model: | Please state →
Capacity, A (Amp): Min. equivalent to max load | Comply and state→ | Yes / No
Pure sine curve | Comply and state → | Yes / No
Certifications: Any one or more of EN50178, 62040, 60950, 61000-2/3/6, EN60529, 50438 or equivalent | Comply and state → | Yes / No
Battery package
Make and model: | Please state →
Capacity: Min. equivalent to hybrid diesel gen set full load - 24 kW - for 1 hour = 24 kWh. | Comply and state→ | Yes / No
Battery type: LiFePo4 | Comply and state→ | Yes / No
Certifications,: Any one or more of UL1642, IEC62133, 61000-6-3 or equivalent | Comply and state→ | Yes / No
PV panel racks, brackets, cables, fittings etc.
PV panels racks for sloped roof mount included for all included PV panels, if not attached to the Hybrid Gen set system itself (permanently or fold-out system etc). | Comply and state→ | Yes / No
All cables, junctions, contacts, breakers, earthing spears, fittings, screws, nut and bots etc included | Comply and state → | Yes / No
Installation
The system must be plug and play. Inverter, charge controller, battery package, battery charger must be pre-installed and wired either inside one common Hybrid system cage or in a separate cabinet, in order to easily connect the PV array and the local installation. All cables for establishing the PV array must be readily available with pre-installed connections and clearly marked in a way that no mistakes can occur. | Comply and state → | Yes / No
Other
Lifting points for handling | Comply and state → | Yes / No
Installation instructions, drawings, photos, brochures etc. English/French/Spanish | Comply and state → | Yes / No
Operators and maintenance manual, English/French/Spanish | Comply and state → | Yes / No
Tool kit | Comply and state → | Yes / No
Basic maintenance kit, engine: Min. 4 x oil filters, 2 x air filters, 2 x fuel filters | Comply and state → | Yes / No
Dimensions, L x W x H, mm | Please state →
Weight, dry, entire hybrid system incl. Battery package and all PV panels, cables, brackets etc etc.: kg: | Please state →
WARRANTY
Diesel Generator set: 2 years/2500 hours of operation which ever occur first. PV panels: Min. 10 years. Min. 90% performance guarantee at 10 years. Min. 80% performance guarantee at 20 years. Battery package: Min. 5 years. Inverter/charge controller/charger: Min. 4 years. Other equipment: Min. 2 years | Comply and state → | Yes / No
Sustainability
The bidder must demonstrate that its organisation has an environmental management system in place which as a minimum shall submit at least one or more of the following : the environmental policy principles of the organisation; the management measures and procedures taken or that will be taken to assess, monitor, measure and mitigate environmental impacts of the business processes/products associated with the execution of the contract; how attention is paid to the awareness and training/competency of employee(s) and supplier(s) with regard to dealing with the environmental aspects relevant to this bid; and that compliance with the environmental legislation applicable to the required performance(s) is guaranteed, ISO 14001 certificate, EMAS or an equivalent certificate | Comply and state → | Yes / No
The bidder shall provide documentation which outlines their approach to ensuring equal opportunity, diversity and inclusion within their organisation (e.g. equal pay policy, parental leave, ratio of females/males employees, % of female in management positions, grievances disaggregated by gender, transparency of promotion criteria, sexual harassment policies) | Comply and state → | Yes / No
Mandatory Options
Diesel engine spare parts & maintenance kit for min. 2500 hours of operation | Mandatory | enter prices on Form C: Price Schedule
Sound insolating and water proof canopy (max. 70 dB(A) at 7 m) | Mandatory | enter prices on Form C: Price Schedule
Work shop manual | Mandatory | enter prices on Form C: Price Schedule
Spare parts catalogue | Mandatory | enter prices on Form C: Price Schedule
60 Hz version of Generator set, please enter any surcharge to the std 50 Hz version offered above | Mandatory | enter prices on Form C: Price Schedule
Suggested Options
Heavy duty air filter for dusty conditions | Please provide price or state STD→ | Submit other option prices on a separate form
Heavy duty fuel filter/additional fuel filter in line with original | Please provide price or state STD→ | Submit other option prices on a separate form
Additional silencer, state dB(A) at 1 m and/or 7 m | Please provide price or state STD→ | Submit other option prices on a separate form
High chimney for exhaust, state height and materials | Please provide price or state STD→ | Submit other option prices on a separate form
(ATS) Automatic Transfer Switch | Please provide price or state STD→ | Submit other option prices on a separate form
Over speed protection | Please provide price or state STD→ | Submit other option prices on a separate form
Manual transfer switch | Please provide price or state STD→ | Submit other option prices on a separate form
External fuel tank with pipes including min.. 10 meter non-corrosive material and fittings, state volume of tank and material | Please provide price or state STD→ | Submit other option prices on a separate form
Slow moving trolley/trailer | Please provide price or state STD→ | Submit other option prices on a separate form
(AMF) Automatic Mains Failure Power generation set | Please provide price or state STD→ | Submit other option prices on a separate form
Automatic main circuit breaker | Please provide price or state STD→ | Submit other option prices on a separate form
Installation instructions and eventual. drawings, other languages | Please provide price or state STD→ | Submit other option prices on a separate form
Change over switch positions for: 1) Mains 2) Off 3) GENERATOR SET | Please provide price or state STD→ | Submit other option prices on a separate form
Automatic main circuit breaker | Please provide price or state STD→ | Submit other option prices on a separate form
Operators and maintenance manual, other languages | Please provide price or state STD→ | Submit other option prices on a separate form

## 4. 30 kVA PV 10% Ground
Bidder name:
Make and model:
Lot 4. 30 kVA PV 10% Ground or flat roof mounted
HYBRID PV SOLAR/DIESEL GENERATOR SET SPECS | UNOPS REQUIREMENTS | Bidder: Compliant/Non-compliant to UNOPS requirements? Please mark YES/NO in this coloumn. Not indicating YES/NO in this column may render your bid non-compliant. | Bidders are required to provide information in this column on the specifications of their bid to demonstrate compliance to set specifications. Not providing specifications under this column may render your bid non-compliant.
Complete Hybrid PV solar/diesel generator set for autonomous operation, including PV solar power array, battery package, inverter and charge controller. Diesel engine, alternator, control panel with monitoring gauges/indicators, starting equipment, fuel tank as well as other accessories. Charger to charge battery package by diesel gen set and PV solar system interface between diesel gen set and PV solar power unit for a smooth operation for the two energy sources in conjunction, automatically without any manual intervention. Factory test certificates must be included and must be in accordance to internationally recognised standards. Suitable for tropical conditions. | Comply and state → | Yes / No
KEY DATA
Make | Please state →
Model | Please state →
Country of origin | Please state →
DIESEL GEN SET
Rated power output, min. 30 kVA | Comply and state → | Yes / No
Power factor: 0.8 | Comply and state → | Yes / No
Rated power output, 24 kW, min. | Comply and state → | Yes / No
Voltage, 220/230/240 and 380/400 V | Comply and state → | Yes / No
Phase: 1 and 3 | Comply and state → | Yes / No
AC frequency, 50/60 Hz | Comply and state → | Yes / No
Speed: rpm 1500 or 3000 or other | Please state →
Prime power according to ISO 8528 or equivalent, i.e. power available at variable load with no limitations on hours of operation and capable of min. 10% overload for min. 1 hour in any 12 hours. | Comply and state → | Yes / No
Prime rating of min. the stated output rating at Normal Temperature and Pressure conditions (NTP). Please state | Comply and state → | Yes / No
Derating information (temperature, altitude and humidity), please state | Please state →
Engine
Make | Please state →
Model | Please state →
Engine power output, kW at rpm: | Please state →
Fuel: Diesel | Comply and state → | Yes / No
Cooling, liquid or air or combined, suitable for tropical conditions | Please state →
Speed governor, state type | Please state →
Exhaust with suitable piping and residential silencer | Comply and state → | Yes / No
Noise level, dB(A) at 1 m (silencer fitted) | Please state →
Fuel consumption at 75% load: L/hour | Please state →
CO2 emissions at 75% load: g/hour | Please state →
Mounted on anti-vibration mounts | Comply and state → | Yes / No
ENVIRONMENTAL
EU Non-road emissions regulations schedule, e.g. EU STAGE II, III A, III B, IV. US Non-road and stationary emissions regulations to Tier 1,2,3,4 or equivalent. Please state. | Comply and state → | Yes / No
Alternator
Make: | Please state →
Model: | Please state →
Brushless type | Comply and state → | Yes / No
Cooling, liquid, air, other | Please state →
Protection class min. IP 23 | Comply and state → | Yes / No
Suitable AC power outlets protected by circuit breaker (state type) | Comply and state → | Yes / No
Insulation to min. IEC 60085 - >155 ° C - (F) or equivalent | Comply and state → | Yes / No
Voltage regulator | Comply and state → | Yes / No
Standard accessories
Fuel tank. Integrated or separate, suitable for continuous operation of min. 8 hours at rated capacity. State capacity, litres. Fuel level gauge. Including all necessary pipework, connections etc. Possibility for connection to external tank. | Comply and state→ | Yes / No
Low oil pressure protection, automatic shut down | Comply and state → | Yes / No
Over heating protection | Comply and state → | Yes / No
Overload protection | Comply and state → | Yes / No
Emergency stop | Comply and state → | Yes / No
Electric starter with key and battery | Comply and state → | Yes / No
Min. Voltmeter, ammeter, hour meter, Hz meter, water temp gauge/indicator (where applicable) | Comply and state → | Yes / No
Earthing/grounding facility | Comply and state → | Yes / No
PV SOLAR POWER SYSTEM STANDARD ARRAY NOMINAL MIN. 2.4 kWp. Battery pack 24 kWh. For Ground or flat roof mount
PV solar array
Make and model: | Please state →
Array kWp, min 10% of diesel generator set max output which is 30 kVA/24 kW, hence = 2.4kWp min. | Comply and state→ | Yes / No
PV panels, total surface covering, m2 | Please state →
Nominal power output each panel, kWp | Please state →
Isc array, A (Amp) | Please state →
Certifications: Any one or more of IEC61215, UL1703 or equivalent | Comply and state → | Yes / No
Charge controller
Make and model: | Please state →
Type: MTTP | Comply and state → | Yes / No
Certifications. Any one or more of EN60730-1/2-11, 55022, 61000-4-27374/5/6 or equivalent | Comply and state→ | Yes / No
Capacity: Isc array +20%, min. | Comply and state→ | Yes / No
Inverter
Make and model: | Please state →
Capacity, A (Amp): Min. equivalent to max load | Comply and state→ | Yes / No
Pure sine curve | Comply and state → | Yes / No
Certifications: Any one or more of EN50178, 62040, 60950, 61000-2/3/6, EN60529, 50438 or equivalent | Comply and state → | Yes / No
Battery package
Make and model: | Please state →
Capacity: Min. equivalent to hybrid diesel gen set full load - 24 kW - for 1 hour = 24 kWh. | Comply and state→ | Yes / No
Battery type: LiFePo4 | Comply and state→ | Yes / No
Certifications,: Any one or more of UL1642, IEC62133, 61000-6-3 or equivalent | Comply and state→ | Yes / No
PV panel racks, brackets, cables, fittings etc.
PV panels racks for Ground or flat roof mount. | Comply and state→ | Yes / No
All cables, junctions, contacts, breakers, earthing spears, fittings, screws, nut and bots etc included | Comply and state → | Yes / No
Installation
The system must be plug and play. Inverter, charge controller, battery package, battery charger must be pre-installed and wired either inside one common Hybrid system cage or in a separate cabinet, in order to easily connect the PV array and the local installation. All cables for establishing the PV array must be readily available with pre-installed connections and clearly marked in a way that no mistakes can occur. | Comply and state → | Yes / No
Other
Lifting points for handling | Comply and state → | Yes / No
Installation instructions, drawings, photos, brochures etc. English/French/Spanish | Comply and state → | Yes / No
Operators and maintenance manual, English/French/Spanish | Comply and state → | Yes / No
Tool kit | Comply and state → | Yes / No
Basic maintenance kit, engine: Min. 4 x oil filters, 2 x air filters, 2 x fuel filters | Comply and state → | Yes / No
Dimensions, L x W x H, mm | Please state →
Weight, dry, entire hybrid system incl. Battery package and all PV panels, cables, brackets etc etc.: kg: | Please state →
WARRANTY
Diesel Generator set: 2 years/2500 hours of operation which ever occur first. PV panels: Min. 10 years. Min. 90% performance guarantee at 10 years. Min. 80% performance guarantee at 20 years. Battery package: Min. 5 years. Inverter/charge controller/charger: Min. 4 years. Other equipment: Min. 2 years | Comply and state → | Yes / No
Sustainability
The bidder must demonstrate that its organisation has an environmental management system in place which as a minimum shall submit at least one or more of the following : the environmental policy principles of the organisation; the management measures and procedures taken or that will be taken to assess, monitor, measure and mitigate environmental impacts of the business processes/products associated with the execution of the contract; how attention is paid to the awareness and training/competency of employee(s) and supplier(s) with regard to dealing with the environmental aspects relevant to this bid; and that compliance with the environmental legislation applicable to the required performance(s) is guaranteed, ISO 14001 certificate, EMAS or an equivalent certificate | Comply and state → | Yes / No
The bidder shall provide documentation which outlines their approach to ensuring equal opportunity, diversity and inclusion within their organisation (e.g. equal pay policy, parental leave, ratio of females/males employees, % of female in management positions, grievances disaggregated by gender, transparency of promotion criteria, sexual harassment policies) | Comply and state → | Yes / No
Mandatory Options
Diesel engine spare parts & maintenance kit for min. 2500 hours of operation | Mandatory | enter prices on Form C: Price Schedule
Sound insolating and water proof canopy (max. 70 dB(A) at 7 m) | Mandatory | enter prices on Form C: Price Schedule
Work shop manual | Mandatory | enter prices on Form C: Price Schedule
Spare parts catalogue | Mandatory | enter prices on Form C: Price Schedule
60 Hz version of Generator set, please enter any surcharge to the std 50 Hz version offered above | Mandatory | enter prices on Form C: Price Schedule
Suggested Options
Heavy duty air filter for dusty conditions | Please provide price or state STD→ | Submit other option prices on a separate form
Heavy duty fuel filter/additional fuel filter in line with original | Please provide price or state STD→ | Submit other option prices on a separate form
Additional silencer, state dB(A) at 1 m and/or 7 m | Please provide price or state STD→ | Submit other option prices on a separate form
High chimney for exhaust, state height and materials | Please provide price or state STD→ | Submit other option prices on a separate form
(ATS) Automatic Transfer Switch | Please provide price or state STD→ | Submit other option prices on a separate form
Over speed protection | Please provide price or state STD→ | Submit other option prices on a separate form
Manual transfer switch | Please provide price or state STD→ | Submit other option prices on a separate form
External fuel tank with pipes including min.. 10 meter non-corrosive material and fittings, state volume of tank and material | Please provide price or state STD→ | Submit other option prices on a separate form
Slow moving trolley/trailer | Please provide price or state STD→ | Submit other option prices on a separate form
(AMF) Automatic Mains Failure Power generation set | Please provide price or state STD→ | Submit other option prices on a separate form
Automatic main circuit breaker | Please provide price or state STD→ | Submit other option prices on a separate form
Installation instructions and eventual. drawings, other languages | Please provide price or state STD→ | Submit other option prices on a separate form
Change over switch positions for: 1) Mains 2) Off 3) GENERATOR SET | Please provide price or state STD→ | Submit other option prices on a separate form
Automatic main circuit breaker | Please provide price or state STD→ | Submit other option prices on a separate form
Operators and maintenance manual, other languages | Please provide price or state STD→ | Submit other option prices on a separate form

## 5. 30 kVA PV 20% Ground
Bidder name:
Make and model:
Lot 5. 30 kVA PV 20% Ground or flat roof mounted
HYBRID PV SOLAR/DIESEL GENERATOR SET SPECS | UNOPS REQUIREMENTS | Bidder: Compliant/Non-compliant to UNOPS requirements? Please mark YES/NO in this coloumn. Not indicating YES/NO in this column may render your bid non-compliant. | Bidders are required to provide information in this column on the specifications of their bid to demonstrate compliance to set specifications. Not providing specifications under this column may render your bid non-compliant.
Complete Hybrid PV solar/diesel generator set for autonomous operation, including PV solar power array, battery package, inverter and charge controller. Diesel engine, alternator, control panel with monitoring gauges/indicators, starting equipment, fuel tank as well as other accessories. Charger to charge battery package by diesel gen set and PV solar system interface between diesel gen set and PV solar power unit for a smooth operation for the two energy sources in conjunction, automatically without any manual intervention. Factory test certificates must be included and must be in accordance to internationally recognised standards. Suitable for tropical conditions. | Comply and state → | Yes / No
KEY DATA
Make | Please state →
Model | Please state →
Country of origin | Please state →
DIESEL GEN SET
Rated power output, min. 30 kVA | Comply and state → | Yes / No
Power factor: 0.8 | Comply and state → | Yes / No
Rated power output, 24 kW, min. | Comply and state → | Yes / No
Voltage, 220/230/240 and 380/400 V | Comply and state → | Yes / No
Phase: 1 and 3 | Comply and state → | Yes / No
AC frequency, 50/60 Hz | Comply and state → | Yes / No
Speed: rpm 1500 or 3000 or other | Please state →
Prime power according to ISO 8528 or equivalent, i.e. power available at variable load with no limitations on hours of operation and capable of min. 10% overload for min. 1 hour in any 12 hours. | Comply and state → | Yes / No
Prime rating of min. the stated output rating at Normal Temperature and Pressure conditions (NTP). Please state | Comply and state → | Yes / No
Derating information (temperature, altitude and humidity), please state | Please state →
Engine
Make | Please state →
Model | Please state →
Engine power output, kW at rpm: | Please state →
Fuel: Diesel | Comply and state → | Yes / No
Cooling, liquid or air or combined, suitable for tropical conditions | Please state →
Speed governor, state type | Please state →
Exhaust with suitable piping and residential silencer | Comply and state → | Yes / No
Noise level, dB(A) at 1 m (silencer fitted) | Please state →
Fuel consumption at 75% load: L/hour | Please state →
CO2 emissions at 75% load: g/hour | Please state →
Mounted on anti-vibration mounts | Comply and state → | Yes / No
ENVIRONMENTAL
EU Non-road emissions regulations schedule, e.g. EU STAGE II, III A, III B, IV. US Non-road and stationary emissions regulations to Tier 1,2,3,4 or equivalent. Please state. | Comply and state → | Yes / No
Alternator
Make: | Please state →
Model: | Please state →
Brushless type | Comply and state → | Yes / No
Cooling, liquid, air, other | Please state →
Protection class min. IP 23 | Comply and state → | Yes / No
Suitable AC power outlets protected by circuit breaker (state type) | Comply and state → | Yes / No
Insulation to min. IEC 60085 - >155 ° C - (F) or equivalent | Comply and state → | Yes / No
Voltage regulator | Comply and state → | Yes / No
Standard accessories
Fuel tank. Integrated or separate, suitable for continuous operation of min. 8 hours at rated capacity. State capacity, litres. Fuel level gauge. Including all necessary pipework, connections etc. Possibility for connection to external tank. | Comply and state→ | Yes / No
Low oil pressure protection, automatic shut down | Comply and state → | Yes / No
Over heating protection | Comply and state → | Yes / No
Overload protection | Comply and state → | Yes / No
Emergency stop | Comply and state → | Yes / No
Electric starter with key and battery | Comply and state → | Yes / No
Min. Voltmeter, ammeter, hour meter, Hz meter, water temp gauge/indicator (where applicable) | Comply and state → | Yes / No
Earthing/grounding facility | Comply and state → | Yes / No
PV SOLAR POWER SYSTEM STANDARD ARRAY NOMINAL MIN. 4.8 kWp. Battery pack 24 kWh. For Ground or flat roof mount
PV solar array
Make and model: | Please state →
Array kWp, min 20% of diesel generator set max output which is 30 kVA/24 kW, hence = 4.8 kWp min. | Comply and state→ | Yes / No
PV panels, total surface covering, m2 | Please state →
Nominal power output each panel, kWp | Please state →
Isc array, A (Amp) | Please state →
Certifications: Any one or more of IEC61215, UL1703 or equivalent | Comply and state → | Yes / No
Charge controller
Make and model: | Please state →
Type: MTTP | Comply and state → | Yes / No
Certifications. Any one or more of EN60730-1/2-11, 55022, 61000-4-27374/5/6 or equivalent | Comply and state→ | Yes / No
Capacity: Isc array +20%, min. | Comply and state→ | Yes / No
Inverter
Make and model: | Please state →
Capacity, A (Amp): Min. equivalent to max load | Comply and state→ | Yes / No
Pure sine curve | Comply and state → | Yes / No
Certifications: Any one or more of EN50178, 62040, 60950, 61000-2/3/6, EN60529, 50438 or equivalent | Comply and state → | Yes / No
Battery package
Make and model: | Please state →
Capacity: Min. equivalent to hybrid diesel gen set full load - 24 kW - for 1 hour = 24 kWh. | Comply and state→ | Yes / No
Battery type: LiFePo4 | Comply and state→ | Yes / No
Certifications,: Any one or more of UL1642, IEC62133, 61000-6-3 or equivalent | Comply and state→ | Yes / No
PV panel racks, brackets, cables, fittings etc.
PV panels racks for Ground or flat roof mount. | Comply and state→ | Yes / No
All cables, junctions, contacts, breakers, earthing spears, fittings, screws, nut and bots etc included | Comply and state → | Yes / No
Installation
The system must be plug and play. Inverter, charge controller, battery package, battery charger must be pre-installed and wired either inside one common Hybrid system cage or in a separate cabinet, in order to easily connect the PV array and the local installation. All cables for establishing the PV array must be readily available with pre-installed connections and clearly marked in a way that no mistakes can occur. | Comply and state → | Yes / No
Other
Lifting points for handling | Comply and state → | Yes / No
Installation instructions, drawings, photos, brochures etc. English/French/Spanish | Comply and state → | Yes / No
Operators and maintenance manual, English/French/Spanish | Comply and state → | Yes / No
Tool kit | Comply and state → | Yes / No
Basic maintenance kit, engine: Min. 4 x oil filters, 2 x air filters, 2 x fuel filters | Comply and state → | Yes / No
Dimensions, L x W x H, mm | Please state →
Weight, dry, entire hybrid system incl. Battery package and all PV panels, cables, brackets etc etc.: kg: | Please state →
WARRANTY
Diesel Generator set: 2 years/2500 hours of operation which ever occur first. PV panels: Min. 10 years. Min. 90% performance guarantee at 10 years. Min. 80% performance guarantee at 20 years. Battery package: Min. 5 years. Inverter/charge controller/charger: Min. 4 years. Other equipment: Min. 2 years | Comply and state → | Yes / No
Sustainability
The bidder must demonstrate that its organisation has an environmental management system in place which as a minimum shall submit at least one or more of the following : the environmental policy principles of the organisation; the management measures and procedures taken or that will be taken to assess, monitor, measure and mitigate environmental impacts of the business processes/products associated with the execution of the contract; how attention is paid to the awareness and training/competency of employee(s) and supplier(s) with regard to dealing with the environmental aspects relevant to this bid; and that compliance with the environmental legislation applicable to the required performance(s) is guaranteed, ISO 14001 certificate, EMAS or an equivalent certificate | Comply and state → | Yes / No
The bidder shall provide documentation which outlines their approach to ensuring equal opportunity, diversity and inclusion within their organisation (e.g. equal pay policy, parental leave, ratio of females/males employees, % of female in management positions, grievances disaggregated by gender, transparency of promotion criteria, sexual harassment policies) | Comply and state → | Yes / No
Mandatory Options
Diesel engine spare parts & maintenance kit for min. 2500 hours of operation | Mandatory | enter prices on Form C: Price Schedule
Sound insolating and water proof canopy (max. 70 dB(A) at 7 m) | Mandatory | enter prices on Form C: Price Schedule
Work shop manual | Mandatory | enter prices on Form C: Price Schedule
Spare parts catalogue | Mandatory | enter prices on Form C: Price Schedule
60 Hz version of Generator set, please enter any surcharge to the std 50 Hz version offered above | Mandatory | enter prices on Form C: Price Schedule
Suggested Options
Heavy duty air filter for dusty conditions | Please provide price or state STD→ | Submit other option prices on a separate form
Heavy duty fuel filter/additional fuel filter in line with original | Please provide price or state STD→ | Submit other option prices on a separate form
Additional silencer, state dB(A) at 1 m and/or 7 m | Please provide price or state STD→ | Submit other option prices on a separate form
High chimney for exhaust, state height and materials | Please provide price or state STD→ | Submit other option prices on a separate form
(ATS) Automatic Transfer Switch | Please provide price or state STD→ | Submit other option prices on a separate form
Over speed protection | Please provide price or state STD→ | Submit other option prices on a separate form
Manual transfer switch | Please provide price or state STD→ | Submit other option prices on a separate form
External fuel tank with pipes including min.. 10 meter non-corrosive material and fittings, state volume of tank and material | Please provide price or state STD→ | Submit other option prices on a separate form
Slow moving trolley/trailer | Please provide price or state STD→ | Submit other option prices on a separate form
(AMF) Automatic Mains Failure Power generation set | Please provide price or state STD→ | Submit other option prices on a separate form
Automatic main circuit breaker | Please provide price or state STD→ | Submit other option prices on a separate form
Installation instructions and eventual. drawings, other languages | Please provide price or state STD→ | Submit other option prices on a separate form
Change over switch positions for: 1) Mains 2) Off 3) GENERATOR SET | Please provide price or state STD→ | Submit other option prices on a separate form
Automatic main circuit breaker | Please provide price or state STD→ | Submit other option prices on a separate form
Operators and maintenance manual, other languages | Please provide price or state STD→ | Submit other option prices on a separate form

## 6. 30 kVA PV 40% Ground
Bidder name:
Make and model:
Lot 6. 30 kVA PV 40% Ground or flat roof mounted
HYBRID PV SOLAR/DIESEL GENERATOR SET SPECS | UNOPS REQUIREMENTS | Bidder: Compliant/Non-compliant to UNOPS requirements? Please mark YES/NO in this coloumn. Not indicating YES/NO in this column may render your bid non-compliant. | Bidders are required to provide information in this column on the specifications of their bid to demonstrate compliance to set specifications. Not providing specifications under this column may render your bid non-compliant.
Complete Hybrid PV solar/diesel generator set for autonomous operation, including PV solar power array, battery package, inverter and charge controller. Diesel engine, alternator, control panel with monitoring gauges/indicators, starting equipment, fuel tank as well as other accessories. Charger to charge battery package by diesel gen set and PV solar system interface between diesel gen set and PV solar power unit for a smooth operation for the two energy sources in conjunction, automatically without any manual intervention. Factory test certificates must be included and must be in accordance to internationally recognised standards. Suitable for tropical conditions. | Comply and state → | Yes / No
KEY DATA
Make | Please state →
Model | Please state →
Country of origin | Please state →
DIESEL GEN SET
Rated power output, min. 30 kVA | Comply and state → | Yes / No
Power factor: 0.8 | Comply and state → | Yes / No
Rated power output, 24 kW, min. | Comply and state → | Yes / No
Voltage, 220/230/240 and 380/400 V | Comply and state → | Yes / No
Phase: 1 and 3 | Comply and state → | Yes / No
AC frequency, 50/60 Hz | Comply and state → | Yes / No
Speed: rpm 1500 or 3000 or other | Please state →
Prime power according to ISO 8528 or equivalent, i.e. power available at variable load with no limitations on hours of operation and capable of min. 10% overload for min. 1 hour in any 12 hours. | Comply and state → | Yes / No
Prime rating of min. the stated output rating at Normal Temperature and Pressure conditions (NTP). Please state | Comply and state → | Yes / No
Derating information (temperature, altitude and humidity), please state | Please state →
Engine
Make | Please state →
Model | Please state →
Engine power output, kW at rpm: | Please state →
Fuel: Diesel | Comply and state → | Yes / No
Cooling, liquid or air or combined, suitable for tropical conditions | Please state →
Speed governor, state type | Please state →
Exhaust with suitable piping and residential silencer | Comply and state → | Yes / No
Noise level, dB(A) at 1 m (silencer fitted) | Please state →
Fuel consumption at 75% load: L/hour | Please state →
CO2 emissions at 75% load: g/hour | Please state →
Mounted on anti-vibration mounts | Comply and state → | Yes / No
ENVIRONMENTAL
EU Non-road emissions regulations schedule, e.g. EU STAGE II, III A, III B, IV. US Non-road and stationary emissions regulations to Tier 1,2,3,4 or equivalent. Please state. | Comply and state → | Yes / No
Alternator
Make: | Please state →
Model: | Please state →
Brushless type | Comply and state → | Yes / No
Cooling, liquid, air, other | Please state →
Protection class min. IP 23 | Comply and state → | Yes / No
Suitable AC power outlets protected by circuit breaker (state type) | Comply and state → | Yes / No
Insulation to min. IEC 60085 - >155 ° C - (F) or equivalent | Comply and state → | Yes / No
Voltage regulator | Comply and state → | Yes / No
Standard accessories
Fuel tank. Integrated or separate, suitable for continuous operation of min. 8 hours at rated capacity. State capacity, litres. Fuel level gauge. Including all necessary pipework, connections etc. Possibility for connection to external tank. | Comply and state→ | Yes / No
Low oil pressure protection, automatic shut down | Comply and state → | Yes / No
Over heating protection | Comply and state → | Yes / No
Overload protection | Comply and state → | Yes / No
Emergency stop | Comply and state → | Yes / No
Electric starter with key and battery | Comply and state → | Yes / No
Min. Voltmeter, ammeter, hour meter, Hz meter, water temp gauge/indicator (where applicable) | Comply and state → | Yes / No
Earthing/grounding facility | Comply and state → | Yes / No
PV SOLAR POWER SYSTEM STANDARD ARRAY NOMINAL MIN. 9.6 kWp. Battery pack 24 kWh. For Ground or flat roof mount
PV solar array
Make and model: | Please state →
Array kWp, min 40% of diesel generator set max output which is 30 kVA/24 kW, hence = 9.6 kWp min. | Comply and state→ | Yes / No
PV panels, total surface covering, m2 | Please state →
Nominal power output each panel, kWp | Please state →
Isc array, A (Amp) | Please state →
Certifications: Any one or more of IEC61215, UL1703 or equivalent | Comply and state → | Yes / No
Charge controller
Make and model: | Please state →
Type: MTTP | Comply and state → | Yes / No
Certifications. Any one or more of EN60730-1/2-11, 55022, 61000-4-27374/5/6 or equivalent | Comply and state→ | Yes / No
Capacity: Isc array +20%, min. | Comply and state→ | Yes / No
Inverter
Make and model: | Please state →
Capacity, A (Amp): Min. equivalent to max load | Comply and state→ | Yes / No
Pure sine curve | Comply and state → | Yes / No
Certifications: Any one or more of EN50178, 62040, 60950, 61000-2/3/6, EN60529, 50438 or equivalent | Comply and state → | Yes / No
Battery package
Make and model: | Please state →
Capacity: Min. equivalent to hybrid diesel gen set full load - 24 kW - for 1 hour = 24 kWh. | Comply and state→ | Yes / No
Battery type: LiFePo4 | Comply and state→ | Yes / No
Certifications,: Any one or more of UL1642, IEC62133, 61000-6-3 or equivalent | Comply and state→ | Yes / No
PV panel racks, brackets, cables, fittings etc.
PV panels racks for Ground or flat roof mount. | Comply and state→ | Yes / No
All cables, junctions, contacts, breakers, earthing spears, fittings, screws, nut and bots etc included | Comply and state → | Yes / No
Installation
The system must be plug and play. Inverter, charge controller, battery package, battery charger must be pre-installed and wired either inside one common Hybrid system cage or in a separate cabinet, in order to easily connect the PV array and the local installation. All cables for establishing the PV array must be readily available with pre-installed connections and clearly marked in a way that no mistakes can occur. | Comply and state → | Yes / No
Other
Lifting points for handling | Comply and state → | Yes / No
Installation instructions, drawings, photos, brochures etc. English/French/Spanish | Comply and state → | Yes / No
Operators and maintenance manual, English/French/Spanish | Comply and state → | Yes / No
Tool kit | Comply and state → | Yes / No
Basic maintenance kit, engine: Min. 4 x oil filters, 2 x air filters, 2 x fuel filters | Comply and state → | Yes / No
Dimensions, L x W x H, mm | Please state →
Weight, dry, entire hybrid system incl. Battery package and all PV panels, cables, brackets etc etc.: kg: | Please state →
WARRANTY
Diesel Generator set: 2 years/2500 hours of operation which ever occur first. PV panels: Min. 10 years. Min. 90% performance guarantee at 10 years. Min. 80% performance guarantee at 20 years. Battery package: Min. 5 years. Inverter/charge controller/charger: Min. 4 years. Other equipment: Min. 2 years | Comply and state → | Yes / No
Sustainability
The bidder must demonstrate that its organisation has an environmental management system in place which as a minimum shall submit at least one or more of the following : the environmental policy principles of the organisation; the management measures and procedures taken or that will be taken to assess, monitor, measure and mitigate environmental impacts of the business processes/products associated with the execution of the contract; how attention is paid to the awareness and training/competency of employee(s) and supplier(s) with regard to dealing with the environmental aspects relevant to this bid; and that compliance with the environmental legislation applicable to the required performance(s) is guaranteed, ISO 14001 certificate, EMAS or an equivalent certificate | Comply and state → | Yes / No
The bidder shall provide documentation which outlines their approach to ensuring equal opportunity, diversity and inclusion within their organisation (e.g. equal pay policy, parental leave, ratio of females/males employees, % of female in management positions, grievances disaggregated by gender, transparency of promotion criteria, sexual harassment policies) | Comply and state → | Yes / No
Mandatory Options
Diesel engine spare parts & maintenance kit for min. 2500 hours of operation | Mandatory | enter prices on Form C: Price Schedule
Sound insolating and water proof canopy (max. 70 dB(A) at 7 m) | Mandatory | enter prices on Form C: Price Schedule
Work shop manual | Mandatory | enter prices on Form C: Price Schedule
Spare parts catalogue | Mandatory | enter prices on Form C: Price Schedule
60 Hz version of Generator set, please enter any surcharge to the std 50 Hz version offered above | Mandatory | enter prices on Form C: Price Schedule
Suggested Options
Heavy duty air filter for dusty conditions | Please provide price or state STD→ | Submit other option prices on a separate form
Heavy duty fuel filter/additional fuel filter in line with original | Please provide price or state STD→ | Submit other option prices on a separate form
Additional silencer, state dB(A) at 1 m and/or 7 m | Please provide price or state STD→ | Submit other option prices on a separate form
High chimney for exhaust, state height and materials | Please provide price or state STD→ | Submit other option prices on a separate form
(ATS) Automatic Transfer Switch | Please provide price or state STD→ | Submit other option prices on a separate form
Over speed protection | Please provide price or state STD→ | Submit other option prices on a separate form
Manual transfer switch | Please provide price or state STD→ | Submit other option prices on a separate form
External fuel tank with pipes including min.. 10 meter non-corrosive material and fittings, state volume of tank and material | Please provide price or state STD→ | Submit other option prices on a separate form
Slow moving trolley/trailer | Please provide price or state STD→ | Submit other option prices on a separate form
(AMF) Automatic Mains Failure Power generation set | Please provide price or state STD→ | Submit other option prices on a separate form
Automatic main circuit breaker | Please provide price or state STD→ | Submit other option prices on a separate form
Installation instructions and eventual. drawings, other languages | Please provide price or state STD→ | Submit other option prices on a separate form
Change over switch positions for: 1) Mains 2) Off 3) GENERATOR SET | Please provide price or state STD→ | Submit other option prices on a separate form
Automatic main circuit breaker | Please provide price or state STD→ | Submit other option prices on a separate form
Operators and maintenance manual, other languages | Please provide price or state STD→ | Submit other option prices on a separate form

## Lot 7 60 kVA PV 10% Roof
Bidder name:
Make and model:
Lot 7. 60 kVA PV 10% Sloped Roof or Gen set mount.
HYBRID PV SOLAR/DIESEL GENERATOR SET SPECS | UNOPS REQUIREMENTS | Bidder: Compliant/Non-compliant to UNOPS requirements? Please mark YES/NO in this coloumn. Not indicating YES/NO in this column may render your bid non-compliant. | Bidders are required to provide information in this column on the specifications of their bid to demonstrate compliance to set specifications. Not providing specifications under this column may render your bid non-compliant.
Complete Hybrid PV solar/diesel generator set for autonomous operation, including PV solar power array, battery package, inverter and charge controller. Diesel engine, alternator, control panel with monitoring gauges/indicators, starting equipment, fuel tank as well as other accessories. Charger to charge battery package by diesel gen set and PV solar system interface between diesel gen set and PV solar power unit for a smooth operation for the two energy sources in conjunction, automatically without any manual intervention. Factory test certificates must be included and must be in accordance to internationally recognised standards. Suitable for tropical conditions. | Comply and state → | Yes / No
KEY DATA
Make | Please state →
Model | Please state →
Country of origin | Please state →
DIESEL GEN SET
Rated power output, min. 60kVA | Comply and state → | Yes / No
Power factor: 0.8 | Comply and state → | Yes / No
Rated power output, 48 kW, min. | Comply and state → | Yes / No
Voltage, 220/230/240 and 380/400 V | Comply and state → | Yes / No
Phase: 1 and 3 | Comply and state → | Yes / No
AC frequency, 50/60 Hz | Comply and state → | Yes / No
Speed: rpm 1500 or 3000 or other | Please state →
Prime power according to ISO 8528 or equivalent, i.e. power available at variable load with no limitations on hours of operation and capable of min. 10% overload for min. 1 hour in any 12 hours. | Comply and state → | Yes / No
Prime rating of min. the stated output rating at Normal Temperature and Pressure conditions (NTP). Please state | Comply and state → | Yes / No
Derating information (temperature, altitude and humidity), please state | Please state →
Engine
Make | Please state →
Model | Please state →
Engine power output, kW at rpm: | Please state →
Fuel: Diesel | Comply and state → | Yes / No
Cooling, liquid or air or combined, suitable for tropical conditions | Please state →
Speed governor, state type | Please state →
Exhaust with suitable piping and residential silencer | Comply and state → | Yes / No
Noise level, dB(A) at 1 m (silencer fitted) | Please state →
Fuel consumption at 75% load: L/hour | Please state →
CO2 emissions at 75% load: g/hour | Please state →
Mounted on anti-vibration mounts | Comply and state → | Yes / No
ENVIRONMENTAL
EU Non-road emissions regulations schedule, e.g. EU STAGE II, III A, III B, IV. US Non-road and stationary emissions regulations to Tier 1,2,3,4 or equivalent. Please state. | Comply and state → | Yes / No
Alternator
Make: | Please state →
Model: | Please state →
Brushless type | Comply and state → | Yes / No
Cooling, liquid, air, other | Please state →
Protection class min. IP 23 | Comply and state → | Yes / No
Suitable AC power outlets protected by circuit breaker (state type) | Comply and state → | Yes / No
Insulation to min. IEC 60085 - >155 ° C - (F) or equivalent | Comply and state → | Yes / No
Voltage regulator | Comply and state → | Yes / No
Standard accessories
Fuel tank. Integrated or separate, suitable for continuous operation of min. 8 hours at rated capacity. State capacity, litres. Fuel level gauge. Including all necessary pipework, connections etc. Possibility for connection to external tank. | Comply and state→ | Yes / No
Low oil pressure protection, automatic shut down | Comply and state → | Yes / No
Over heating protection | Comply and state → | Yes / No
Overload protection | Comply and state → | Yes / No
Emergency stop | Comply and state → | Yes / No
Electric starter with key and battery | Comply and state → | Yes / No
Min. Voltmeter, ammeter, hour meter, Hz meter, water temp gauge/indicator (where applicable) | Comply and state → | Yes / No
Earthing/grounding facility | Comply and state → | Yes / No
PV SOLAR POWER SYSTEM STANDARD ARRAY NOMINAL MIN. 4.8 kWp. Battery pack 48kWh. For Sloped Roof or Gen set mount.
PV solar array
Make and model: | Please state →
Array kWp, min 10% of diesel generator set max output which is 60kVA/48kW, hence = 4.8 kWp min. | Comply and state→ | Yes / No
PV panels, total surface covering, m2 | Please state →
Nominal power output each panel, kWp | Please state →
Isc array, A (Amp) | Please state →
Certifications: Any one or more of IEC61215, UL1703 or equivalent | Comply and state → | Yes / No
Charge controller
Make and model: | Please state →
Type: MTTP | Comply and state → | Yes / No
Certifications. Any one or more of EN60730-1/2-11, 55022, 61000-4-27374/5/6 or equivalent | Comply and state→ | Yes / No
Capacity: Isc array +20%, min. | Comply and state→ | Yes / No
Inverter
Make and model: | Please state →
Capacity, A (Amp): Min. equivalent to max load | Comply and state→ | Yes / No
Pure sine curve | Comply and state → | Yes / No
Certifications: Any one or more of EN50178, 62040, 60950, 61000-2/3/6, EN60529, 50438 or equivalent | Comply and state → | Yes / No
Battery package
Make and model: | Please state →
Capacity: Min. equivalent to hybrid diesel gen set full load - 24 kW - for 1 hour = 48 kWh. | Comply and state→ | Yes / No
Battery type: LiFePo4 | Comply and state→ | Yes / No
Certifications,: Any one or more of UL1642, IEC62133, 61000-6-3 or equivalent | Comply and state→ | Yes / No
PV panel racks, brackets, cables, fittings etc.
PV panels racks for sloped roof mount included for all included PV panels, if not attached to the Hybrid Gen set system itself (permanently or fold-out system etc). | Comply and state→ | Yes / No
All cables, junctions, contacts, breakers, earthing spears, fittings, screws, nut and bots etc included | Comply and state → | Yes / No
Installation
The system must be plug and play. Inverter, charge controller, battery package, battery charger must be pre-installed and wired either inside one common Hybrid system cage or in a separate cabinet, in order to easily connect the PV array and the local installation. All cables for establishing the PV array must be readily available with pre-installed connections and clearly marked in a way that no mistakes can occur. | Comply and state → | Yes / No
Other
Lifting points for handling | Comply and state → | Yes / No
Installation instructions, drawings, photos, brochures etc. English/French/Spanish | Comply and state → | Yes / No
Operators and maintenance manual, English/French/Spanish | Comply and state → | Yes / No
Tool kit | Comply and state → | Yes / No
Basic maintenance kit, engine: Min. 4 x oil filters, 2 x air filters, 2 x fuel filters | Comply and state → | Yes / No
Dimensions, L x W x H, mm | Please state →
Weight, dry, entire hybrid system incl. Battery package and all PV panels, cables, brackets etc etc.: kg: | Please state →
WARRANTY
Diesel Generator set: 2 years/2500 hours of operation which ever occur first. PV panels: Min. 10 years. Min. 90% performance guarantee at 10 years. Min. 80% performance guarantee at 20 years. Battery package: Min. 5 years. Inverter/charge controller/charger: Min. 4 years. Other equipment: Min. 2 years | Comply and state → | Yes / No
Sustainability
The bidder must demonstrate that its organisation has an environmental management system in place which as a minimum shall submit at least one or more of the following : the environmental policy principles of the organisation; the management measures and procedures taken or that will be taken to assess, monitor, measure and mitigate environmental impacts of the business processes/products associated with the execution of the contract; how attention is paid to the awareness and training/competency of employee(s) and supplier(s) with regard to dealing with the environmental aspects relevant to this bid; and that compliance with the environmental legislation applicable to the required performance(s) is guaranteed, ISO 14001 certificate, EMAS or an equivalent certificate | Comply and state → | Yes / No
The bidder shall provide documentation which outlines their approach to ensuring equal opportunity, diversity and inclusion within their organisation (e.g. equal pay policy, parental leave, ratio of females/males employees, % of female in management positions, grievances disaggregated by gender, transparency of promotion criteria, sexual harassment policies) | Comply and state → | Yes / No
Mandatory Options
Diesel engine spare parts & maintenance kit for min. 2500 hours of operation | Mandatory | enter prices on Form C: Price Schedule
Sound insolating and water proof canopy (max. 70 dB(A) at 7 m) | Mandatory | enter prices on Form C: Price Schedule
Work shop manual | Mandatory | enter prices on Form C: Price Schedule
Spare parts catalogue | Mandatory | enter prices on Form C: Price Schedule
60 Hz version of Generator set, please enter any surcharge to the std 50 Hz version offered above | Mandatory | enter prices on Form C: Price Schedule
Suggested Options
Heavy duty air filter for dusty conditions | Please provide price or state STD→ | Submit other option prices on a separate form
Heavy duty fuel filter/additional fuel filter in line with original | Please provide price or state STD→ | Submit other option prices on a separate form
Additional silencer, state dB(A) at 1 m and/or 7 m | Please provide price or state STD→ | Submit other option prices on a separate form
High chimney for exhaust, state height and materials | Please provide price or state STD→ | Submit other option prices on a separate form
(ATS) Automatic Transfer Switch | Please provide price or state STD→ | Submit other option prices on a separate form
Over speed protection | Please provide price or state STD→ | Submit other option prices on a separate form
Manual transfer switch | Please provide price or state STD→ | Submit other option prices on a separate form
External fuel tank with pipes including min.. 10 meter non-corrosive material and fittings, state volume of tank and material | Please provide price or state STD→ | Submit other option prices on a separate form
Slow moving trolley/trailer | Please provide price or state STD→ | Submit other option prices on a separate form
(AMF) Automatic Mains Failure Power generation set | Please provide price or state STD→ | Submit other option prices on a separate form
Automatic main circuit breaker | Please provide price or state STD→ | Submit other option prices on a separate form
Installation instructions and eventual. drawings, other languages | Please provide price or state STD→ | Submit other option prices on a separate form
Change over switch positions for: 1) Mains 2) Off 3) GENERATOR SET | Please provide price or state STD→ | Submit other option prices on a separate form
Automatic main circuit breaker | Please provide price or state STD→ | Submit other option prices on a separate form
Operators and maintenance manual, other languages | Please provide price or state STD→ | Submit other option prices on a separate form

## Lot 8 60 kVA PV 20% Roof
Bidder name:
Make and model:
Lot 8. 60 kVA PV 20% Sloped Roof or Gen set mount.
HYBRID PV SOLAR/DIESEL GENERATOR SET SPECS | UNOPS REQUIREMENTS | Bidder: Compliant/Non-compliant to UNOPS requirements? Please mark YES/NO in this coloumn. Not indicating YES/NO in this column may render your bid non-compliant. | Bidders are required to provide information in this column on the specifications of their bid to demonstrate compliance to set specifications. Not providing specifications under this column may render your bid non-compliant.
Complete Hybrid PV solar/diesel generator set for autonomous operation, including PV solar power array, battery package, inverter and charge controller. Diesel engine, alternator, control panel with monitoring gauges/indicators, starting equipment, fuel tank as well as other accessories. Charger to charge battery package by diesel gen set and PV solar system interface between diesel gen set and PV solar power unit for a smooth operation for the two energy sources in conjunction, automatically without any manual intervention. Factory test certificates must be included and must be in accordance to internationally recognised standards. Suitable for tropical conditions. | Comply and state → | Yes / No
KEY DATA
Make | Please state →
Model | Please state →
Country of origin | Please state →
DIESEL GEN SET
Rated power output, min. 60kVA | Comply and state → | Yes / No
Power factor: 0.8 | Comply and state → | Yes / No
Rated power output, 48 kW, min. | Comply and state → | Yes / No
Voltage, 220/230/240 and 380/400 V | Comply and state → | Yes / No
Phase: 1 and 3 | Comply and state → | Yes / No
AC frequency, 50/60 Hz | Comply and state → | Yes / No
Speed: rpm 1500 or 3000 or other | Please state →
Prime power according to ISO 8528 or equivalent, i.e. power available at variable load with no limitations on hours of operation and capable of min. 10% overload for min. 1 hour in any 12 hours. | Comply and state → | Yes / No
Prime rating of min. the stated output rating at Normal Temperature and Pressure conditions (NTP). Please state | Comply and state → | Yes / No
Derating information (temperature, altitude and humidity), please state | Please state →
Engine
Make | Please state →
Model | Please state →
Engine power output, kW at rpm: | Please state →
Fuel: Diesel | Comply and state → | Yes / No
Cooling, liquid or air or combined, suitable for tropical conditions | Please state →
Speed governor, state type | Please state →
Exhaust with suitable piping and residential silencer | Comply and state → | Yes / No
Noise level, dB(A) at 1 m (silencer fitted) | Please state →
Fuel consumption at 75% load: L/hour | Please state →
CO2 emissions at 75% load: g/hour | Please state →
Mounted on anti-vibration mounts | Comply and state → | Yes / No
ENVIRONMENTAL
EU Non-road emissions regulations schedule, e.g. EU STAGE II, III A, III B, IV. US Non-road and stationary emissions regulations to Tier 1,2,3,4 or equivalent. Please state. | Comply and state → | Yes / No
Alternator
Make: | Please state →
Model: | Please state →
Brushless type | Comply and state → | Yes / No
Cooling, liquid, air, other | Please state →
Protection class min. IP 23 | Comply and state → | Yes / No
Suitable AC power outlets protected by circuit breaker (state type) | Comply and state → | Yes / No
Insulation to min. IEC 60085 - >155 ° C - (F) or equivalent | Comply and state → | Yes / No
Voltage regulator | Comply and state → | Yes / No
Standard accessories
Fuel tank. Integrated or separate, suitable for continuous operation of min. 8 hours at rated capacity. State capacity, litres. Fuel level gauge. Including all necessary pipework, connections etc. Possibility for connection to external tank. | Comply and state→ | Yes / No
Low oil pressure protection, automatic shut down | Comply and state → | Yes / No
Over heating protection | Comply and state → | Yes / No
Overload protection | Comply and state → | Yes / No
Emergency stop | Comply and state → | Yes / No
Electric starter with key and battery | Comply and state → | Yes / No
Min. Voltmeter, ammeter, hour meter, Hz meter, water temp gauge/indicator (where applicable) | Comply and state → | Yes / No
Earthing/grounding facility | Comply and state → | Yes / No
PV SOLAR POWER SYSTEM STANDARD ARRAY NOMINAL MIN. 9.6 kWp. Battery pack 48 kWh. For Sloped Roof or Gen set mount.
PV solar array
Make and model: | Please state →
Array kWp, min 20% of diesel generator set max output which is 60 kVA/48 kW, hence = 9.6 kWp min. | Comply and state→ | Yes / No
PV panels, total surface covering, m2 | Please state →
Nominal power output each panel, kWp | Please state →
Isc array, A (Amp) | Please state →
Certifications: Any one or more of IEC61215, UL1703 or equivalent | Comply and state → | Yes / No
Charge controller
Make and model: | Please state →
Type: MTTP | Comply and state → | Yes / No
Certifications. Any one or more of EN60730-1/2-11, 55022, 61000-4-27374/5/6 or equivalent | Comply and state→ | Yes / No
Capacity: Isc array +20%, min. | Comply and state→ | Yes / No
Inverter
Make and model: | Please state →
Capacity, A (Amp): Min. equivalent to max load | Comply and state→ | Yes / No
Pure sine curve | Comply and state → | Yes / No
Certifications: Any one or more of EN50178, 62040, 60950, 61000-2/3/6, EN60529, 50438 or equivalent | Comply and state → | Yes / No
Battery package
Make and model: | Please state →
Capacity: Min. equivalent to hybrid diesel gen set full load - 24 kW - for 1 hour = 48 kWh. | Comply and state→ | Yes / No
Battery type: LiFePo4 | Comply and state→ | Yes / No
Certifications,: Any one or more of UL1642, IEC62133, 61000-6-3 or equivalent | Comply and state→ | Yes / No
PV panel racks, brackets, cables, fittings etc.
PV panels racks for sloped roof mount included for all included PV panels, if not attached to the Hybrid Gen set system itself (permanently or fold-out system etc). | Comply and state→ | Yes / No
All cables, junctions, contacts, breakers, earthing spears, fittings, screws, nut and bots etc included | Comply and state → | Yes / No
Installation
The system must be plug and play. Inverter, charge controller, battery package, battery charger must be pre-installed and wired either inside one common Hybrid system cage or in a separate cabinet, in order to easily connect the PV array and the local installation. All cables for establishing the PV array must be readily available with pre-installed connections and clearly marked in a way that no mistakes can occur. | Comply and state → | Yes / No
Other
Lifting points for handling | Comply and state → | Yes / No
Installation instructions, drawings, photos, brochures etc. English/French/Spanish | Comply and state → | Yes / No
Operators and maintenance manual, English/French/Spanish | Comply and state → | Yes / No
Tool kit | Comply and state → | Yes / No
Basic maintenance kit, engine: Min. 4 x oil filters, 2 x air filters, 2 x fuel filters | Comply and state → | Yes / No
Dimensions, L x W x H, mm | Please state →
Weight, dry, entire hybrid system incl. Battery package and all PV panels, cables, brackets etc etc.: kg: | Please state →
WARRANTY
Diesel Generator set: 2 years/2500 hours of operation which ever occur first. PV panels: Min. 10 years. Min. 90% performance guarantee at 10 years. Min. 80% performance guarantee at 20 years. Battery package: Min. 5 years. Inverter/charge controller/charger: Min. 4 years. Other equipment: Min. 2 years | Comply and state → | Yes / No
Sustainability
The bidder must demonstrate that its organisation has an environmental management system in place which as a minimum shall submit at least one or more of the following : the environmental policy principles of the organisation; the management measures and procedures taken or that will be taken to assess, monitor, measure and mitigate environmental impacts of the business processes/products associated with the execution of the contract; how attention is paid to the awareness and training/competency of employee(s) and supplier(s) with regard to dealing with the environmental aspects relevant to this bid; and that compliance with the environmental legislation applicable to the required performance(s) is guaranteed, ISO 14001 certificate, EMAS or an equivalent certificate | Comply and state → | Yes / No
The bidder shall provide documentation which outlines their approach to ensuring equal opportunity, diversity and inclusion within their organisation (e.g. equal pay policy, parental leave, ratio of females/males employees, % of female in management positions, grievances disaggregated by gender, transparency of promotion criteria, sexual harassment policies) | Comply and state → | Yes / No
Mandatory Options
Diesel engine spare parts & maintenance kit for min. 2500 hours of operation | Mandatory | enter prices on Form C: Price Schedule
Sound insolating and water proof canopy (max. 70 dB(A) at 7 m) | Mandatory | enter prices on Form C: Price Schedule
Work shop manual | Mandatory | enter prices on Form C: Price Schedule
Spare parts catalogue | Mandatory | enter prices on Form C: Price Schedule
60 Hz version of Generator set, please enter any surcharge to the std 50 Hz version offered above | Mandatory | enter prices on Form C: Price Schedule
Suggested Options
Heavy duty air filter for dusty conditions | Please provide price or state STD→ | Submit other option prices on a separate form
Heavy duty fuel filter/additional fuel filter in line with original | Please provide price or state STD→ | Submit other option prices on a separate form
Additional silencer, state dB(A) at 1 m and/or 7 m | Please provide price or state STD→ | Submit other option prices on a separate form
High chimney for exhaust, state height and materials | Please provide price or state STD→ | Submit other option prices on a separate form
(ATS) Automatic Transfer Switch | Please provide price or state STD→ | Submit other option prices on a separate form
Over speed protection | Please provide price or state STD→ | Submit other option prices on a separate form
Manual transfer switch | Please provide price or state STD→ | Submit other option prices on a separate form
External fuel tank with pipes including min.. 10 meter non-corrosive material and fittings, state volume of tank and material | Please provide price or state STD→ | Submit other option prices on a separate form
Slow moving trolley/trailer | Please provide price or state STD→ | Submit other option prices on a separate form
(AMF) Automatic Mains Failure Power generation set | Please provide price or state STD→ | Submit other option prices on a separate form
Automatic main circuit breaker | Please provide price or state STD→ | Submit other option prices on a separate form
Installation instructions and eventual. drawings, other languages | Please provide price or state STD→ | Submit other option prices on a separate form
Change over switch positions for: 1) Mains 2) Off 3) GENERATOR SET | Please provide price or state STD→ | Submit other option prices on a separate form
Automatic main circuit breaker | Please provide price or state STD→ | Submit other option prices on a separate form
Operators and maintenance manual, other languages | Please provide price or state STD→ | Submit other option prices on a separate form

## Lot 9 60 kVA PV 40% Roof
Bidder name:
Make and model:
Lot 9. 60 kVA PV 40% Sloped Roof or Gen set mount.
HYBRID PV SOLAR/DIESEL GENERATOR SET SPECS | UNOPS REQUIREMENTS | Bidder: Compliant/Non-compliant to UNOPS requirements? Please mark YES/NO in this coloumn. Not indicating YES/NO in this column may render your bid non-compliant. | Bidders are required to provide information in this column on the specifications of their bid to demonstrate compliance to set specifications. Not providing specifications under this column may render your bid non-compliant.
Complete Hybrid PV solar/diesel generator set for autonomous operation, including PV solar power array, battery package, inverter and charge controller. Diesel engine, alternator, control panel with monitoring gauges/indicators, starting equipment, fuel tank as well as other accessories. Charger to charge battery package by diesel gen set and PV solar system interface between diesel gen set and PV solar power unit for a smooth operation for the two energy sources in conjunction, automatically without any manual intervention. Factory test certificates must be included and must be in accordance to internationally recognised standards. Suitable for tropical conditions. | Comply and state → | Yes / No
KEY DATA
Make | Please state → | Yes / No
Model | Please state → | Yes / No
Country of origin | Please state → | Yes / No
DIESEL GEN SET
Rated power output, min. 60kVA | Comply and state → | Yes / No
Power factor: 0.8 | Comply and state → | Yes / No
Rated power output, 48 kW, min. | Comply and state → | Yes / No
Voltage, 220/230/240 and 380/400 V | Comply and state → | Yes / No
Phase: 1 and 3 | Comply and state → | Yes / No
AC frequency, 50/60 Hz | Comply and state → | Yes / No
Speed: rpm 1500 or 3000 or other | Please state →
Prime power according to ISO 8528 or equivalent, i.e. power available at variable load with no limitations on hours of operation and capable of min. 10% overload for min. 1 hour in any 12 hours. | Comply and state → | Yes / No
Prime rating of min. the stated output rating at Normal Temperature and Pressure conditions (NTP). Please state | Comply and state → | Yes / No
Derating information (temperature, altitude and humidity), please state | Please state →
Engine
Make | Please state →
Model | Please state →
Engine power output, kW at rpm: | Please state →
Fuel: Diesel | Comply and state → | Yes / No
Cooling, liquid or air or combined, suitable for tropical conditions | Please state →
Speed governor, state type | Please state →
Exhaust with suitable piping and residential silencer | Comply and state → | Yes / No
Noise level, dB(A) at 1 m (silencer fitted) | Please state →
Fuel consumption at 75% load: L/hour | Please state →
CO2 emissions at 75% load: g/hour | Please state →
Mounted on anti-vibration mounts | Comply and state → | Yes / No
ENVIRONMENTAL
EU Non-road emissions regulations schedule, e.g. EU STAGE II, III A, III B, IV. US Non-road and stationary emissions regulations to Tier 1,2,3,4 or equivalent. Please state. | Comply and state → | Yes / No
Alternator
Make: | Please state →
Model: | Please state →
Brushless type | Comply and state → | Yes / No
Cooling, liquid, air, other | Please state →
Protection class min. IP 23 | Comply and state → | Yes / No
Suitable AC power outlets protected by circuit breaker (state type) | Comply and state → | Yes / No
Insulation to min. IEC 60085 - >155 ° C - (F) or equivalent | Comply and state → | Yes / No
Voltage regulator | Comply and state → | Yes / No
Standard accessories
Fuel tank. Integrated or separate, suitable for continuous operation of min. 8 hours at rated capacity. State capacity, litres. Fuel level gauge. Including all necessary pipework, connections etc. Possibility for connection to external tank. | Comply and state→ | Yes / No
Low oil pressure protection, automatic shut down | Comply and state → | Yes / No
Over heating protection | Comply and state → | Yes / No
Overload protection | Comply and state → | Yes / No
Emergency stop | Comply and state → | Yes / No
Electric starter with key and battery | Comply and state → | Yes / No
Min. Voltmeter, ammeter, hour meter, Hz meter, water temp gauge/indicator (where applicable) | Comply and state → | Yes / No
Earthing/grounding facility | Comply and state → | Yes / No
PV SOLAR POWER SYSTEM STANDARD ARRAY NOMINAL MIN. 19.2 kWp. Battery pack 48 kWh. For Sloped Roof or Gen set mount.
PV solar array
Make and model: | Please state →
Array kWp, min 40% of diesel generator set max output which is 60 kVA/48 kW, hence = 19.2 kWp min. | Comply and state→ | Yes / No
PV panels, total surface covering, m2 | Please state →
Nominal power output each panel, kWp | Please state →
Isc array, A (Amp) | Please state →
Certifications: Any one or more of IEC61215, UL1703 or equivalent | Comply and state → | Yes / No
Charge controller
Make and model: | Please state →
Type: MTTP | Comply and state → | Yes / No
Certifications. Any one or more of EN60730-1/2-11, 55022, 61000-4-27374/5/6 or equivalent | Comply and state→ | Yes / No
Capacity: Isc array +20%, min. | Comply and state→ | Yes / No
Inverter
Make and model: | Please state →
Capacity, A (Amp): Min. equivalent to max load | Comply and state→ | Yes / No
Pure sine curve | Comply and state → | Yes / No
Certifications: Any one or more of EN50178, 62040, 60950, 61000-2/3/6, EN60529, 50438 or equivalent | Comply and state → | Yes / No
Battery package
Make and model: | Please state →
Capacity: Min. equivalent to hybrid diesel gen set full load - 24 kW - for 1 hour = 48 kWh. | Comply and state→ | Yes / No
Battery type: LiFePo4 | Comply and state→ | Yes / No
Certifications,: Any one or more of UL1642, IEC62133, 61000-6-3 or equivalent | Comply and state→ | Yes / No
PV panel racks, brackets, cables, fittings etc.
PV panels racks for sloped roof mount included for all included PV panels, if not attached to the Hybrid Gen set system itself (permanently or fold-out system etc). | Comply and state→ | Yes / No
All cables, junctions, contacts, breakers, earthing spears, fittings, screws, nut and bots etc included | Comply and state → | Yes / No
Installation
The system must be plug and play. Inverter, charge controller, battery package, battery charger must be pre-installed and wired either inside one common Hybrid system cage or in a separate cabinet, in order to easily connect the PV array and the local installation. All cables for establishing the PV array must be readily available with pre-installed connections and clearly marked in a way that no mistakes can occur. | Comply and state → | Yes / No
Other
Lifting points for handling | Comply and state → | Yes / No
Installation instructions, drawings, photos, brochures etc. English/French/Spanish | Comply and state → | Yes / No
Operators and maintenance manual, English/French/Spanish | Comply and state → | Yes / No
Tool kit | Comply and state → | Yes / No
Basic maintenance kit, engine: Min. 4 x oil filters, 2 x air filters, 2 x fuel filters | Comply and state → | Yes / No
Dimensions, L x W x H, mm | Please state →
Weight, dry, entire hybrid system incl. Battery package and all PV panels, cables, brackets etc etc.: kg: | Please state →
WARRANTY
Diesel Generator set: 2 years/2500 hours of operation which ever occur first. PV panels: Min. 10 years. Min. 90% performance guarantee at 10 years. Min. 80% performance guarantee at 20 years. Battery package: Min. 5 years. Inverter/charge controller/charger: Min. 4 years. Other equipment: Min. 2 years | Comply and state → | Yes / No
Sustainability
The bidder must demonstrate that its organisation has an environmental management system in place which as a minimum shall submit at least one or more of the following : the environmental policy principles of the organisation; the management measures and procedures taken or that will be taken to assess, monitor, measure and mitigate environmental impacts of the business processes/products associated with the execution of the contract; how attention is paid to the awareness and training/competency of employee(s) and supplier(s) with regard to dealing with the environmental aspects relevant to this bid; and that compliance with the environmental legislation applicable to the required performance(s) is guaranteed, ISO 14001 certificate, EMAS or an equivalent certificate | Comply and state → | Yes / No
The bidder shall provide documentation which outlines their approach to ensuring equal opportunity, diversity and inclusion within their organisation (e.g. equal pay policy, parental leave, ratio of females/males employees, % of female in management positions, grievances disaggregated by gender, transparency of promotion criteria, sexual harassment policies) | Comply and state → | Yes / No
Mandatory Options
Diesel engine spare parts & maintenance kit for min. 2500 hours of operation | Mandatory | enter prices on Form C: Price Schedule
Sound insolating and water proof canopy (max. 70 dB(A) at 7 m) | Mandatory | enter prices on Form C: Price Schedule
Work shop manual | Mandatory | enter prices on Form C: Price Schedule
Spare parts catalogue | Mandatory | enter prices on Form C: Price Schedule
60 Hz version of Generator set, please enter any surcharge to the std 50 Hz version offered above | Mandatory | enter prices on Form C: Price Schedule
Suggested Options
Heavy duty air filter for dusty conditions | Please provide price or state STD→ | Submit other option prices on a separate form
Heavy duty fuel filter/additional fuel filter in line with original | Please provide price or state STD→ | Submit other option prices on a separate form
Additional silencer, state dB(A) at 1 m and/or 7 m | Please provide price or state STD→ | Submit other option prices on a separate form
High chimney for exhaust, state height and materials | Please provide price or state STD→ | Submit other option prices on a separate form
(ATS) Automatic Transfer Switch | Please provide price or state STD→ | Submit other option prices on a separate form
Over speed protection | Please provide price or state STD→ | Submit other option prices on a separate form
Manual transfer switch | Please provide price or state STD→ | Submit other option prices on a separate form
External fuel tank with pipes including min.. 10 meter non-corrosive material and fittings, state volume of tank and material | Please provide price or state STD→ | Submit other option prices on a separate form
Slow moving trolley/trailer | Please provide price or state STD→ | Submit other option prices on a separate form
(AMF) Automatic Mains Failure Power generation set | Please provide price or state STD→ | Submit other option prices on a separate form
Automatic main circuit breaker | Please provide price or state STD→ | Submit other option prices on a separate form
Installation instructions and eventual. drawings, other languages | Please provide price or state STD→ | Submit other option prices on a separate form
Change over switch positions for: 1) Mains 2) Off 3) GENERATOR SET | Please provide price or state STD→ | Submit other option prices on a separate form
Automatic main circuit breaker | Please provide price or state STD→ | Submit other option prices on a separate form
Operators and maintenance manual, other languages | Please provide price or state STD→ | Submit other option prices on a separate form

## Lot 10 60 kVA PV 10% Ground
Bidder name:
Make and model:
Lot 10. 60 kVA PV 10% Ground or flat roof mounted
HYBRID PV SOLAR/DIESEL GENERATOR SET SPECS | UNOPS REQUIREMENTS | Bidder: Compliant/Non-compliant to UNOPS requirements? Please mark YES/NO in this coloumn. Not indicating YES/NO in this column may render your bid non-compliant. | Bidders are required to provide information in this column on the specifications of their bid to demonstrate compliance to set specifications. Not providing specifications under this column may render your bid non-compliant.
Complete Hybrid PV solar/diesel generator set for autonomous operation, including PV solar power array, battery package, inverter and charge controller. Diesel engine, alternator, control panel with monitoring gauges/indicators, starting equipment, fuel tank as well as other accessories. Charger to charge battery package by diesel gen set and PV solar system interface between diesel gen set and PV solar power unit for a smooth operation for the two energy sources in conjunction, automatically without any manual intervention. Factory test certificates must be included and must be in accordance to internationally recognised standards. Suitable for tropical conditions. | Comply and state → | Yes / No
KEY DATA
Make | Please state →
Model | Please state →
Country of origin | Please state →
DIESEL GEN SET
Rated power output, min. 60 kVA | Comply and state → | Yes / No
Power factor: 0.8 | Comply and state → | Yes / No
Rated power output, 48 kW, min. | Comply and state → | Yes / No
Voltage, 220/230/240 and 380/400 V | Comply and state → | Yes / No
Phase: 1 and 3 | Comply and state → | Yes / No
AC frequency, 50/60 Hz | Comply and state → | Yes / No
Speed: rpm 1500 or 3000 or other | Please state →
Prime power according to ISO 8528 or equivalent, i.e. power available at variable load with no limitations on hours of operation and capable of min. 10% overload for min. 1 hour in any 12 hours. | Comply and state → | Yes / No
Prime rating of min. the stated output rating at Normal Temperature and Pressure conditions (NTP). Please state | Comply and state → | Yes / No
Derating information (temperature, altitude and humidity), please state | Please state →
Engine
Make | Please state →
Model | Please state →
Engine power output, kW at rpm: | Please state →
Fuel: Diesel | Comply and state → | Yes / No
Cooling, liquid or air or combined, suitable for tropical conditions | Please state →
Speed governor, state type | Please state →
Exhaust with suitable piping and residential silencer | Comply and state → | Yes / No
Noise level, dB(A) at 1 m (silencer fitted) | Please state →
Fuel consumption at 75% load: L/hour | Please state →
CO2 emissions at 75% load: g/hour | Please state →
Mounted on anti-vibration mounts | Comply and state → | Yes / No
ENVIRONMENTAL
EU Non-road emissions regulations schedule, e.g. EU STAGE II, III A, III B, IV. US Non-road and stationary emissions regulations to Tier 1,2,3,4 or equivalent. Please state. | Comply and state → | Yes / No
Alternator
Make: | Please state →
Model: | Please state →
Brushless type | Comply and state → | Yes / No
Cooling, liquid, air, other | Please state →
Protection class min. IP 23 | Comply and state → | Yes / No
Suitable AC power outlets protected by circuit breaker (state type) | Comply and state → | Yes / No
Insulation to min. IEC 60085 - >155 ° C - (F) or equivalent | Comply and state → | Yes / No
Voltage regulator | Comply and state → | Yes / No
Standard accessories
Fuel tank. Integrated or separate, suitable for continuous operation of min. 8 hours at rated capacity. State capacity, litres. Fuel level gauge. Including all necessary pipework, connections etc. Possibility for connection to external tank. | Comply and state→ | Yes / No
Low oil pressure protection, automatic shut down | Comply and state → | Yes / No
Over heating protection | Comply and state → | Yes / No
Overload protection | Comply and state → | Yes / No
Emergency stop | Comply and state → | Yes / No
Electric starter with key and battery | Comply and state → | Yes / No
Min. Voltmeter, ammeter, hour meter, Hz meter, water temp gauge/indicator (where applicable) | Comply and state → | Yes / No
Earthing/grounding facility | Comply and state → | Yes / No
PV SOLAR POWER SYSTEM STANDARD ARRAY NOMINAL MIN. 4.8 kWp. Battery pack 48 kWh. For Ground or flat roof mount
PV solar array
Make and model: | Please state →
Array kWp, min 10% of diesel generator set max output which is 60kVA/48 kW, hence = 4.8kWp min. | Comply and state→ | Yes / No
PV panels, total surface covering, m2 | Please state →
Nominal power output each panel, kWp | Please state →
Isc array, A (Amp) | Please state →
Certifications: Any one or more of IEC61215, UL1703 or equivalent | Comply and state → | Yes / No
Charge controller
Make and model: | Please state →
Type: MTTP | Comply and state → | Yes / No
Certifications. Any one or more of EN60730-1/2-11, 55022, 61000-4-27374/5/6 or equivalent | Comply and state→ | Yes / No
Capacity: Isc array +20%, min. | Comply and state→ | Yes / No
Inverter
Make and model: | Please state →
Capacity, A (Amp): Min. equivalent to max load | Comply and state→ | Yes / No
Pure sine curve | Comply and state → | Yes / No
Certifications: Any one or more of EN50178, 62040, 60950, 61000-2/3/6, EN60529, 50438 or equivalent | Comply and state → | Yes / No
Battery package
Make and model: | Please state →
Capacity: Min. equivalent to hybrid diesel gen set full load - 24 kW - for 1 hour = 48 kWh. | Comply and state→ | Yes / No
Battery type: LiFePo4 | Comply and state→ | Yes / No
Certifications,: Any one or more of UL1642, IEC62133, 61000-6-3 or equivalent | Comply and state→ | Yes / No
PV panel racks, brackets, cables, fittings etc.
PV panels racks for Ground or flat roof mount. | Comply and state→ | Yes / No
All cables, junctions, contacts, breakers, earthing spears, fittings, screws, nut and bots etc included | Comply and state → | Yes / No
Installation
The system must be plug and play. Inverter, charge controller, battery package, battery charger must be pre-installed and wired either inside one common Hybrid system cage or in a separate cabinet, in order to easily connect the PV array and the local installation. All cables for establishing the PV array must be readily available with pre-installed connections and clearly marked in a way that no mistakes can occur. | Comply and state → | Yes / No
Other
Lifting points for handling | Comply and state → | Yes / No
Installation instructions, drawings, photos, brochures etc. English/French/Spanish | Comply and state → | Yes / No
Operators and maintenance manual, English/French/Spanish | Comply and state → | Yes / No
Tool kit | Comply and state → | Yes / No
Basic maintenance kit, engine: Min. 4 x oil filters, 2 x air filters, 2 x fuel filters | Comply and state → | Yes / No
Dimensions, L x W x H, mm | Please state →
Weight, dry, entire hybrid system incl. Battery package and all PV panels, cables, brackets etc etc.: kg: | Please state →
WARRANTY
Diesel Generator set: 2 years/2500 hours of operation which ever occur first. PV panels: Min. 10 years. Min. 90% performance guarantee at 10 years. Min. 80% performance guarantee at 20 years. Battery package: Min. 5 years. Inverter/charge controller/charger: Min. 4 years. Other equipment: Min. 2 years | Comply and state → | Yes / No
Sustainability
The bidder must demonstrate that its organisation has an environmental management system in place which as a minimum shall submit at least one or more of the following : the environmental policy principles of the organisation; the management measures and procedures taken or that will be taken to assess, monitor, measure and mitigate environmental impacts of the business processes/products associated with the execution of the contract; how attention is paid to the awareness and training/competency of employee(s) and supplier(s) with regard to dealing with the environmental aspects relevant to this bid; and that compliance with the environmental legislation applicable to the required performance(s) is guaranteed, ISO 14001 certificate, EMAS or an equivalent certificate | Comply and state → | Yes / No
The bidder shall provide documentation which outlines their approach to ensuring equal opportunity, diversity and inclusion within their organisation (e.g. equal pay policy, parental leave, ratio of females/males employees, % of female in management positions, grievances disaggregated by gender, transparency of promotion criteria, sexual harassment policies) | Comply and state → | Yes / No
Mandatory Options
Diesel engine spare parts & maintenance kit for min. 2500 hours of operation | Mandatory | enter prices on Form C: Price Schedule
Sound insolating and water proof canopy (max. 70 dB(A) at 7 m) | Mandatory | enter prices on Form C: Price Schedule
Work shop manual | Mandatory | enter prices on Form C: Price Schedule
Spare parts catalogue | Mandatory | enter prices on Form C: Price Schedule
60 Hz version of Generator set, please enter any surcharge to the std 50 Hz version offered above | Mandatory | enter prices on Form C: Price Schedule
Suggested Options
Heavy duty air filter for dusty conditions | Please provide price or state STD→ | Submit other option prices on a separate form
Heavy duty fuel filter/additional fuel filter in line with original | Please provide price or state STD→ | Submit other option prices on a separate form
Additional silencer, state dB(A) at 1 m and/or 7 m | Please provide price or state STD→ | Submit other option prices on a separate form
High chimney for exhaust, state height and materials | Please provide price or state STD→ | Submit other option prices on a separate form
(ATS) Automatic Transfer Switch | Please provide price or state STD→ | Submit other option prices on a separate form
Over speed protection | Please provide price or state STD→ | Submit other option prices on a separate form
Manual transfer switch | Please provide price or state STD→ | Submit other option prices on a separate form
External fuel tank with pipes including min.. 10 meter non-corrosive material and fittings, state volume of tank and material | Please provide price or state STD→ | Submit other option prices on a separate form
Slow moving trolley/trailer | Please provide price or state STD→ | Submit other option prices on a separate form
(AMF) Automatic Mains Failure Power generation set | Please provide price or state STD→ | Submit other option prices on a separate form
Automatic main circuit breaker | Please provide price or state STD→ | Submit other option prices on a separate form
Installation instructions and eventual. drawings, other languages | Please provide price or state STD→ | Submit other option prices on a separate form
Change over switch positions for: 1) Mains 2) Off 3) GENERATOR SET | Please provide price or state STD→ | Submit other option prices on a separate form
Automatic main circuit breaker | Please provide price or state STD→ | Submit other option prices on a separate form
Operators and maintenance manual, other languages | Please provide price or state STD→ | Submit other option prices on a separate form

## Lot 11 60 kVA PV 20% Ground
Bidder name:
Make and model:
Lot 11. 60 kVA PV 20% Ground or flat roof mounted
HYBRID PV SOLAR/DIESEL GENERATOR SET SPECS | UNOPS REQUIREMENTS | Bidder: Compliant/Non-compliant to UNOPS requirements? Please mark YES/NO in this coloumn. Not indicating YES/NO in this column may render your bid non-compliant. | Bidders are required to provide information in this column on the specifications of their bid to demonstrate compliance to set specifications. Not providing specifications under this column may render your bid non-compliant.
Complete Hybrid PV solar/diesel generator set for autonomous operation, including PV solar power array, battery package, inverter and charge controller. Diesel engine, alternator, control panel with monitoring gauges/indicators, starting equipment, fuel tank as well as other accessories. Charger to charge battery package by diesel gen set and PV solar system interface between diesel gen set and PV solar power unit for a smooth operation for the two energy sources in conjunction, automatically without any manual intervention. Factory test certificates must be included and must be in accordance to internationally recognised standards. Suitable for tropical conditions. | Comply and state → | Yes / No
KEY DATA
Make | Please state →
Model | Please state →
Country of origin | Please state →
DIESEL GEN SET
Rated power output, min. 60kVA | Comply and state → | Yes / No
Power factor: 0.8 | Comply and state → | Yes / No
Rated power output, 48 kW, min. | Comply and state → | Yes / No
Voltage, 220/230/240 and 380/400 V | Comply and state → | Yes / No
Phase: 1 and 3 | Comply and state → | Yes / No
AC frequency, 50/60 Hz | Comply and state → | Yes / No
Speed: rpm 1500 or 3000 or other | Please state →
Prime power according to ISO 8528 or equivalent, i.e. power available at variable load with no limitations on hours of operation and capable of min. 10% overload for min. 1 hour in any 12 hours. | Comply and state → | Yes / No
Prime rating of min. the stated output rating at Normal Temperature and Pressure conditions (NTP). Please state | Comply and state → | Yes / No
Derating information (temperature, altitude and humidity), please state | Please state →
Engine
Make | Please state →
Model | Please state →
Engine power output, kW at rpm: | Please state →
Fuel: Diesel | Comply and state → | Yes / No
Cooling, liquid or air or combined, suitable for tropical conditions | Please state →
Speed governor, state type | Please state →
Exhaust with suitable piping and residential silencer | Comply and state → | Yes / No
Noise level, dB(A) at 1 m (silencer fitted) | Please state →
Fuel consumption at 75% load: L/hour | Please state →
CO2 emissions at 75% load: g/hour | Please state →
Mounted on anti-vibration mounts | Comply and state → | Yes / No
ENVIRONMENTAL
EU Non-road emissions regulations schedule, e.g. EU STAGE II, III A, III B, IV. US Non-road and stationary emissions regulations to Tier 1,2,3,4 or equivalent. Please state. | Comply and state → | Yes / No
Alternator
Make: | Please state →
Model: | Please state →
Brushless type | Comply and state → | Yes / No
Cooling, liquid, air, other | Please state →
Protection class min. IP 23 | Comply and state → | Yes / No
Suitable AC power outlets protected by circuit breaker (state type) | Comply and state → | Yes / No
Insulation to min. IEC 60085 - >155 ° C - (F) or equivalent | Comply and state → | Yes / No
Voltage regulator | Comply and state → | Yes / No
Standard accessories
Fuel tank. Integrated or separate, suitable for continuous operation of min. 8 hours at rated capacity. State capacity, litres. Fuel level gauge. Including all necessary pipework, connections etc. Possibility for connection to external tank. | Comply and state→ | Yes / No
Low oil pressure protection, automatic shut down | Comply and state → | Yes / No
Over heating protection | Comply and state → | Yes / No
Overload protection | Comply and state → | Yes / No
Emergency stop | Comply and state → | Yes / No
Electric starter with key and battery | Comply and state → | Yes / No
Min. Voltmeter, ammeter, hour meter, Hz meter, water temp gauge/indicator (where applicable) | Comply and state → | Yes / No
Earthing/grounding facility | Comply and state → | Yes / No
PV SOLAR POWER SYSTEM STANDARD ARRAY NOMINAL MIN. 9.6 kWp. Battery pack 48 kWh. For Sloped Roof or Gen set mount.
PV solar array
Make and model: | Please state →
Array kWp, min 20% of diesel generator set max output which is 60 kVA/48 kW, hence = 9.6 kWp min. | Comply and state→ | Yes / No
PV panels, total surface covering, m2 | Please state →
Nominal power output each panel, kWp | Please state →
Isc array, A (Amp) | Please state →
Certifications: Any one or more of IEC61215, UL1703 or equivalent | Comply and state → | Yes / No
Charge controller
Make and model: | Please state →
Type: MTTP | Comply and state → | Yes / No
Certifications. Any one or more of EN60730-1/2-11, 55022, 61000-4-27374/5/6 or equivalent | Comply and state→ | Yes / No
Capacity: Isc array +20%, min. | Comply and state→ | Yes / No
Inverter
Make and model: | Please state →
Capacity, A (Amp): Min. equivalent to max load | Comply and state→ | Yes / No
Pure sine curve | Comply and state → | Yes / No
Certifications: Any one or more of EN50178, 62040, 60950, 61000-2/3/6, EN60529, 50438 or equivalent | Comply and state → | Yes / No
Battery package
Make and model: | Please state →
Capacity: Min. equivalent to hybrid diesel gen set full load - 24 kW - for 1 hour = 48 kWh. | Comply and state→ | Yes / No
Battery type: LiFePo4 | Comply and state→ | Yes / No
Certifications,: Any one or more of UL1642, IEC62133, 61000-6-3 or equivalent | Comply and state→ | Yes / No
PV panel racks, brackets, cables, fittings etc.
PV panels racks for Ground or flat roof mount. | Comply and state→ | Yes / No
All cables, junctions, contacts, breakers, earthing spears, fittings, screws, nut and bots etc included | Comply and state → | Yes / No
Installation
The system must be plug and play. Inverter, charge controller, battery package, battery charger must be pre-installed and wired either inside one common Hybrid system cage or in a separate cabinet, in order to easily connect the PV array and the local installation. All cables for establishing the PV array must be readily available with pre-installed connections and clearly marked in a way that no mistakes can occur. | Comply and state → | Yes / No
Other
Lifting points for handling | Comply and state → | Yes / No
Installation instructions, drawings, photos, brochures etc. English/French/Spanish | Comply and state → | Yes / No
Operators and maintenance manual, English/French/Spanish | Comply and state → | Yes / No
Tool kit | Comply and state → | Yes / No
Basic maintenance kit, engine: Min. 4 x oil filters, 2 x air filters, 2 x fuel filters | Comply and state → | Yes / No
Dimensions, L x W x H, mm | Please state →
Weight, dry, entire hybrid system incl. Battery package and all PV panels, cables, brackets etc etc.: kg: | Please state →
WARRANTY
Diesel Generator set: 2 years/2500 hours of operation which ever occur first. PV panels: Min. 10 years. Min. 90% performance guarantee at 10 years. Min. 80% performance guarantee at 20 years. Battery package: Min. 5 years. Inverter/charge controller/charger: Min. 4 years. Other equipment: Min. 2 years | Comply and state → | Yes / No
Sustainability
The bidder must demonstrate that its organisation has an environmental management system in place which as a minimum shall submit at least one or more of the following : the environmental policy principles of the organisation; the management measures and procedures taken or that will be taken to assess, monitor, measure and mitigate environmental impacts of the business processes/products associated with the execution of the contract; how attention is paid to the awareness and training/competency of employee(s) and supplier(s) with regard to dealing with the environmental aspects relevant to this bid; and that compliance with the environmental legislation applicable to the required performance(s) is guaranteed, ISO 14001 certificate, EMAS or an equivalent certificate | Comply and state → | Yes / No
The bidder shall provide documentation which outlines their approach to ensuring equal opportunity, diversity and inclusion within their organisation (e.g. equal pay policy, parental leave, ratio of females/males employees, % of female in management positions, grievances disaggregated by gender, transparency of promotion criteria, sexual harassment policies) | Comply and state → | Yes / No
Mandatory Options
Diesel engine spare parts & maintenance kit for min. 2500 hours of operation | Mandatory | enter prices on Form C: Price Schedule
Sound insolating and water proof canopy (max. 70 dB(A) at 7 m) | Mandatory | enter prices on Form C: Price Schedule
Work shop manual | Mandatory | enter prices on Form C: Price Schedule
Spare parts catalogue | Mandatory | enter prices on Form C: Price Schedule
60 Hz version of Generator set, please enter any surcharge to the std 50 Hz version offered above | Mandatory | enter prices on Form C: Price Schedule
Suggested Options
Heavy duty air filter for dusty conditions | Please provide price or state STD→ | Submit other option prices on a separate form
Heavy duty fuel filter/additional fuel filter in line with original | Please provide price or state STD→ | Submit other option prices on a separate form
Additional silencer, state dB(A) at 1 m and/or 7 m | Please provide price or state STD→ | Submit other option prices on a separate form
High chimney for exhaust, state height and materials | Please provide price or state STD→ | Submit other option prices on a separate form
(ATS) Automatic Transfer Switch | Please provide price or state STD→ | Submit other option prices on a separate form
Over speed protection | Please provide price or state STD→ | Submit other option prices on a separate form
Manual transfer switch | Please provide price or state STD→ | Submit other option prices on a separate form
External fuel tank with pipes including min.. 10 meter non-corrosive material and fittings, state volume of tank and material | Please provide price or state STD→ | Submit other option prices on a separate form
Slow moving trolley/trailer | Please provide price or state STD→ | Submit other option prices on a separate form
(AMF) Automatic Mains Failure Power generation set | Please provide price or state STD→ | Submit other option prices on a separate form
Automatic main circuit breaker | Please provide price or state STD→ | Submit other option prices on a separate form
Installation instructions and eventual. drawings, other languages | Please provide price or state STD→ | Submit other option prices on a separate form
Change over switch positions for: 1) Mains 2) Off 3) GENERATOR SET | Please provide price or state STD→ | Submit other option prices on a separate form
Automatic main circuit breaker | Please provide price or state STD→ | Submit other option prices on a separate form
Operators and maintenance manual, other languages | Please provide price or state STD→ | Submit other option prices on a separate form

## Lot 12 60 kVA PV 40% Ground
Bidder name:
Make and model:
Lot 12. 60 kVA PV 40% . Ground or flat roof mounted
HYBRID PV SOLAR/DIESEL GENERATOR SET SPECS | UNOPS REQUIREMENTS | Bidder: Compliant/Non-compliant to UNOPS requirements? Please mark YES/NO in this coloumn. Not indicating YES/NO in this column may render your bid non-compliant. | Bidders are required to provide information in this column on the specifications of their bid to demonstrate compliance to set specifications. Not providing specifications under this column may render your bid non-compliant.
Complete Hybrid PV solar/diesel generator set for autonomous operation, including PV solar power array, battery package, inverter and charge controller. Diesel engine, alternator, control panel with monitoring gauges/indicators, starting equipment, fuel tank as well as other accessories. Charger to charge battery package by diesel gen set and PV solar system interface between diesel gen set and PV solar power unit for a smooth operation for the two energy sources in conjunction, automatically without any manual intervention. Factory test certificates must be included and must be in accordance to internationally recognised standards. Suitable for tropical conditions. | Comply and state → | Yes / No
KEY DATA
Make | Please state →
Model | Please state →
Country of origin | Please state →
DIESEL GEN SET
Rated power output, min. 60kVA | Comply and state → | Yes / No
Power factor: 0.8 | Comply and state → | Yes / No
Rated power output, 48 kW, min. | Comply and state → | Yes / No
Voltage, 220/230/240 and 380/400 V | Comply and state → | Yes / No
Phase: 1 and 3 | Comply and state → | Yes / No
AC frequency, 50/60 Hz | Comply and state → | Yes / No
Speed: rpm 1500 or 3000 or other | Please state →
Prime power according to ISO 8528 or equivalent, i.e. power available at variable load with no limitations on hours of operation and capable of min. 10% overload for min. 1 hour in any 12 hours. | Comply and state → | Yes / No
Prime rating of min. the stated output rating at Normal Temperature and Pressure conditions (NTP). Please state | Comply and state → | Yes / No
Derating information (temperature, altitude and humidity), please state | Please state →
Engine
Make | Please state →
Model | Please state →
Engine power output, kW at rpm: | Please state →
Fuel: Diesel | Comply and state → | Yes / No
Cooling, liquid or air or combined, suitable for tropical conditions | Please state →
Speed governor, state type | Please state →
Exhaust with suitable piping and residential silencer | Comply and state → | Yes / No
Noise level, dB(A) at 1 m (silencer fitted) | Please state →
Fuel consumption at 75% load: L/hour | Please state →
CO2 emissions at 75% load: g/hour | Please state →
Mounted on anti-vibration mounts | Comply and state → | Yes / No
ENVIRONMENTAL
EU Non-road emissions regulations schedule, e.g. EU STAGE II, III A, III B, IV. US Non-road and stationary emissions regulations to Tier 1,2,3,4 or equivalent. Please state. | Comply and state → | Yes / No
Alternator
Make: | Please state →
Model: | Please state →
Brushless type | Comply and state → | Yes / No
Cooling, liquid, air, other | Please state →
Protection class min. IP 23 | Comply and state → | Yes / No
Suitable AC power outlets protected by circuit breaker (state type) | Comply and state → | Yes / No
Insulation to min. IEC 60085 - >155 ° C - (F) or equivalent | Comply and state → | Yes / No
Voltage regulator | Comply and state → | Yes / No
Standard accessories
Fuel tank. Integrated or separate, suitable for continuous operation of min. 8 hours at rated capacity. State capacity, litres. Fuel level gauge. Including all necessary pipework, connections etc. Possibility for connection to external tank. | Comply and state→ | Yes / No
Low oil pressure protection, automatic shut down | Comply and state → | Yes / No
Over heating protection | Comply and state → | Yes / No
Overload protection | Comply and state → | Yes / No
Emergency stop | Comply and state → | Yes / No
Electric starter with key and battery | Comply and state → | Yes / No
Min. Voltmeter, ammeter, hour meter, Hz meter, water temp gauge/indicator (where applicable) | Comply and state → | Yes / No
Earthing/grounding facility | Comply and state → | Yes / No
PV SOLAR POWER SYSTEM STANDARD ARRAY NOMINAL MIN. 19.2 kWp. Battery pack 48 kWh. For Sloped Roof or Gen set mount.
PV solar array
Make and model: | Please state →
Array kWp, min 40% of diesel generator set max output which is 60 kVA/48 kW, hence = 19.2 kWp min. | Comply and state→ | Yes / No
PV panels, total surface covering, m2 | Please state →
Nominal power output each panel, kWp | Please state →
Isc array, A (Amp) | Please state →
Certifications: Any one or more of IEC61215, UL1703 or equivalent | Comply and state → | Yes / No
Charge controller
Make and model: | Please state →
Type: MTTP | Comply and state → | Yes / No
Certifications. Any one or more of EN60730-1/2-11, 55022, 61000-4-27374/5/6 or equivalent | Comply and state→ | Yes / No
Capacity: Isc array +20%, min. | Comply and state→ | Yes / No
Inverter
Make and model: | Please state →
Capacity, A (Amp): Min. equivalent to max load | Comply and state→ | Yes / No
Pure sine curve | Comply and state → | Yes / No
Certifications: Any one or more of EN50178, 62040, 60950, 61000-2/3/6, EN60529, 50438 or equivalent | Comply and state → | Yes / No
Battery package
Make and model: | Please state →
Capacity: Min. equivalent to hybrid diesel gen set full load - 24 kW - for 1 hour = 48 kWh. | Comply and state→ | Yes / No
Battery type: LiFePo4 | Comply and state→ | Yes / No
Certifications,: Any one or more of UL1642, IEC62133, 61000-6-3 or equivalent | Comply and state→ | Yes / No
PV panel racks, brackets, cables, fittings etc. | Comply and state→
PV panels racks for Ground or flat roof mount. | Comply and state→ | Yes / No
All cables, junctions, contacts, breakers, earthing spears, fittings, screws, nut and bots etc included | Comply and state → | Yes / No
Installation
The system must be plug and play. Inverter, charge controller, battery package, battery charger must be pre-installed and wired either inside one common Hybrid system cage or in a separate cabinet, in order to easily connect the PV array and the local installation. All cables for establishing the PV array must be readily available with pre-installed connections and clearly marked in a way that no mistakes can occur. | Comply and state → | Yes / No
Other
Lifting points for handling | Comply and state → | Yes / No
Installation instructions, drawings, photos, brochures etc. English/French/Spanish | Comply and state → | Yes / No
Operators and maintenance manual, English/French/Spanish | Comply and state → | Yes / No
Tool kit | Comply and state → | Yes / No
Basic maintenance kit, engine: Min. 4 x oil filters, 2 x air filters, 2 x fuel filters | Comply and state → | Yes / No
Dimensions, L x W x H, mm | Please state →
Weight, dry, entire hybrid system incl. Battery package and all PV panels, cables, brackets etc etc.: kg: | Please state →
WARRANTY
Diesel Generator set: 2 years/2500 hours of operation which ever occur first. PV panels: Min. 10 years. Min. 90% performance guarantee at 10 years. Min. 80% performance guarantee at 20 years. Battery package: Min. 5 years. Inverter/charge controller/charger: Min. 4 years. Other equipment: Min. 2 years | Comply and state → | Yes / No
Sustainability
The bidder must demonstrate that its organisation has an environmental management system in place which as a minimum shall submit at least one or more of the following : the environmental policy principles of the organisation; the management measures and procedures taken or that will be taken to assess, monitor, measure and mitigate environmental impacts of the business processes/products associated with the execution of the contract; how attention is paid to the awareness and training/competency of employee(s) and supplier(s) with regard to dealing with the environmental aspects relevant to this bid; and that compliance with the environmental legislation applicable to the required performance(s) is guaranteed, ISO 14001 certificate, EMAS or an equivalent certificate | Comply and state → | Yes / No
The bidder shall provide documentation which outlines their approach to ensuring equal opportunity, diversity and inclusion within their organisation (e.g. equal pay policy, parental leave, ratio of females/males employees, % of female in management positions, grievances disaggregated by gender, transparency of promotion criteria, sexual harassment policies) | Comply and state → | Yes / No
Mandatory Options
Diesel engine spare parts & maintenance kit for min. 2500 hours of operation | Mandatory | enter prices on Form C: Price Schedule
Sound insolating and water proof canopy (max. 70 dB(A) at 7 m) | Mandatory | enter prices on Form C: Price Schedule
Work shop manual | Mandatory | enter prices on Form C: Price Schedule
Spare parts catalogue | Mandatory | enter prices on Form C: Price Schedule
60 Hz version of Generator set, please enter any surcharge to the std 50 Hz version offered above | Mandatory | enter prices on Form C: Price Schedule
Suggested Options
Heavy duty air filter for dusty conditions | Please provide price or state STD→ | Submit other option prices on a separate form
Heavy duty fuel filter/additional fuel filter in line with original | Please provide price or state STD→ | Submit other option prices on a separate form
Additional silencer, state dB(A) at 1 m and/or 7 m | Please provide price or state STD→ | Submit other option prices on a separate form
High chimney for exhaust, state height and materials | Please provide price or state STD→ | Submit other option prices on a separate form
(ATS) Automatic Transfer Switch | Please provide price or state STD→ | Submit other option prices on a separate form
Over speed protection | Please provide price or state STD→ | Submit other option prices on a separate form
Manual transfer switch | Please provide price or state STD→ | Submit other option prices on a separate form
External fuel tank with pipes including min.. 10 meter non-corrosive material and fittings, state volume of tank and material | Please provide price or state STD→ | Submit other option prices on a separate form
Slow moving trolley/trailer | Please provide price or state STD→ | Submit other option prices on a separate form
(AMF) Automatic Mains Failure Power generation set | Please provide price or state STD→ | Submit other option prices on a separate form
Automatic main circuit breaker | Please provide price or state STD→ | Submit other option prices on a separate form
Installation instructions and eventual. drawings, other languages | Please provide price or state STD→ | Submit other option prices on a separate form
Change over switch positions for: 1) Mains 2) Off 3) GENERATOR SET | Please provide price or state STD→ | Submit other option prices on a separate form
Automatic main circuit breaker | Please provide price or state STD→ | Submit other option prices on a separate form
Operators and maintenance manual, other languages | Please provide price or state STD→ | Submit other option prices on a separate form

## Lot 13 80 kVA PV 10% Roof
Bidder name:
Make and model:
Lot 13 80 kVA PV 10% Sloped Roof or Gen set mount.
HYBRID PV SOLAR/DIESEL GENERATOR SET SPECS | UNOPS REQUIREMENTS | Bidder: Compliant/Non-compliant to UNOPS requirements? Please mark YES/NO in this coloumn. Not indicating YES/NO in this column may render your bid non-compliant. | Bidders are required to provide information in this column on the specifications of their bid to demonstrate compliance to set specifications. Not providing specifications under this column may render your bid non-compliant.
Complete Hybrid PV solar/diesel generator set for autonomous operation, including PV solar power array, battery package, inverter and charge controller. Diesel engine, alternator, control panel with monitoring gauges/indicators, starting equipment, fuel tank as well as other accessories. Charger to charge battery package by diesel gen set and PV solar system interface between diesel gen set and PV solar power unit for a smooth operation for the two energy sources in conjunction, automatically without any manual intervention. Factory test certificates must be included and must be in accordance to internationally recognised standards. Suitable for tropical conditions. | Comply and state → | Yes / No
KEY DATA
Make | Please state →
Model | Please state →
Country of origin | Please state →
DIESEL GEN SET
Rated power output, min. 80kVA | Comply and state → | Yes / No
Power factor: 0.8 | Comply and state → | Yes / No
Rated power output, 64 kW, min. | Comply and state → | Yes / No
Voltage, 220/230/240 and 380/400 V | Comply and state → | Yes / No
Phase: 1 and 3 | Comply and state → | Yes / No
AC frequency, 50/60 Hz | Comply and state → | Yes / No
Speed: rpm 1500 or 3000 or other | Please state →
Prime power according to ISO 8528 or equivalent, i.e. power available at variable load with no limitations on hours of operation and capable of min. 10% overload for min. 1 hour in any 12 hours. | Comply and state → | Yes / No
Prime rating of min. the stated output rating at Normal Temperature and Pressure conditions (NTP). Please state | Comply and state → | Yes / No
Derating information (temperature, altitude and humidity), please state | Please state →
Engine
Make | Please state →
Model | Please state →
Engine power output, kW at rpm: | Please state →
Fuel: Diesel | Comply and state → | Yes / No
Cooling, liquid or air or combined, suitable for tropical conditions | Please state →
Speed governor, state type | Please state →
Exhaust with suitable piping and residential silencer | Comply and state → | Yes / No
Noise level, dB(A) at 1 m (silencer fitted) | Please state →
Fuel consumption at 75% load: L/hour | Please state →
CO2 emissions at 75% load: g/hour | Please state →
Mounted on anti-vibration mounts | Comply and state → | Yes / No
ENVIRONMENTAL
EU Non-road emissions regulations schedule, e.g. EU STAGE II, III A, III B, IV. US Non-road and stationary emissions regulations to Tier 1,2,3,4 or equivalent. Please state. | Comply and state → | Yes / No
Alternator
Make: | Please state →
Model: | Please state →
Brushless type | Comply and state → | Yes / No
Cooling, liquid, air, other | Please state →
Protection class min. IP 23 | Comply and state → | Yes / No
Suitable AC power outlets protected by circuit breaker (state type) | Comply and state → | Yes / No
Insulation to min. IEC 60085 - >155 ° C - (F) or equivalent | Comply and state → | Yes / No
Voltage regulator | Comply and state → | Yes / No
Standard accessories
Fuel tank. Integrated or separate, suitable for continuous operation of min. 8 hours at rated capacity. State capacity, litres. Fuel level gauge. Including all necessary pipework, connections etc. Possibility for connection to external tank. | Comply and state→ | Yes / No
Low oil pressure protection, automatic shut down | Comply and state → | Yes / No
Over heating protection | Comply and state → | Yes / No
Overload protection | Comply and state → | Yes / No
Emergency stop | Comply and state → | Yes / No
Electric starter with key and battery | Comply and state → | Yes / No
Min. Voltmeter, ammeter, hour meter, Hz meter, water temp gauge/indicator (where applicable) | Comply and state → | Yes / No
Earthing/grounding facility | Comply and state → | Yes / No
PV SOLAR POWER SYSTEM STANDARD ARRAY NOMINAL MIN. 6.4 kWp. Battery pack 64 kWh. For Sloped Roof or Gen set mount.
PV solar array
Make and model: | Please state →
Array kWp, min 10% of diesel generator set max output which is 80kVA/64 kW, hence = 6.4 kWp min. | Comply and state→ | Yes / No
PV panels, total surface covering, m2 | Please state →
Nominal power output each panel, kWp | Please state →
Isc array, A (Amp) | Please state →
Certifications: Any one or more of IEC61215, UL1703 or equivalent | Comply and state → | Yes / No
Charge controller
Make and model: | Please state →
Type: MTTP | Comply and state → | Yes / No
Certifications. Any one or more of EN60730-1/2-11, 55022, 61000-4-27374/5/6 or equivalent | Comply and state→ | Yes / No
Capacity: Isc array +20%, min. | Comply and state→ | Yes / No
Inverter
Make and model: | Please state →
Capacity, A (Amp): Min. equivalent to max load | Comply and state→ | Yes / No
Pure sine curve | Comply and state → | Yes / No
Certifications: Any one or more of EN50178, 62040, 60950, 61000-2/3/6, EN60529, 50438 or equivalent | Comply and state → | Yes / No
Battery package
Make and model: | Please state →
Capacity: Min. equivalent to hybrid diesel gen set full load - 24 kW - for 1 hour = 64 kWh. | Comply and state→ | Yes / No
Battery type: LiFePo4 | Comply and state→ | Yes / No
Certifications,: Any one or more of UL1642, IEC62133, 61000-6-3 or equivalent | Comply and state→ | Yes / No
PV panel racks, brackets, cables, fittings etc.
PV panels racks for sloped roof mount included for all included PV panels, if not attached to the Hybrid Gen set system itself (permanently or fold-out system etc). | Comply and state→ | Yes / No
All cables, junctions, contacts, breakers, earthing spears, fittings, screws, nut and bots etc included | Comply and state → | Yes / No
Installation
The system must be plug and play. Inverter, charge controller, battery package, battery charger must be pre-installed and wired either inside one common Hybrid system cage or in a separate cabinet, in order to easily connect the PV array and the local installation. All cables for establishing the PV array must be readily available with pre-installed connections and clearly marked in a way that no mistakes can occur. | Comply and state → | Yes / No
Other
Lifting points for handling | Comply and state → | Yes / No
Installation instructions, drawings, photos, brochures etc. English/French/Spanish | Comply and state → | Yes / No
Operators and maintenance manual, English/French/Spanish | Comply and state → | Yes / No
Tool kit | Comply and state → | Yes / No
Basic maintenance kit, engine: Min. 4 x oil filters, 2 x air filters, 2 x fuel filters | Comply and state → | Yes / No
Dimensions, L x W x H, mm | Please state →
Weight, dry, entire hybrid system incl. Battery package and all PV panels, cables, brackets etc etc.: kg: | Please state →
WARRANTY
Diesel Generator set: 2 years/2500 hours of operation which ever occur first. PV panels: Min. 10 years. Min. 90% performance guarantee at 10 years. Min. 80% performance guarantee at 20 years. Battery package: Min. 5 years. Inverter/charge controller/charger: Min. 4 years. Other equipment: Min. 2 years | Comply and state → | Yes / No
Sustainability
The bidder must demonstrate that its organisation has an environmental management system in place which as a minimum shall submit at least one or more of the following : the environmental policy principles of the organisation; the management measures and procedures taken or that will be taken to assess, monitor, measure and mitigate environmental impacts of the business processes/products associated with the execution of the contract; how attention is paid to the awareness and training/competency of employee(s) and supplier(s) with regard to dealing with the environmental aspects relevant to this bid; and that compliance with the environmental legislation applicable to the required performance(s) is guaranteed, ISO 14001 certificate, EMAS or an equivalent certificate | Comply and state → | Yes / No
The bidder shall provide documentation which outlines their approach to ensuring equal opportunity, diversity and inclusion within their organisation (e.g. equal pay policy, parental leave, ratio of females/males employees, % of female in management positions, grievances disaggregated by gender, transparency of promotion criteria, sexual harassment policies) | Comply and state → | Yes / No
Mandatory Options
Diesel engine spare parts & maintenance kit for min. 2500 hours of operation | Mandatory | enter prices on Form C: Price Schedule
Sound insolating and water proof canopy (max. 70 dB(A) at 7 m) | Mandatory | enter prices on Form C: Price Schedule
Work shop manual | Mandatory | enter prices on Form C: Price Schedule
Spare parts catalogue | Mandatory | enter prices on Form C: Price Schedule
60 Hz version of Generator set, please enter any surcharge to the std 50 Hz version offered above | Mandatory | enter prices on Form C: Price Schedule
Suggested Options
Heavy duty air filter for dusty conditions | Please provide price or state STD→ | Submit other option prices on a separate form
Heavy duty fuel filter/additional fuel filter in line with original | Please provide price or state STD→ | Submit other option prices on a separate form
Additional silencer, state dB(A) at 1 m and/or 7 m | Please provide price or state STD→ | Submit other option prices on a separate form
High chimney for exhaust, state height and materials | Please provide price or state STD→ | Submit other option prices on a separate form
(ATS) Automatic Transfer Switch | Please provide price or state STD→ | Submit other option prices on a separate form
Over speed protection | Please provide price or state STD→ | Submit other option prices on a separate form
Manual transfer switch | Please provide price or state STD→ | Submit other option prices on a separate form
External fuel tank with pipes including min.. 10 meter non-corrosive material and fittings, state volume of tank and material | Please provide price or state STD→ | Submit other option prices on a separate form
Slow moving trolley/trailer | Please provide price or state STD→ | Submit other option prices on a separate form
(AMF) Automatic Mains Failure Power generation set | Please provide price or state STD→ | Submit other option prices on a separate form
Automatic main circuit breaker | Please provide price or state STD→ | Submit other option prices on a separate form
Installation instructions and eventual. drawings, other languages | Please provide price or state STD→ | Submit other option prices on a separate form
Change over switch positions for: 1) Mains 2) Off 3) GENERATOR SET | Please provide price or state STD→ | Submit other option prices on a separate form
Automatic main circuit breaker | Please provide price or state STD→ | Submit other option prices on a separate form
Operators and maintenance manual, other languages | Please provide price or state STD→ | Submit other option prices on a separate form

## Lot 14 80 kVA PV 20% Roof
Bidder name:
Make and model:
Lot 14 80 kVA PV 20% Sloped Roof or Gen set mount.
HYBRID PV SOLAR/DIESEL GENERATOR SET SPECS | UNOPS REQUIREMENTS | Bidder: Compliant/Non-compliant to UNOPS requirements? Please mark YES/NO in this coloumn. Not indicating YES/NO in this column may render your bid non-compliant. | Bidders are required to provide information in this column on the specifications of their bid to demonstrate compliance to set specifications. Not providing specifications under this column may render your bid non-compliant.
Complete Hybrid PV solar/diesel generator set for autonomous operation, including PV solar power array, battery package, inverter and charge controller. Diesel engine, alternator, control panel with monitoring gauges/indicators, starting equipment, fuel tank as well as other accessories. Charger to charge battery package by diesel gen set and PV solar system interface between diesel gen set and PV solar power unit for a smooth operation for the two energy sources in conjunction, automatically without any manual intervention. Factory test certificates must be included and must be in accordance to internationally recognised standards. Suitable for tropical conditions. | Comply and state → | Yes / No
KEY DATA
Make | Please state →
Model | Please state →
Country of origin | Please state →
DIESEL GEN SET
Rated power output, min. 80kVA | Comply and state → | Yes / No
Power factor: 0.8 | Comply and state → | Yes / No
Rated power output, 64 kW, min. | Comply and state → | Yes / No
Voltage, 220/230/240 and 380/400 V | Comply and state → | Yes / No
Phase: 1 and 3 | Comply and state → | Yes / No
AC frequency, 50/60 Hz | Comply and state → | Yes / No
Speed: rpm 1500 or 3000 or other | Please state →
Prime power according to ISO 8528 or equivalent, i.e. power available at variable load with no limitations on hours of operation and capable of min. 10% overload for min. 1 hour in any 12 hours. | Comply and state → | Yes / No
Prime rating of min. the stated output rating at Normal Temperature and Pressure conditions (NTP). Please state | Comply and state → | Yes / No
Derating information (temperature, altitude and humidity), please state | Please state →
Engine
Make | Please state →
Model | Please state →
Engine power output, kW at rpm: | Please state →
Fuel: Diesel | Comply and state → | Yes / No
Cooling, liquid or air or combined, suitable for tropical conditions | Please state →
Speed governor, state type | Please state →
Exhaust with suitable piping and residential silencer | Comply and state → | Yes / No
Noise level, dB(A) at 1 m (silencer fitted) | Please state →
Fuel consumption at 75% load: L/hour | Please state →
CO2 emissions at 75% load: g/hour | Please state →
Mounted on anti-vibration mounts | Comply and state → | Yes / No
ENVIRONMENTAL
EU Non-road emissions regulations schedule, e.g. EU STAGE II, III A, III B, IV. US Non-road and stationary emissions regulations to Tier 1,2,3,4 or equivalent. Please state. | Comply and state → | Yes / No
Alternator
Make: | Please state →
Model: | Please state →
Brushless type | Comply and state → | Yes / No
Cooling, liquid, air, other | Please state →
Protection class min. IP 23 | Comply and state → | Yes / No
Suitable AC power outlets protected by circuit breaker (state type) | Comply and state → | Yes / No
Insulation to min. IEC 60085 - >155 ° C - (F) or equivalent | Comply and state → | Yes / No
Voltage regulator | Comply and state → | Yes / No
Standard accessories
Fuel tank. Integrated or separate, suitable for continuous operation of min. 8 hours at rated capacity. State capacity, litres. Fuel level gauge. Including all necessary pipework, connections etc. Possibility for connection to external tank. | Comply and state→ | Yes / No
Low oil pressure protection, automatic shut down | Comply and state → | Yes / No
Over heating protection | Comply and state → | Yes / No
Overload protection | Comply and state → | Yes / No
Emergency stop | Comply and state → | Yes / No
Electric starter with key and battery | Comply and state → | Yes / No
Min. Voltmeter, ammeter, hour meter, Hz meter, water temp gauge/indicator (where applicable) | Comply and state → | Yes / No
Earthing/grounding facility | Comply and state → | Yes / No
PV SOLAR POWER SYSTEM STANDARD ARRAY NOMINAL MIN. 12.8 kWp. Battery pack 64 kWh. For Sloped Roof or Gen set mount.
PV solar array
Make and model: | Please state →
Array kWp, min 20% of diesel generator set max output which is 80kVA/64 kW, hence = 12.8 kWp min. | Comply and state→ | Yes / No
PV panels, total surface covering, m2 | Please state →
Nominal power output each panel, kWp | Please state →
Isc array, A (Amp) | Please state →
Certifications: Any one or more of IEC61215, UL1703 or equivalent | Comply and state → | Yes / No
Charge controller
Make and model: | Please state →
Type: MTTP | Comply and state → | Yes / No
Certifications. Any one or more of EN60730-1/2-11, 55022, 61000-4-27374/5/6 or equivalent | Comply and state→ | Yes / No
Capacity: Isc array +20%, min. | Comply and state→ | Yes / No
Inverter
Make and model: | Please state →
Capacity, A (Amp): Min. equivalent to max load | Comply and state→ | Yes / No
Pure sine curve | Comply and state → | Yes / No
Certifications: Any one or more of EN50178, 62040, 60950, 61000-2/3/6, EN60529, 50438 or equivalent | Comply and state → | Yes / No
Battery package
Make and model: | Please state →
Capacity: Min. equivalent to hybrid diesel gen set full load - 24 kW - for 1 hour = 64 kWh. | Comply and state→ | Yes / No
Battery type: LiFePo4 | Comply and state→ | Yes / No
Certifications,: Any one or more of UL1642, IEC62133, 61000-6-3 or equivalent | Comply and state→ | Yes / No
PV panel racks, brackets, cables, fittings etc.
PV panels racks for sloped roof mount included for all included PV panels, if not attached to the Hybrid Gen set system itself (permanently or fold-out system etc). | Comply and state→ | Yes / No
All cables, junctions, contacts, breakers, earthing spears, fittings, screws, nut and bots etc included | Comply and state → | Yes / No
Installation
The system must be plug and play. Inverter, charge controller, battery package, battery charger must be pre-installed and wired either inside one common Hybrid system cage or in a separate cabinet, in order to easily connect the PV array and the local installation. All cables for establishing the PV array must be readily available with pre-installed connections and clearly marked in a way that no mistakes can occur. | Comply and state → | Yes / No
Other
Lifting points for handling | Comply and state → | Yes / No
Installation instructions, drawings, photos, brochures etc. English/French/Spanish | Comply and state → | Yes / No
Operators and maintenance manual, English/French/Spanish | Comply and state → | Yes / No
Tool kit | Comply and state → | Yes / No
Basic maintenance kit, engine: Min. 4 x oil filters, 2 x air filters, 2 x fuel filters | Comply and state → | Yes / No
Dimensions, L x W x H, mm | Please state →
Weight, dry, entire hybrid system incl. Battery package and all PV panels, cables, brackets etc etc.: kg: | Please state →
WARRANTY
Diesel Generator set: 2 years/2500 hours of operation which ever occur first. PV panels: Min. 10 years. Min. 90% performance guarantee at 10 years. Min. 80% performance guarantee at 20 years. Battery package: Min. 5 years. Inverter/charge controller/charger: Min. 4 years. Other equipment: Min. 2 years | Comply and state → | Yes / No
Sustainability
The bidder must demonstrate that its organisation has an environmental management system in place which as a minimum shall submit at least one or more of the following : the environmental policy principles of the organisation; the management measures and procedures taken or that will be taken to assess, monitor, measure and mitigate environmental impacts of the business processes/products associated with the execution of the contract; how attention is paid to the awareness and training/competency of employee(s) and supplier(s) with regard to dealing with the environmental aspects relevant to this bid; and that compliance with the environmental legislation applicable to the required performance(s) is guaranteed, ISO 14001 certificate, EMAS or an equivalent certificate | Comply and state → | Yes / No
The bidder shall provide documentation which outlines their approach to ensuring equal opportunity, diversity and inclusion within their organisation (e.g. equal pay policy, parental leave, ratio of females/males employees, % of female in management positions, grievances disaggregated by gender, transparency of promotion criteria, sexual harassment policies) | Comply and state → | Yes / No
Mandatory Options
Diesel engine spare parts & maintenance kit for min. 2500 hours of operation | Mandatory | enter prices on Form C: Price Schedule
Sound insolating and water proof canopy (max. 70 dB(A) at 7 m) | Mandatory | enter prices on Form C: Price Schedule
Work shop manual | Mandatory | enter prices on Form C: Price Schedule
Spare parts catalogue | Mandatory | enter prices on Form C: Price Schedule
60 Hz version of Generator set, please enter any surcharge to the std 50 Hz version offered above | Mandatory | enter prices on Form C: Price Schedule
Suggested Options
Heavy duty air filter for dusty conditions | Please provide price or state STD→ | Submit other option prices on a separate form
Heavy duty fuel filter/additional fuel filter in line with original | Please provide price or state STD→ | Submit other option prices on a separate form
Additional silencer, state dB(A) at 1 m and/or 7 m | Please provide price or state STD→ | Submit other option prices on a separate form
High chimney for exhaust, state height and materials | Please provide price or state STD→ | Submit other option prices on a separate form
(ATS) Automatic Transfer Switch | Please provide price or state STD→ | Submit other option prices on a separate form
Over speed protection | Please provide price or state STD→ | Submit other option prices on a separate form
Manual transfer switch | Please provide price or state STD→ | Submit other option prices on a separate form
External fuel tank with pipes including min.. 10 meter non-corrosive material and fittings, state volume of tank and material | Please provide price or state STD→ | Submit other option prices on a separate form
Slow moving trolley/trailer | Please provide price or state STD→ | Submit other option prices on a separate form
(AMF) Automatic Mains Failure Power generation set | Please provide price or state STD→ | Submit other option prices on a separate form
Automatic main circuit breaker | Please provide price or state STD→ | Submit other option prices on a separate form
Installation instructions and eventual. drawings, other languages | Please provide price or state STD→ | Submit other option prices on a separate form
Change over switch positions for: 1) Mains 2) Off 3) GENERATOR SET | Please provide price or state STD→ | Submit other option prices on a separate form
Automatic main circuit breaker | Please provide price or state STD→ | Submit other option prices on a separate form
Operators and maintenance manual, other languages | Please provide price or state STD→ | Submit other option prices on a separate form

## Lot 15 80 kVA PV 40% Roof
Bidder name:
Make and model:
Lot 15 80 kVA PV 40% Sloped Roof or Gen set mount.
HYBRID PV SOLAR/DIESEL GENERATOR SET SPECS | UNOPS REQUIREMENTS | Bidder: Compliant/Non-compliant to UNOPS requirements? Please mark YES/NO in this coloumn. Not indicating YES/NO in this column may render your bid non-compliant. | Bidders are required to provide information in this column on the specifications of their bid to demonstrate compliance to set specifications. Not providing specifications under this column may render your bid non-compliant.
Complete Hybrid PV solar/diesel generator set for autonomous operation, including PV solar power array, battery package, inverter and charge controller. Diesel engine, alternator, control panel with monitoring gauges/indicators, starting equipment, fuel tank as well as other accessories. Charger to charge battery package by diesel gen set and PV solar system interface between diesel gen set and PV solar power unit for a smooth operation for the two energy sources in conjunction, automatically without any manual intervention. Factory test certificates must be included and must be in accordance to internationally recognised standards. Suitable for tropical conditions. | Comply and state → | Yes / No
KEY DATA
Make | Please state →
Model | Please state →
Country of origin | Please state →
DIESEL GEN SET
Rated power output, min. 80kVA | Comply and state → | Yes / No
Power factor: 0.8 | Comply and state → | Yes / No
Rated power output, 64 kW, min. | Comply and state → | Yes / No
Voltage, 220/230/240 and 380/400 V | Comply and state → | Yes / No
Phase: 1 and 3 | Comply and state → | Yes / No
AC frequency, 50/60 Hz | Comply and state → | Yes / No
Speed: rpm 1500 or 3000 or other | Please state →
Prime power according to ISO 8528 or equivalent, i.e. power available at variable load with no limitations on hours of operation and capable of min. 10% overload for min. 1 hour in any 12 hours. | Comply and state → | Yes / No
Prime rating of min. the stated output rating at Normal Temperature and Pressure conditions (NTP). Please state | Comply and state → | Yes / No
Derating information (temperature, altitude and humidity), please state | Please state →
Engine
Make | Please state →
Model | Please state →
Engine power output, kW at rpm: | Please state →
Fuel: Diesel | Comply and state → | Yes / No
Cooling, liquid or air or combined, suitable for tropical conditions | Please state →
Speed governor, state type | Please state →
Exhaust with suitable piping and residential silencer | Comply and state → | Yes / No
Noise level, dB(A) at 1 m (silencer fitted) | Please state →
Fuel consumption at 75% load: L/hour | Please state →
CO2 emissions at 75% load: g/hour | Please state →
Mounted on anti-vibration mounts | Comply and state → | Yes / No
ENVIRONMENTAL
EU Non-road emissions regulations schedule, e.g. EU STAGE II, III A, III B, IV. US Non-road and stationary emissions regulations to Tier 1,2,3,4 or equivalent. Please state. | Comply and state → | Yes / No
Alternator
Make: | Please state →
Model: | Please state →
Brushless type | Comply and state → | Yes / No
Cooling, liquid, air, other | Please state →
Protection class min. IP 23 | Comply and state → | Yes / No
Suitable AC power outlets protected by circuit breaker (state type) | Comply and state → | Yes / No
Insulation to min. IEC 60085 - >155 ° C - (F) or equivalent | Comply and state → | Yes / No
Voltage regulator | Comply and state → | Yes / No
Standard accessories
Fuel tank. Integrated or separate, suitable for continuous operation of min. 8 hours at rated capacity. State capacity, litres. Fuel level gauge. Including all necessary pipework, connections etc. Possibility for connection to external tank. | Comply and state→ | Yes / No
Low oil pressure protection, automatic shut down | Comply and state → | Yes / No
Over heating protection | Comply and state → | Yes / No
Overload protection | Comply and state → | Yes / No
Emergency stop | Comply and state → | Yes / No
Electric starter with key and battery | Comply and state → | Yes / No
Min. Voltmeter, ammeter, hour meter, Hz meter, water temp gauge/indicator (where applicable) | Comply and state → | Yes / No
Earthing/grounding facility | Comply and state → | Yes / No
PV SOLAR POWER SYSTEM STANDARD ARRAY NOMINAL MIN. 25.6 kWp. Battery pack 64 kWh. For Sloped Roof or Gen set mount.
PV solar array
Make and model: | Please state →
Array kWp, min 40% of diesel generator set max output which is 80kVA/64 kW, hence = 25.6 kWp min. | Comply and state→ | Yes / No
PV panels, total surface covering, m2 | Please state →
Nominal power output each panel, kWp | Please state →
Isc array, A (Amp) | Please state →
Certifications: Any one or more of IEC61215, UL1703 or equivalent | Comply and state → | Yes / No
Charge controller
Make and model: | Please state →
Type: MTTP | Comply and state → | Yes / No
Certifications. Any one or more of EN60730-1/2-11, 55022, 61000-4-27374/5/6 or equivalent | Comply and state→ | Yes / No
Capacity: Isc array +20%, min. | Comply and state→ | Yes / No
Inverter
Make and model: | Please state →
Capacity, A (Amp): Min. equivalent to max load | Comply and state→ | Yes / No
Pure sine curve | Comply and state → | Yes / No
Certifications: Any one or more of EN50178, 62040, 60950, 61000-2/3/6, EN60529, 50438 or equivalent | Comply and state → | Yes / No
Battery package
Make and model: | Please state →
Capacity: Min. equivalent to hybrid diesel gen set full load - 24 kW - for 1 hour = 64 kWh. | Comply and state→ | Yes / No
Battery type: LiFePo4 | Comply and state→ | Yes / No
Certifications,: Any one or more of UL1642, IEC62133, 61000-6-3 or equivalent | Comply and state→ | Yes / No
PV panel racks, brackets, cables, fittings etc.
PV panels racks for sloped roof mount included for all included PV panels, if not attached to the Hybrid Gen set system itself (permanently or fold-out system etc). | Comply and state→ | Yes / No
All cables, junctions, contacts, breakers, earthing spears, fittings, screws, nut and bots etc included | Comply and state → | Yes / No
Installation
The system must be plug and play. Inverter, charge controller, battery package, battery charger must be pre-installed and wired either inside one common Hybrid system cage or in a separate cabinet, in order to easily connect the PV array and the local installation. All cables for establishing the PV array must be readily available with pre-installed connections and clearly marked in a way that no mistakes can occur. | Comply and state → | Yes / No
Other
Lifting points for handling | Comply and state → | Yes / No
Installation instructions, drawings, photos, brochures etc. English/French/Spanish | Comply and state → | Yes / No
Operators and maintenance manual, English/French/Spanish | Comply and state → | Yes / No
Tool kit | Comply and state → | Yes / No
Basic maintenance kit, engine: Min. 4 x oil filters, 2 x air filters, 2 x fuel filters | Comply and state → | Yes / No
Dimensions, L x W x H, mm | Please state →
Weight, dry, entire hybrid system incl. Battery package and all PV panels, cables, brackets etc etc.: kg: | Please state →
WARRANTY
Diesel Generator set: 2 years/2500 hours of operation which ever occur first. PV panels: Min. 10 years. Min. 90% performance guarantee at 10 years. Min. 80% performance guarantee at 20 years. Battery package: Min. 5 years. Inverter/charge controller/charger: Min. 4 years. Other equipment: Min. 2 years | Comply and state → | Yes / No
Sustainability
The bidder must demonstrate that its organisation has an environmental management system in place which as a minimum shall submit at least one or more of the following : the environmental policy principles of the organisation; the management measures and procedures taken or that will be taken to assess, monitor, measure and mitigate environmental impacts of the business processes/products associated with the execution of the contract; how attention is paid to the awareness and training/competency of employee(s) and supplier(s) with regard to dealing with the environmental aspects relevant to this bid; and that compliance with the environmental legislation applicable to the required performance(s) is guaranteed, ISO 14001 certificate, EMAS or an equivalent certificate | Comply and state → | Yes / No
The bidder shall provide documentation which outlines their approach to ensuring equal opportunity, diversity and inclusion within their organisation (e.g. equal pay policy, parental leave, ratio of females/males employees, % of female in management positions, grievances disaggregated by gender, transparency of promotion criteria, sexual harassment policies) | Comply and state → | Yes / No
Mandatory Options
Diesel engine spare parts & maintenance kit for min. 2500 hours of operation | Mandatory | enter prices on Form C: Price Schedule
Sound insolating and water proof canopy (max. 70 dB(A) at 7 m) | Mandatory | enter prices on Form C: Price Schedule
Work shop manual | Mandatory | enter prices on Form C: Price Schedule
Spare parts catalogue | Mandatory | enter prices on Form C: Price Schedule
60 Hz version of Generator set, please enter any surcharge to the std 50 Hz version offered above | Mandatory | enter prices on Form C: Price Schedule
Suggested Options
Heavy duty air filter for dusty conditions | Please provide price or state STD→ | Submit other option prices on a separate form
Heavy duty fuel filter/additional fuel filter in line with original | Please provide price or state STD→ | Submit other option prices on a separate form
Additional silencer, state dB(A) at 1 m and/or 7 m | Please provide price or state STD→ | Submit other option prices on a separate form
High chimney for exhaust, state height and materials | Please provide price or state STD→ | Submit other option prices on a separate form
(ATS) Automatic Transfer Switch | Please provide price or state STD→ | Submit other option prices on a separate form
Over speed protection | Please provide price or state STD→ | Submit other option prices on a separate form
Manual transfer switch | Please provide price or state STD→ | Submit other option prices on a separate form
External fuel tank with pipes including min.. 10 meter non-corrosive material and fittings, state volume of tank and material | Please provide price or state STD→ | Submit other option prices on a separate form
Slow moving trolley/trailer | Please provide price or state STD→ | Submit other option prices on a separate form
(AMF) Automatic Mains Failure Power generation set | Please provide price or state STD→ | Submit other option prices on a separate form
Automatic main circuit breaker | Please provide price or state STD→ | Submit other option prices on a separate form
Installation instructions and eventual. drawings, other languages | Please provide price or state STD→ | Submit other option prices on a separate form
Change over switch positions for: 1) Mains 2) Off 3) GENERATOR SET | Please provide price or state STD→ | Submit other option prices on a separate form
Automatic main circuit breaker | Please provide price or state STD→ | Submit other option prices on a separate form
Operators and maintenance manual, other languages | Please provide price or state STD→ | Submit other option prices on a separate form

## Lot 16 80 kVA PV 10% Ground
Bidder name:
Make and model:
Lot 16. 80 kVA PV 10% Ground or flat roof mounted
HYBRID PV SOLAR/DIESEL GENERATOR SET SPECS | UNOPS REQUIREMENTS | Bidder: Compliant/Non-compliant to UNOPS requirements? Please mark YES/NO in this coloumn. Not indicating YES/NO in this column may render your bid non-compliant. | Bidders are required to provide information in this column on the specifications of their bid to demonstrate compliance to set specifications. Not providing specifications under this column may render your bid non-compliant.
Complete Hybrid PV solar/diesel generator set for autonomous operation, including PV solar power array, battery package, inverter and charge controller. Diesel engine, alternator, control panel with monitoring gauges/indicators, starting equipment, fuel tank as well as other accessories. Charger to charge battery package by diesel gen set and PV solar system interface between diesel gen set and PV solar power unit for a smooth operation for the two energy sources in conjunction, automatically without any manual intervention. Factory test certificates must be included and must be in accordance to internationally recognised standards. Suitable for tropical conditions. | Comply and state → | Yes / No
KEY DATA
Make | Please state →
Model | Please state →
Country of origin | Please state →
DIESEL GEN SET
Rated power output, min. 80 kVA | Comply and state → | Yes / No
Power factor: 0.8 | Comply and state → | Yes / No
Rated power output, 64 kW, min. | Comply and state → | Yes / No
Voltage, 220/230/240 and 380/400 V | Comply and state → | Yes / No
Phase: 1 and 3 | Comply and state → | Yes / No
AC frequency, 50/60 Hz | Comply and state → | Yes / No
Speed: rpm 1500 or 3000 or other | Please state →
Prime power according to ISO 8528 or equivalent, i.e. power available at variable load with no limitations on hours of operation and capable of min. 10% overload for min. 1 hour in any 12 hours. | Comply and state → | Yes / No
Prime rating of min. the stated output rating at Normal Temperature and Pressure conditions (NTP). Please state | Comply and state → | Yes / No
Derating information (temperature, altitude and humidity), please state | Please state →
Engine
Make | Please state →
Model | Please state →
Engine power output, kW at rpm: | Please state →
Fuel: Diesel | Comply and state → | Yes / No
Cooling, liquid or air or combined, suitable for tropical conditions | Please state →
Speed governor, state type | Please state →
Exhaust with suitable piping and residential silencer | Comply and state → | Yes / No
Noise level, dB(A) at 1 m (silencer fitted) | Please state →
Fuel consumption at 75% load: L/hour | Please state →
CO2 emissions at 75% load: g/hour | Please state →
Mounted on anti-vibration mounts | Comply and state → | Yes / No
ENVIRONMENTAL
EU Non-road emissions regulations schedule, e.g. EU STAGE II, III A, III B, IV. US Non-road and stationary emissions regulations to Tier 1,2,3,4 or equivalent. Please state. | Comply and state → | Yes / No
Alternator
Make: | Please state →
Model: | Please state →
Brushless type | Comply and state → | Yes / No
Cooling, liquid, air, other | Please state →
Protection class min. IP 23 | Comply and state → | Yes / No
Suitable AC power outlets protected by circuit breaker (state type) | Comply and state → | Yes / No
Insulation to min. IEC 60085 - >155 ° C - (F) or equivalent | Comply and state → | Yes / No
Voltage regulator | Comply and state → | Yes / No
Standard accessories
Fuel tank. Integrated or separate, suitable for continuous operation of min. 8 hours at rated capacity. State capacity, litres. Fuel level gauge. Including all necessary pipework, connections etc. Possibility for connection to external tank. | Comply and state→ | Yes / No
Low oil pressure protection, automatic shut down | Comply and state → | Yes / No
Over heating protection | Comply and state → | Yes / No
Overload protection | Comply and state → | Yes / No
Emergency stop | Comply and state → | Yes / No
Electric starter with key and battery | Comply and state → | Yes / No
Min. Voltmeter, ammeter, hour meter, Hz meter, water temp gauge/indicator (where applicable) | Comply and state → | Yes / No
Earthing/grounding facility | Comply and state → | Yes / No
PV SOLAR POWER SYSTEM STANDARD ARRAY NOMINAL MIN. 6.4 kWp. Battery pack 64 kWh. For Ground or flat roof mount
PV solar array
Make and model: | Please state →
Array kWp, min 10% of diesel generator set max output which is 80kVA/64 kW, hence = 6.4kWp min. | Comply and state→ | Yes / No
PV panels, total surface covering, m2 | Please state →
Nominal power output each panel, kWp | Please state →
Isc array, A (Amp) | Please state →
Certifications: Any one or more of IEC61215, UL1703 or equivalent | Comply and state → | Yes / No
Charge controller
Make and model: | Please state →
Type: MTTP | Comply and state → | Yes / No
Certifications. Any one or more of EN60730-1/2-11, 55022, 61000-4-27374/5/6 or equivalent | Comply and state→ | Yes / No
Capacity: Isc array +20%, min. | Comply and state→ | Yes / No
Inverter
Make and model: | Please state →
Capacity, A (Amp): Min. equivalent to max load | Comply and state→ | Yes / No
Pure sine curve | Comply and state → | Yes / No
Certifications: Any one or more of EN50178, 62040, 60950, 61000-2/3/6, EN60529, 50438 or equivalent | Comply and state → | Yes / No
Battery package
Make and model: | Please state →
Capacity: Min. equivalent to hybrid diesel gen set full load - 24 kW - for 1 hour = 64 kWh. | Comply and state→ | Yes / No
Battery type: LiFePo4 | Comply and state→ | Yes / No
Certifications,: Any one or more of UL1642, IEC62133, 61000-6-3 or equivalent | Comply and state→ | Yes / No
PV panel racks, brackets, cables, fittings etc.
PV panels racks for Ground or flat roof mount. | Comply and state→ | Yes / No
All cables, junctions, contacts, breakers, earthing spears, fittings, screws, nut and bots etc included | Comply and state → | Yes / No
Installation
The system must be plug and play. Inverter, charge controller, battery package, battery charger must be pre-installed and wired either inside one common Hybrid system cage or in a separate cabinet, in order to easily connect the PV array and the local installation. All cables for establishing the PV array must be readily available with pre-installed connections and clearly marked in a way that no mistakes can occur. | Comply and state → | Yes / No
Other
Lifting points for handling | Comply and state → | Yes / No
Installation instructions, drawings, photos, brochures etc. English/French/Spanish | Comply and state → | Yes / No
Operators and maintenance manual, English/French/Spanish | Comply and state → | Yes / No
Tool kit | Comply and state → | Yes / No
Basic maintenance kit, engine: Min. 4 x oil filters, 2 x air filters, 2 x fuel filters | Comply and state → | Yes / No
Dimensions, L x W x H, mm | Please state →
Weight, dry, entire hybrid system incl. Battery package and all PV panels, cables, brackets etc etc.: kg: | Please state →
WARRANTY
Diesel Generator set: 2 years/2500 hours of operation which ever occur first. PV panels: Min. 10 years. Min. 90% performance guarantee at 10 years. Min. 80% performance guarantee at 20 years. Battery package: Min. 5 years. Inverter/charge controller/charger: Min. 4 years. Other equipment: Min. 2 years | Comply and state → | Yes / No
Sustainability
The bidder must demonstrate that its organisation has an environmental management system in place which as a minimum shall submit at least one or more of the following : the environmental policy principles of the organisation; the management measures and procedures taken or that will be taken to assess, monitor, measure and mitigate environmental impacts of the business processes/products associated with the execution of the contract; how attention is paid to the awareness and training/competency of employee(s) and supplier(s) with regard to dealing with the environmental aspects relevant to this bid; and that compliance with the environmental legislation applicable to the required performance(s) is guaranteed, ISO 14001 certificate, EMAS or an equivalent certificate | Comply and state → | Yes / No
The bidder shall provide documentation which outlines their approach to ensuring equal opportunity, diversity and inclusion within their organisation (e.g. equal pay policy, parental leave, ratio of females/males employees, % of female in management positions, grievances disaggregated by gender, transparency of promotion criteria, sexual harassment policies) | Comply and state → | Yes / No
Mandatory Options
Diesel engine spare parts & maintenance kit for min. 2500 hours of operation | Mandatory | enter prices on Form C: Price Schedule
Sound insolating and water proof canopy (max. 70 dB(A) at 7 m) | Mandatory | enter prices on Form C: Price Schedule
Work shop manual | Mandatory | enter prices on Form C: Price Schedule
Spare parts catalogue | Mandatory | enter prices on Form C: Price Schedule
60 Hz version of Generator set, please enter any surcharge to the std 50 Hz version offered above | Mandatory | enter prices on Form C: Price Schedule
Suggested Options
Heavy duty air filter for dusty conditions | Please provide price or state STD→ | Submit other option prices on a separate form
Heavy duty fuel filter/additional fuel filter in line with original | Please provide price or state STD→ | Submit other option prices on a separate form
Additional silencer, state dB(A) at 1 m and/or 7 m | Please provide price or state STD→ | Submit other option prices on a separate form
High chimney for exhaust, state height and materials | Please provide price or state STD→ | Submit other option prices on a separate form
(ATS) Automatic Transfer Switch | Please provide price or state STD→ | Submit other option prices on a separate form
Over speed protection | Please provide price or state STD→ | Submit other option prices on a separate form
Manual transfer switch | Please provide price or state STD→ | Submit other option prices on a separate form
External fuel tank with pipes including min.. 10 meter non-corrosive material and fittings, state volume of tank and material | Please provide price or state STD→ | Submit other option prices on a separate form
Slow moving trolley/trailer | Please provide price or state STD→ | Submit other option prices on a separate form
(AMF) Automatic Mains Failure Power generation set | Please provide price or state STD→ | Submit other option prices on a separate form
Automatic main circuit breaker | Please provide price or state STD→ | Submit other option prices on a separate form
Installation instructions and eventual. drawings, other languages | Please provide price or state STD→ | Submit other option prices on a separate form
Change over switch positions for: 1) Mains 2) Off 3) GENERATOR SET | Please provide price or state STD→ | Submit other option prices on a separate form
Automatic main circuit breaker | Please provide price or state STD→ | Submit other option prices on a separate form
Operators and maintenance manual, other languages | Please provide price or state STD→ | Submit other option prices on a separate form

## Lot 17 80 kVA PV 20% Ground
Bidder name:
Make and model:
Lot 17. 80 kVA PV 20% Ground or flat roof mounted
HYBRID PV SOLAR/DIESEL GENERATOR SET SPECS | UNOPS REQUIREMENTS | Bidder: Compliant/Non-compliant to UNOPS requirements? Please mark YES/NO in this coloumn. Not indicating YES/NO in this column may render your bid non-compliant. | Bidders are required to provide information in this column on the specifications of their bid to demonstrate compliance to set specifications. Not providing specifications under this column may render your bid non-compliant.
Complete Hybrid PV solar/diesel generator set for autonomous operation, including PV solar power array, battery package, inverter and charge controller. Diesel engine, alternator, control panel with monitoring gauges/indicators, starting equipment, fuel tank as well as other accessories. Charger to charge battery package by diesel gen set and PV solar system interface between diesel gen set and PV solar power unit for a smooth operation for the two energy sources in conjunction, automatically without any manual intervention. Factory test certificates must be included and must be in accordance to internationally recognised standards. Suitable for tropical conditions. | Comply and state → | Yes / No
KEY DATA
Make | Please state →
Model | Please state →
Country of origin | Please state →
DIESEL GEN SET
Rated power output, min. 80 kVA | Comply and state → | Yes / No
Power factor: 0.8 | Comply and state → | Yes / No
Rated power output, 64 kW, min. | Comply and state → | Yes / No
Voltage, 220/230/240 and 380/400 V | Comply and state → | Yes / No
Phase: 1 and 3 | Comply and state → | Yes / No
AC frequency, 50/60 Hz | Comply and state → | Yes / No
Speed: rpm 1500 or 3000 or other | Please state →
Prime power according to ISO 8528 or equivalent, i.e. power available at variable load with no limitations on hours of operation and capable of min. 10% overload for min. 1 hour in any 12 hours. | Comply and state → | Yes / No
Prime rating of min. the stated output rating at Normal Temperature and Pressure conditions (NTP). Please state | Comply and state → | Yes / No
Derating information (temperature, altitude and humidity), please state | Please state →
Engine
Make | Please state →
Model | Please state →
Engine power output, kW at rpm: | Please state →
Fuel: Diesel | Comply and state → | Yes / No
Cooling, liquid or air or combined, suitable for tropical conditions | Please state →
Speed governor, state type | Please state →
Exhaust with suitable piping and residential silencer | Comply and state → | Yes / No
Noise level, dB(A) at 1 m (silencer fitted) | Please state →
Fuel consumption at 75% load: L/hour | Please state →
CO2 emissions at 75% load: g/hour | Please state →
Mounted on anti-vibration mounts | Comply and state → | Yes / No
ENVIRONMENTAL
EU Non-road emissions regulations schedule, e.g. EU STAGE II, III A, III B, IV. US Non-road and stationary emissions regulations to Tier 1,2,3,4 or equivalent. Please state. | Comply and state → | Yes / No
Alternator
Make: | Please state →
Model: | Please state →
Brushless type | Comply and state → | Yes / No
Cooling, liquid, air, other | Please state →
Protection class min. IP 23 | Comply and state → | Yes / No
Suitable AC power outlets protected by circuit breaker (state type) | Comply and state → | Yes / No
Insulation to min. IEC 60085 - >155 ° C - (F) or equivalent | Comply and state → | Yes / No
Voltage regulator | Comply and state → | Yes / No
Standard accessories
Fuel tank. Integrated or separate, suitable for continuous operation of min. 8 hours at rated capacity. State capacity, litres. Fuel level gauge. Including all necessary pipework, connections etc. Possibility for connection to external tank. | Comply and state→ | Yes / No
Low oil pressure protection, automatic shut down | Comply and state → | Yes / No
Over heating protection | Comply and state → | Yes / No
Overload protection | Comply and state → | Yes / No
Emergency stop | Comply and state → | Yes / No
Electric starter with key and battery | Comply and state → | Yes / No
Min. Voltmeter, ammeter, hour meter, Hz meter, water temp gauge/indicator (where applicable) | Comply and state → | Yes / No
Earthing/grounding facility | Comply and state → | Yes / No
PV SOLAR POWER SYSTEM STANDARD ARRAY NOMINAL MIN. 12.8 kWp. Battery pack 64 kWh. For Ground or flat roof mount
PV solar array
Make and model: | Please state →
Array kWp, min 20% of diesel generator set max output which is 80kVA/64 kW, hence = 12.8 kWp min. | Comply and state→ | Yes / No
PV panels, total surface covering, m2 | Please state →
Nominal power output each panel, kWp | Please state →
Isc array, A (Amp) | Please state →
Certifications: Any one or more of IEC61215, UL1703 or equivalent | Comply and state → | Yes / No
Charge controller
Make and model: | Please state →
Type: MTTP | Comply and state → | Yes / No
Certifications. Any one or more of EN60730-1/2-11, 55022, 61000-4-27374/5/6 or equivalent | Comply and state→ | Yes / No
Capacity: Isc array +20%, min. | Comply and state→ | Yes / No
Inverter
Make and model: | Please state →
Capacity, A (Amp): Min. equivalent to max load | Comply and state→ | Yes / No
Pure sine curve | Comply and state → | Yes / No
Certifications: Any one or more of EN50178, 62040, 60950, 61000-2/3/6, EN60529, 50438 or equivalent | Comply and state → | Yes / No
Battery package
Make and model: | Please state →
Capacity: Min. equivalent to hybrid diesel gen set full load - 24 kW - for 1 hour = 64 kWh. | Comply and state→ | Yes / No
Battery type: LiFePo4 | Comply and state→ | Yes / No
Certifications,: Any one or more of UL1642, IEC62133, 61000-6-3 or equivalent | Comply and state→ | Yes / No
PV panel racks, brackets, cables, fittings etc.
PV panels racks for Ground or flat roof mount. | Comply and state→ | Yes / No
All cables, junctions, contacts, breakers, earthing spears, fittings, screws, nut and bots etc included | Comply and state → | Yes / No
Installation
The system must be plug and play. Inverter, charge controller, battery package, battery charger must be pre-installed and wired either inside one common Hybrid system cage or in a separate cabinet, in order to easily connect the PV array and the local installation. All cables for establishing the PV array must be readily available with pre-installed connections and clearly marked in a way that no mistakes can occur. | Comply and state → | Yes / No
Other
Lifting points for handling | Comply and state → | Yes / No
Installation instructions, drawings, photos, brochures etc. English/French/Spanish | Comply and state → | Yes / No
Operators and maintenance manual, English/French/Spanish | Comply and state → | Yes / No
Tool kit | Comply and state → | Yes / No
Basic maintenance kit, engine: Min. 4 x oil filters, 2 x air filters, 2 x fuel filters | Comply and state → | Yes / No
Dimensions, L x W x H, mm | Please state →
Weight, dry, entire hybrid system incl. Battery package and all PV panels, cables, brackets etc etc.: kg: | Please state →
WARRANTY
Diesel Generator set: 2 years/2500 hours of operation which ever occur first. PV panels: Min. 10 years. Min. 90% performance guarantee at 10 years. Min. 80% performance guarantee at 20 years. Battery package: Min. 5 years. Inverter/charge controller/charger: Min. 4 years. Other equipment: Min. 2 years | Comply and state → | Yes / No
Sustainability
The bidder must demonstrate that its organisation has an environmental management system in place which as a minimum shall submit at least one or more of the following : the environmental policy principles of the organisation; the management measures and procedures taken or that will be taken to assess, monitor, measure and mitigate environmental impacts of the business processes/products associated with the execution of the contract; how attention is paid to the awareness and training/competency of employee(s) and supplier(s) with regard to dealing with the environmental aspects relevant to this bid; and that compliance with the environmental legislation applicable to the required performance(s) is guaranteed, ISO 14001 certificate, EMAS or an equivalent certificate | Comply and state → | Yes / No
The bidder shall provide documentation which outlines their approach to ensuring equal opportunity, diversity and inclusion within their organisation (e.g. equal pay policy, parental leave, ratio of females/males employees, % of female in management positions, grievances disaggregated by gender, transparency of promotion criteria, sexual harassment policies) | Comply and state → | Yes / No
Mandatory Options
Diesel engine spare parts & maintenance kit for min. 2500 hours of operation | Mandatory | enter prices on Form C: Price Schedule
Sound insolating and water proof canopy (max. 70 dB(A) at 7 m) | Mandatory | enter prices on Form C: Price Schedule
Work shop manual | Mandatory | enter prices on Form C: Price Schedule
Spare parts catalogue | Mandatory | enter prices on Form C: Price Schedule
60 Hz version of Generator set, please enter any surcharge to the std 50 Hz version offered above | Mandatory | enter prices on Form C: Price Schedule
Suggested Options
Heavy duty air filter for dusty conditions | Please provide price or state STD→ | Submit other option prices on a separate form
Heavy duty fuel filter/additional fuel filter in line with original | Please provide price or state STD→ | Submit other option prices on a separate form
Additional silencer, state dB(A) at 1 m and/or 7 m | Please provide price or state STD→ | Submit other option prices on a separate form
High chimney for exhaust, state height and materials | Please provide price or state STD→ | Submit other option prices on a separate form
(ATS) Automatic Transfer Switch | Please provide price or state STD→ | Submit other option prices on a separate form
Over speed protection | Please provide price or state STD→ | Submit other option prices on a separate form
Manual transfer switch | Please provide price or state STD→ | Submit other option prices on a separate form
External fuel tank with pipes including min.. 10 meter non-corrosive material and fittings, state volume of tank and material | Please provide price or state STD→ | Submit other option prices on a separate form
Slow moving trolley/trailer | Please provide price or state STD→ | Submit other option prices on a separate form
(AMF) Automatic Mains Failure Power generation set | Please provide price or state STD→ | Submit other option prices on a separate form
Automatic main circuit breaker | Please provide price or state STD→ | Submit other option prices on a separate form
Installation instructions and eventual. drawings, other languages | Please provide price or state STD→ | Submit other option prices on a separate form
Change over switch positions for: 1) Mains 2) Off 3) GENERATOR SET | Please provide price or state STD→ | Submit other option prices on a separate form
Automatic main circuit breaker | Please provide price or state STD→ | Submit other option prices on a separate form
Operators and maintenance manual, other languages | Please provide price or state STD→ | Submit other option prices on a separate form

## Lot 18 80 kVA PV 40% Ground
Bidder name:
Make and model:
Lot 18. 80 kVA PV 40% Ground or flat roof mounted
HYBRID PV SOLAR/DIESEL GENERATOR SET SPECS | UNOPS REQUIREMENTS | Bidder: Compliant/Non-compliant to UNOPS requirements? Please mark YES/NO in this coloumn. Not indicating YES/NO in this column may render your bid non-compliant. | Bidders are required to provide information in this column on the specifications of their bid to demonstrate compliance to set specifications. Not providing specifications under this column may render your bid non-compliant.
Complete Hybrid PV solar/diesel generator set for autonomous operation, including PV solar power array, battery package, inverter and charge controller. Diesel engine, alternator, control panel with monitoring gauges/indicators, starting equipment, fuel tank as well as other accessories. Charger to charge battery package by diesel gen set and PV solar system interface between diesel gen set and PV solar power unit for a smooth operation for the two energy sources in conjunction, automatically without any manual intervention. Factory test certificates must be included and must be in accordance to internationally recognised standards. Suitable for tropical conditions. | Comply and state → | Yes / No
KEY DATA
Make | Please state →
Model | Please state →
Country of origin | Please state →
DIESEL GEN SET
Rated power output, min. 80 kVA | Comply and state → | Yes / No
Power factor: 0.8 | Comply and state → | Yes / No
Rated power output, 64 kW, min. | Comply and state → | Yes / No
Voltage, 220/230/240 and 380/400 V | Comply and state → | Yes / No
Phase: 1 and 3 | Comply and state → | Yes / No
AC frequency, 50/60 Hz | Comply and state → | Yes / No
Speed: rpm 1500 or 3000 or other | Please state →
Prime power according to ISO 8528 or equivalent, i.e. power available at variable load with no limitations on hours of operation and capable of min. 10% overload for min. 1 hour in any 12 hours. | Comply and state → | Yes / No
Prime rating of min. the stated output rating at Normal Temperature and Pressure conditions (NTP). Please state | Comply and state → | Yes / No
Derating information (temperature, altitude and humidity), please state | Please state →
Engine
Make | Please state →
Model | Please state →
Engine power output, kW at rpm: | Please state →
Fuel: Diesel | Comply and state → | Yes / No
Cooling, liquid or air or combined, suitable for tropical conditions | Please state →
Speed governor, state type | Please state →
Exhaust with suitable piping and residential silencer | Comply and state → | Yes / No
Noise level, dB(A) at 1 m (silencer fitted) | Please state →
Fuel consumption at 75% load: L/hour | Please state →
CO2 emissions at 75% load: g/hour | Please state →
Mounted on anti-vibration mounts | Comply and state → | Yes / No
ENVIRONMENTAL
EU Non-road emissions regulations schedule, e.g. EU STAGE II, III A, III B, IV. US Non-road and stationary emissions regulations to Tier 1,2,3,4 or equivalent. Please state. | Comply and state → | Yes / No
Alternator
Make: | Please state →
Model: | Please state →
Brushless type | Comply and state → | Yes / No
Cooling, liquid, air, other | Please state →
Protection class min. IP 23 | Comply and state → | Yes / No
Suitable AC power outlets protected by circuit breaker (state type) | Comply and state → | Yes / No
Insulation to min. IEC 60085 - >155 ° C - (F) or equivalent | Comply and state → | Yes / No
Voltage regulator | Comply and state → | Yes / No
Standard accessories
Fuel tank. Integrated or separate, suitable for continuous operation of min. 8 hours at rated capacity. State capacity, litres. Fuel level gauge. Including all necessary pipework, connections etc. Possibility for connection to external tank. | Comply and state→ | Yes / No
Low oil pressure protection, automatic shut down | Comply and state → | Yes / No
Over heating protection | Comply and state → | Yes / No
Overload protection | Comply and state → | Yes / No
Emergency stop | Comply and state → | Yes / No
Electric starter with key and battery | Comply and state → | Yes / No
Min. Voltmeter, ammeter, hour meter, Hz meter, water temp gauge/indicator (where applicable) | Comply and state → | Yes / No
Earthing/grounding facility | Comply and state → | Yes / No
PV SOLAR POWER SYSTEM STANDARD ARRAY NOMINAL MIN. 25.6 kWp. Battery pack 64 kWh. For Ground or flat roof mount
PV solar array
Make and model: | Please state →
Array kWp, min 40% of diesel generator set max output which is 80kVA/64 kW, hence = 25.6 kWp min. | Comply and state→ | Yes / No
PV panels, total surface covering, m2 | Please state →
Nominal power output each panel, kWp | Please state →
Isc array, A (Amp) | Please state →
Certifications: Any one or more of IEC61215, UL1703 or equivalent | Comply and state → | Yes / No
Charge controller
Make and model: | Please state →
Type: MTTP | Comply and state → | Yes / No
Certifications. Any one or more of EN60730-1/2-11, 55022, 61000-4-27374/5/6 or equivalent | Comply and state→ | Yes / No
Capacity: Isc array +20%, min. | Comply and state→ | Yes / No
Inverter
Make and model: | Please state →
Capacity, A (Amp): Min. equivalent to max load | Comply and state→ | Yes / No
Pure sine curve | Comply and state → | Yes / No
Certifications, EN50178, 62040, 60950 and 61000-2/3/6 and EN60529, 50438, VDE 0126-1-1 (grid connection) or similar | Comply and state → | Yes / No
Battery package
Make and model: | Please state →
Capacity: Min. equivalent to hybrid diesel gen set full load - 24 kW - for 1 hour = 64 kWh. | Comply and state→ | Yes / No
Battery type: LiFePo4 | Comply and state→ | Yes / No
Certifications,: Any one or more of UL1642, IEC62133, 61000-6-3 or equivalent | Comply and state→ | Yes / No
PV panel racks, brackets, cables, fittings etc.
PV panels racks for Ground or flat roof mount. | Comply and state→ | Yes / No
All cables, junctions, contacts, breakers, earthing spears, fittings, screws, nut and bots etc included | Comply and state → | Yes / No
Installation
The system must be plug and play. Inverter, charge controller, battery package, battery charger must be pre-installed and wired either inside one common Hybrid system cage or in a separate cabinet, in order to easily connect the PV array and the local installation. All cables for establishing the PV array must be readily available with pre-installed connections and clearly marked in a way that no mistakes can occur. | Comply and state → | Yes / No
Other
Lifting points for handling | Comply and state → | Yes / No
Installation instructions, drawings, photos, brochures etc. English/French/Spanish | Comply and state → | Yes / No
Operators and maintenance manual, English/French/Spanish | Comply and state → | Yes / No
Tool kit | Comply and state → | Yes / No
Basic maintenance kit, engine: Min. 4 x oil filters, 2 x air filters, 2 x fuel filters | Comply and state → | Yes / No
Dimensions, L x W x H, mm | Please state →
Weight, dry, entire hybrid system incl. Battery package and all PV panels, cables, brackets etc etc.: kg: | Please state →
WARRANTY
Diesel Generator set: 2 years/2500 hours of operation which ever occur first. PV panels: Min. 10 years. Min. 90% performance guarantee at 10 years. Min. 80% performance guarantee at 20 years. Battery package: Min. 5 years. Inverter/charge controller/charger: Min. 4 years. Other equipment: Min. 2 years | Comply and state → | Yes / No
Sustainability
The bidder must demonstrate that its organisation has an environmental management system in place which as a minimum shall submit at least one or more of the following : the environmental policy principles of the organisation; the management measures and procedures taken or that will be taken to assess, monitor, measure and mitigate environmental impacts of the business processes/products associated with the execution of the contract; how attention is paid to the awareness and training/competency of employee(s) and supplier(s) with regard to dealing with the environmental aspects relevant to this bid; and that compliance with the environmental legislation applicable to the required performance(s) is guaranteed, ISO 14001 certificate, EMAS or an equivalent certificate | Comply and state → | Yes / No
The bidder shall provide documentation which outlines their approach to ensuring equal opportunity, diversity and inclusion within their organisation (e.g. equal pay policy, parental leave, ratio of females/males employees, % of female in management positions, grievances disaggregated by gender, transparency of promotion criteria, sexual harassment policies) | Comply and state → | Yes / No
Mandatory Options
Diesel engine spare parts & maintenance kit for min. 2500 hours of operation | Mandatory | enter prices on Form C: Price Schedule
Sound insolating and water proof canopy (max. 70 dB(A) at 7 m) | Mandatory | enter prices on Form C: Price Schedule
Work shop manual | Mandatory | enter prices on Form C: Price Schedule
Spare parts catalogue | Mandatory | enter prices on Form C: Price Schedule
60 Hz version of Generator set, please enter any surcharge to the std 50 Hz version offered above | Mandatory | enter prices on Form C: Price Schedule
Suggested Options
Heavy duty air filter for dusty conditions | Please provide price or state STD→ | Submit other option prices on a separate form
Heavy duty fuel filter/additional fuel filter in line with original | Please provide price or state STD→ | Submit other option prices on a separate form
Additional silencer, state dB(A) at 1 m and/or 7 m | Please provide price or state STD→ | Submit other option prices on a separate form
High chimney for exhaust, state height and materials | Please provide price or state STD→ | Submit other option prices on a separate form
(ATS) Automatic Transfer Switch | Please provide price or state STD→ | Submit other option prices on a separate form
Over speed protection | Please provide price or state STD→ | Submit other option prices on a separate form
Manual transfer switch | Please provide price or state STD→ | Submit other option prices on a separate form
External fuel tank with pipes including min.. 10 meter non-corrosive material and fittings, state volume of tank and material | Please provide price or state STD→ | Submit other option prices on a separate form
Slow moving trolley/trailer | Please provide price or state STD→ | Submit other option prices on a separate form
(AMF) Automatic Mains Failure Power generation set | Please provide price or state STD→ | Submit other option prices on a separate form
Automatic main circuit breaker | Please provide price or state STD→ | Submit other option prices on a separate form
Installation instructions and eventual. drawings, other languages | Please provide price or state STD→ | Submit other option prices on a separate form
Change over switch positions for: 1) Mains 2) Off 3) GENERATOR SET | Please provide price or state STD→ | Submit other option prices on a separate form
Automatic main circuit breaker | Please provide price or state STD→ | Submit other option prices on a separate form
Operators and maintenance manual, other languages | Please provide price or state STD→ | Submit other option prices on a separate form

## Lot 19 100 kVA PV 10% Roof
Bidder name:
Make and model:
Lot 19 100 kVA PV 10% Sloped Roof or Gen set mount.
HYBRID PV SOLAR/DIESEL GENERATOR SET SPECS | UNOPS REQUIREMENTS | Bidder: Compliant/Non-compliant to UNOPS requirements? Please mark YES/NO in this coloumn. Not indicating YES/NO in this column may render your bid non-compliant. | Bidders are required to provide information in this column on the specifications of their bid to demonstrate compliance to set specifications. Not providing specifications under this column may render your bid non-compliant.
Complete Hybrid PV solar/diesel generator set for autonomous operation, including PV solar power array, battery package, inverter and charge controller. Diesel engine, alternator, control panel with monitoring gauges/indicators, starting equipment, fuel tank as well as other accessories. Charger to charge battery package by diesel gen set and PV solar system interface between diesel gen set and PV solar power unit for a smooth operation for the two energy sources in conjunction, automatically without any manual intervention. Factory test certificates must be included and must be in accordance to internationally recognised standards. Suitable for tropical conditions. | Comply and state → | Yes / No | `
KEY DATA
Make | Please state →
Model | Please state →
Country of origin | Please state →
DIESEL GEN SET
Rated power output, min. 100 kVA | Comply and state → | Yes / No
Power factor: 0.8 | Comply and state → | Yes / No
Rated power output, 80 kW, min. | Comply and state → | Yes / No
Voltage, 220/230/240 and 380/400 V | Comply and state → | Yes / No
Phase: 1 and 3 | Comply and state → | Yes / No
AC frequency, 50/60 Hz | Comply and state → | Yes / No
Speed: rpm 1500 or 3000 or other | Please state →
Prime power according to ISO 8528 or equivalent, i.e. power available at variable load with no limitations on hours of operation and capable of min. 10% overload for min. 1 hour in any 12 hours. | Comply and state → | Yes / No
Prime rating of min. the stated output rating at Normal Temperature and Pressure conditions (NTP). Please state | Comply and state → | Yes / No
Derating information (temperature, altitude and humidity), please state | Please state →
Engine
Make | Please state →
Model | Please state →
Engine power output, kW at rpm: | Please state →
Fuel: Diesel | Comply and state → | Yes / No
Cooling, liquid or air or combined, suitable for tropical conditions | Please state →
Speed governor, state type | Please state →
Exhaust with suitable piping and residential silencer | Comply and state → | Yes / No
Noise level, dB(A) at 1 m (silencer fitted) | Please state →
Fuel consumption at 75% load: L/hour | Please state →
CO2 emissions at 75% load: g/hour | Please state →
Mounted on anti-vibration mounts | Comply and state → | Yes / No
ENVIRONMENTAL
EU Non-road emissions regulations schedule, e.g. EU STAGE II, III A, III B, IV. US Non-road and stationary emissions regulations to Tier 1,2,3,4 or equivalent. Please state. | Comply and state → | Yes / No
Alternator
Make: | Please state →
Model: | Please state →
Brushless type | Comply and state → | Yes / No
Cooling, liquid, air, other | Please state →
Protection class min. IP 23 | Comply and state → | Yes / No
Suitable AC power outlets protected by circuit breaker (state type) | Comply and state → | Yes / No
Insulation to min. IEC 60085 - >155 ° C - (F) or equivalent | Comply and state → | Yes / No
Voltage regulator | Comply and state → | Yes / No
Standard accessories
Fuel tank. Integrated or separate, suitable for continuous operation of min. 8 hours at rated capacity. State capacity, litres. Fuel level gauge. Including all necessary pipework, connections etc. Possibility for connection to external tank. | Comply and state→ | Yes / No
Low oil pressure protection, automatic shut down | Comply and state → | Yes / No
Over heating protection | Comply and state → | Yes / No
Overload protection | Comply and state → | Yes / No
Emergency stop | Comply and state → | Yes / No
Electric starter with key and battery | Comply and state → | Yes / No
Min. Voltmeter, ammeter, hour meter, Hz meter, water temp gauge/indicator (where applicable) | Comply and state → | Yes / No
Earthing/grounding facility | Comply and state → | Yes / No
PV SOLAR POWER SYSTEM STANDARD ARRAY NOMINAL MIN. 8.0 kWp. Battery pack 80 kWh. For Sloped Roof or Gen set mount.
PV solar array
Make and model: | Please state →
Array kWp, min 10% of diesel generator set max output which is 100 kVA/80 kW, hence = 8.0 kWp min. | Comply and state→ | Yes / No
PV panels, total surface covering, m2 | Please state →
Nominal power output each panel, kWp | Please state →
Isc array, A (Amp) | Please state →
Certifications: Any one or more of IEC61215, UL1703 or equivalent | Comply and state → | Yes / No
Charge controller
Make and model: | Please state →
Type: MTTP | Comply and state → | Yes / No
Certifications. Any one or more of EN60730-1/2-11, 55022, 61000-4-27374/5/6 or equivalent | Comply and state→ | Yes / No
Capacity: Isc array +20%, min. | Comply and state→ | Yes / No
Inverter
Make and model: | Please state →
Capacity, A (Amp): Min. equivalent to max load | Comply and state→ | Yes / No
Pure sine curve | Comply and state → | Yes / No
Certifications: Any one or more of EN50178, 62040, 60950, 61000-2/3/6, EN60529, 50438 or equivalent | Comply and state → | Yes / No
Battery package
Make and model: | Please state →
Capacity: Min. equivalent to hybrid diesel gen set full load - 24 kW - for 1 hour = 80 kWh. | Comply and state→ | Yes / No
Battery type: LiFePo4 | Comply and state→ | Yes / No
Certifications,: Any one or more of UL1642, IEC62133, 61000-6-3 or equivalent | Comply and state→ | Yes / No
PV panel racks, brackets, cables, fittings etc.
PV panels racks for sloped roof mount included for all included PV panels, if not attached to the Hybrid Gen set system itself (permanently or fold-out system etc). | Comply and state→ | Yes / No
All cables, junctions, contacts, breakers, earthing spears, fittings, screws, nut and bots etc included | Comply and state → | Yes / No
Installation
The system must be plug and play. Inverter, charge controller, battery package, battery charger must be pre-installed and wired either inside one common Hybrid system cage or in a separate cabinet, in order to easily connect the PV array and the local installation. All cables for establishing the PV array must be readily available with pre-installed connections and clearly marked in a way that no mistakes can occur. | Comply and state → | Yes / No
Other
Lifting points for handling | Comply and state → | Yes / No
Installation instructions, drawings, photos, brochures etc. English/French/Spanish | Comply and state → | Yes / No
Operators and maintenance manual, English/French/Spanish | Comply and state → | Yes / No
Tool kit | Comply and state → | Yes / No
Basic maintenance kit, engine: Min. 4 x oil filters, 2 x air filters, 2 x fuel filters | Comply and state → | Yes / No
Dimensions, L x W x H, mm | Please state →
Weight, dry, entire hybrid system incl. Battery package and all PV panels, cables, brackets etc etc.: kg: | Please state →
WARRANTY
Diesel Generator set: 2 years/2500 hours of operation which ever occur first. PV panels: Min. 10 years. Min. 90% performance guarantee at 10 years. Min. 80% performance guarantee at 20 years. Battery package: Min. 5 years. Inverter/charge controller/charger: Min. 4 years. Other equipment: Min. 2 years | Comply and state → | Yes / No
Sustainability
The bidder must demonstrate that its organisation has an environmental management system in place which as a minimum shall submit at least one or more of the following : the environmental policy principles of the organisation; the management measures and procedures taken or that will be taken to assess, monitor, measure and mitigate environmental impacts of the business processes/products associated with the execution of the contract; how attention is paid to the awareness and training/competency of employee(s) and supplier(s) with regard to dealing with the environmental aspects relevant to this bid; and that compliance with the environmental legislation applicable to the required performance(s) is guaranteed, ISO 14001 certificate, EMAS or an equivalent certificate | Comply and state → | Yes / No
The bidder shall provide documentation which outlines their approach to ensuring equal opportunity, diversity and inclusion within their organisation (e.g. equal pay policy, parental leave, ratio of females/males employees, % of female in management positions, grievances disaggregated by gender, transparency of promotion criteria, sexual harassment policies) | Comply and state → | Yes / No
Mandatory Options
Diesel engine spare parts & maintenance kit for min. 2500 hours of operation | Mandatory | enter prices on Form C: Price Schedule
Sound insolating and water proof canopy (max. 70 dB(A) at 7 m) | Mandatory | enter prices on Form C: Price Schedule
Work shop manual | Mandatory | enter prices on Form C: Price Schedule
Spare parts catalogue | Mandatory | enter prices on Form C: Price Schedule
60 Hz version of Generator set, please enter any surcharge to the std 50 Hz version offered above | Mandatory | enter prices on Form C: Price Schedule
Suggested Options
Heavy duty air filter for dusty conditions | Please provide price or state STD→ | Submit other option prices on a separate form
Heavy duty fuel filter/additional fuel filter in line with original | Please provide price or state STD→ | Submit other option prices on a separate form
Additional silencer, state dB(A) at 1 m and/or 7 m | Please provide price or state STD→ | Submit other option prices on a separate form
High chimney for exhaust, state height and materials | Please provide price or state STD→ | Submit other option prices on a separate form
(ATS) Automatic Transfer Switch | Please provide price or state STD→ | Submit other option prices on a separate form
Over speed protection | Please provide price or state STD→ | Submit other option prices on a separate form
Manual transfer switch | Please provide price or state STD→ | Submit other option prices on a separate form
External fuel tank with pipes including min.. 10 meter non-corrosive material and fittings, state volume of tank and material | Please provide price or state STD→ | Submit other option prices on a separate form
Slow moving trolley/trailer | Please provide price or state STD→ | Submit other option prices on a separate form
(AMF) Automatic Mains Failure Power generation set | Please provide price or state STD→ | Submit other option prices on a separate form
Automatic main circuit breaker | Please provide price or state STD→ | Submit other option prices on a separate form
Installation instructions and eventual. drawings, other languages | Please provide price or state STD→ | Submit other option prices on a separate form
Change over switch positions for: 1) Mains 2) Off 3) GENERATOR SET | Please provide price or state STD→ | Submit other option prices on a separate form
Automatic main circuit breaker | Please provide price or state STD→ | Submit other option prices on a separate form
Operators and maintenance manual, other languages | Please provide price or state STD→ | Submit other option prices on a separate form

## Lot 20 100 kVA PV 20% Roof
Bidder name:
Make and model:
Lot 20 100 kVA PV 20% Sloped Roof or Gen set mount.
HYBRID PV SOLAR/DIESEL GENERATOR SET SPECS | UNOPS REQUIREMENTS | Bidder: Compliant/Non-compliant to UNOPS requirements? Please mark YES/NO in this coloumn. Not indicating YES/NO in this column may render your bid non-compliant. | Bidders are required to provide information in this column on the specifications of their bid to demonstrate compliance to set specifications. Not providing specifications under this column may render your bid non-compliant.
Complete Hybrid PV solar/diesel generator set for autonomous operation, including PV solar power array, battery package, inverter and charge controller. Diesel engine, alternator, control panel with monitoring gauges/indicators, starting equipment, fuel tank as well as other accessories. Charger to charge battery package by diesel gen set and PV solar system interface between diesel gen set and PV solar power unit for a smooth operation for the two energy sources in conjunction, automatically without any manual intervention. Factory test certificates must be included and must be in accordance to internationally recognised standards. Suitable for tropical conditions. | Comply and state → | Yes / No
KEY DATA
Make | Please state →
Model | Please state →
Country of origin | Please state →
DIESEL GEN SET
Rated power output, min. 100 kVA | Comply and state → | Yes / No
Power factor: 0.8 | Comply and state → | Yes / No
Rated power output, 80 kW, min. | Comply and state → | Yes / No
Voltage, 220/230/240 and 380/400 V | Comply and state → | Yes / No
Phase: 1 and 3 | Comply and state → | Yes / No
AC frequency, 50/60 Hz | Comply and state → | Yes / No
Speed: rpm 1500 or 3000 or other | Please state →
Prime power according to ISO 8528 or equivalent, i.e. power available at variable load with no limitations on hours of operation and capable of min. 10% overload for min. 1 hour in any 12 hours. | Comply and state → | Yes / No
Prime rating of min. the stated output rating at Normal Temperature and Pressure conditions (NTP). Please state | Comply and state → | Yes / No
Derating information (temperature, altitude and humidity), please state | Please state →
Engine
Make | Please state →
Model | Please state →
Engine power output, kW at rpm: | Please state →
Fuel: Diesel | Comply and state → | Yes / No
Cooling, liquid or air or combined, suitable for tropical conditions | Please state →
Speed governor, state type | Please state →
Exhaust with suitable piping and residential silencer | Comply and state → | Yes / No
Noise level, dB(A) at 1 m (silencer fitted) | Please state →
Fuel consumption at 75% load: L/hour | Please state →
CO2 emissions at 75% load: g/hour | Please state →
Mounted on anti-vibration mounts | Comply and state → | Yes / No
ENVIRONMENTAL
EU Non-road emissions regulations schedule, e.g. EU STAGE II, III A, III B, IV. US Non-road and stationary emissions regulations to Tier 1,2,3,4 or equivalent. Please state. | Comply and state → | Yes / No
Alternator
Make: | Please state →
Model: | Please state →
Brushless type | Comply and state → | Yes / No
Cooling, liquid, air, other | Please state →
Protection class min. IP 23 | Comply and state → | Yes / No
Suitable AC power outlets protected by circuit breaker (state type) | Comply and state → | Yes / No
Insulation to min. IEC 60085 - >155 ° C - (F) or equivalent | Comply and state → | Yes / No
Voltage regulator | Comply and state → | Yes / No
Standard accessories
Fuel tank. Integrated or separate, suitable for continuous operation of min. 8 hours at rated capacity. State capacity, litres. Fuel level gauge. Including all necessary pipework, connections etc. Possibility for connection to external tank. | Comply and state→ | Yes / No
Low oil pressure protection, automatic shut down | Comply and state → | Yes / No
Over heating protection | Comply and state → | Yes / No
Overload protection | Comply and state → | Yes / No
Emergency stop | Comply and state → | Yes / No
Electric starter with key and battery | Comply and state → | Yes / No
Min. Voltmeter, ammeter, hour meter, Hz meter, water temp gauge/indicator (where applicable) | Comply and state → | Yes / No
Earthing/grounding facility | Comply and state → | Yes / No
PV SOLAR POWER SYSTEM STANDARD ARRAY NOMINAL MIN. 16.0 kWp. Battery pack 80 kWh. For Sloped Roof or Gen set mount.
PV solar array
Make and model: | Please state →
Array kWp, min 20% of diesel generator set max output which is 100 kVA/80 kW, hence = 16.0 kWp min. | Comply and state→ | Yes / No
PV panels, total surface covering, m2 | Please state →
Nominal power output each panel, kWp | Please state →
Isc array, A (Amp) | Please state →
Certifications: Any one or more of IEC61215, UL1703 or equivalent | Comply and state → | Yes / No
Charge controller
Make and model: | Please state →
Type: MTTP | Comply and state → | Yes / No
Certifications. Any one or more of EN60730-1/2-11, 55022, 61000-4-27374/5/6 or equivalent | Comply and state→ | Yes / No
Capacity: Isc array +20%, min. | Comply and state→ | Yes / No
Inverter
Make and model: | Please state →
Capacity, A (Amp): Min. equivalent to max load | Comply and state→ | Yes / No
Pure sine curve | Comply and state → | Yes / No
Certifications: Any one or more of EN50178, 62040, 60950, 61000-2/3/6, EN60529, 50438 or equivalent | Comply and state → | Yes / No
Battery package
Make and model: | Please state →
Capacity: Min. equivalent to hybrid diesel gen set full load - 24 kW - for 1 hour = 80 kWh. | Comply and state→ | Yes / No
Battery type: LiFePo4 | Comply and state→ | Yes / No
Certifications,: Any one or more of UL1642, IEC62133, 61000-6-3 or equivalent | Comply and state→ | Yes / No
PV panel racks, brackets, cables, fittings etc. | Comply and state→
PV panels racks for sloped roof mount included for all included PV panels, if not attached to the Hybrid Gen set system itself (permanently or fold-out system etc). | Comply and state→ | Yes / No
All cables, junctions, contacts, breakers, earthing spears, fittings, screws, nut and bots etc included | Comply and state → | Yes / No
Installation
The system must be plug and play. Inverter, charge controller, battery package, battery charger must be pre-installed and wired either inside one common Hybrid system cage or in a separate cabinet, in order to easily connect the PV array and the local installation. All cables for establishing the PV array must be readily available with pre-installed connections and clearly marked in a way that no mistakes can occur. | Comply and state → | Yes / No
Other
Lifting points for handling | Comply and state → | Yes / No
Installation instructions, drawings, photos, brochures etc. English/French/Spanish | Comply and state → | Yes / No
Operators and maintenance manual, English/French/Spanish | Comply and state → | Yes / No
Tool kit | Comply and state → | Yes / No
Basic maintenance kit, engine: Min. 4 x oil filters, 2 x air filters, 2 x fuel filters | Comply and state → | Yes / No
Dimensions, L x W x H, mm | Please state →
Weight, dry, entire hybrid system incl. Battery package and all PV panels, cables, brackets etc etc.: kg: | Please state →
WARRANTY
Diesel Generator set: 2 years/2500 hours of operation which ever occur first. PV panels: Min. 10 years. Min. 90% performance guarantee at 10 years. Min. 80% performance guarantee at 20 years. Battery package: Min. 5 years. Inverter/charge controller/charger: Min. 4 years. Other equipment: Min. 2 years | Comply and state → | Yes / No
Sustainability
The bidder must demonstrate that its organisation has an environmental management system in place which as a minimum shall submit at least one or more of the following : the environmental policy principles of the organisation; the management measures and procedures taken or that will be taken to assess, monitor, measure and mitigate environmental impacts of the business processes/products associated with the execution of the contract; how attention is paid to the awareness and training/competency of employee(s) and supplier(s) with regard to dealing with the environmental aspects relevant to this bid; and that compliance with the environmental legislation applicable to the required performance(s) is guaranteed, ISO 14001 certificate, EMAS or an equivalent certificate | Comply and state → | Yes / No
The bidder shall provide documentation which outlines their approach to ensuring equal opportunity, diversity and inclusion within their organisation (e.g. equal pay policy, parental leave, ratio of females/males employees, % of female in management positions, grievances disaggregated by gender, transparency of promotion criteria, sexual harassment policies) | Comply and state → | Yes / No
Mandatory Options
Diesel engine spare parts & maintenance kit for min. 2500 hours of operation | Mandatory | enter prices on Form C: Price Schedule
Sound insolating and water proof canopy (max. 70 dB(A) at 7 m) | Mandatory | enter prices on Form C: Price Schedule
Work shop manual | Mandatory | enter prices on Form C: Price Schedule
Spare parts catalogue | Mandatory | enter prices on Form C: Price Schedule
60 Hz version of Generator set, please enter any surcharge to the std 50 Hz version offered above | Mandatory | enter prices on Form C: Price Schedule
Suggested Options
Heavy duty air filter for dusty conditions | Please provide price or state STD→ | Submit other option prices on a separate form
Heavy duty fuel filter/additional fuel filter in line with original | Please provide price or state STD→ | Submit other option prices on a separate form
Additional silencer, state dB(A) at 1 m and/or 7 m | Please provide price or state STD→ | Submit other option prices on a separate form
High chimney for exhaust, state height and materials | Please provide price or state STD→ | Submit other option prices on a separate form
(ATS) Automatic Transfer Switch | Please provide price or state STD→ | Submit other option prices on a separate form
Over speed protection | Please provide price or state STD→ | Submit other option prices on a separate form
Manual transfer switch | Please provide price or state STD→ | Submit other option prices on a separate form
External fuel tank with pipes including min.. 10 meter non-corrosive material and fittings, state volume of tank and material | Please provide price or state STD→ | Submit other option prices on a separate form
Slow moving trolley/trailer | Please provide price or state STD→ | Submit other option prices on a separate form
(AMF) Automatic Mains Failure Power generation set | Please provide price or state STD→ | Submit other option prices on a separate form
Automatic main circuit breaker | Please provide price or state STD→ | Submit other option prices on a separate form
Installation instructions and eventual. drawings, other languages | Please provide price or state STD→ | Submit other option prices on a separate form
Change over switch positions for: 1) Mains 2) Off 3) GENERATOR SET | Please provide price or state STD→ | Submit other option prices on a separate form
Automatic main circuit breaker | Please provide price or state STD→ | Submit other option prices on a separate form
Operators and maintenance manual, other languages | Please provide price or state STD→ | Submit other option prices on a separate form

## Lot 21 100 kVA PV 40% Roof
Bidder name:
Make and model:
Lot 21 100 kVA PV 40% Sloped Roof or Gen set mount.
HYBRID PV SOLAR/DIESEL GENERATOR SET SPECS | UNOPS REQUIREMENTS | Bidder: Compliant/Non-compliant to UNOPS requirements? Please mark YES/NO in this coloumn. Not indicating YES/NO in this column may render your bid non-compliant. | Bidders are required to provide information in this column on the specifications of their bid to demonstrate compliance to set specifications. Not providing specifications under this column may render your bid non-compliant.
Complete Hybrid PV solar/diesel generator set for autonomous operation, including PV solar power array, battery package, inverter and charge controller. Diesel engine, alternator, control panel with monitoring gauges/indicators, starting equipment, fuel tank as well as other accessories. Charger to charge battery package by diesel gen set and PV solar system interface between diesel gen set and PV solar power unit for a smooth operation for the two energy sources in conjunction, automatically without any manual intervention. Factory test certificates must be included and must be in accordance to internationally recognised standards. Suitable for tropical conditions. | Comply and state → | Yes / No
KEY DATA
Make | Please state →
Model | Please state →
Country of origin | Please state →
DIESEL GEN SET
Rated power output, min. 100 kVA | Comply and state → | Yes / No
Power factor: 0.8 | Comply and state → | Yes / No
Rated power output, 80 kW, min. | Comply and state → | Yes / No
Voltage, 220/230/240 and 380/400 V | Comply and state → | Yes / No
Phase: 1 and 3 | Comply and state → | Yes / No
AC frequency, 50/60 Hz | Comply and state → | Yes / No
Speed: rpm 1500 or 3000 or other | Please state →
Prime power according to ISO 8528 or equivalent, i.e. power available at variable load with no limitations on hours of operation and capable of min. 10% overload for min. 1 hour in any 12 hours. | Comply and state → | Yes / No
Prime rating of min. the stated output rating at Normal Temperature and Pressure conditions (NTP). Please state | Comply and state → | Yes / No
Derating information (temperature, altitude and humidity), please state | Please state →
Engine
Make | Please state →
Model | Please state →
Engine power output, kW at rpm: | Please state →
Fuel: Diesel | Comply and state → | Yes / No
Cooling, liquid or air or combined, suitable for tropical conditions | Please state →
Speed governor, state type | Please state →
Exhaust with suitable piping and residential silencer | Comply and state → | Yes / No
Noise level, dB(A) at 1 m (silencer fitted) | Please state →
Fuel consumption at 75% load: L/hour | Please state →
CO2 emissions at 75% load: g/hour | Please state →
Mounted on anti-vibration mounts | Comply and state → | Yes / No
ENVIRONMENTAL
EU Non-road emissions regulations schedule, e.g. EU STAGE II, III A, III B, IV. US Non-road and stationary emissions regulations to Tier 1,2,3,4 or equivalent. Please state. | Comply and state → | Yes / No
Alternator
Make: | Please state →
Model: | Please state →
Brushless type | Comply and state → | Yes / No
Cooling, liquid, air, other | Please state →
Protection class min. IP 23 | Comply and state → | Yes / No
Suitable AC power outlets protected by circuit breaker (state type) | Comply and state → | Yes / No
Insulation to min. IEC 60085 - >155 ° C - (F) or equivalent | Comply and state → | Yes / No
Voltage regulator | Comply and state → | Yes / No
Standard accessories
Fuel tank. Integrated or separate, suitable for continuous operation of min. 8 hours at rated capacity. State capacity, litres. Fuel level gauge. Including all necessary pipework, connections etc. Possibility for connection to external tank. | Comply and state→ | Yes / No
Low oil pressure protection, automatic shut down | Comply and state → | Yes / No
Over heating protection | Comply and state → | Yes / No
Overload protection | Comply and state → | Yes / No
Emergency stop | Comply and state → | Yes / No
Electric starter with key and battery | Comply and state → | Yes / No
Min. Voltmeter, ammeter, hour meter, Hz meter, water temp gauge/indicator (where applicable) | Comply and state → | Yes / No
Earthing/grounding facility | Comply and state → | Yes / No
PV SOLAR POWER SYSTEM STANDARD ARRAY NOMINAL MIN. 32.0 kWp. Battery pack 80 kWh. For Sloped Roof or Gen set mount.
PV solar array
Make and model: | Please state →
Array kWp, min 40% of diesel generator set max output which is 100 kVA/80 kW, hence = 32.0 kWp min. | Comply and state→ | Yes / No
PV panels, total surface covering, m2 | Please state →
Nominal power output each panel, kWp | Please state →
Isc array, A (Amp) | Please state →
Certifications: Any one or more of IEC61215, UL1703 or equivalent | Comply and state → | Yes / No
Charge controller
Make and model: | Please state →
Type: MTTP | Comply and state → | Yes / No
Certifications. Any one or more of EN60730-1/2-11, 55022, 61000-4-27374/5/6 or equivalent | Comply and state→ | Yes / No
Capacity: Isc array +20%, min. | Comply and state→ | Yes / No
Inverter
Make and model: | Please state →
Capacity, A (Amp): Min. equivalent to max load | Comply and state→ | Yes / No
Pure sine curve | Comply and state → | Yes / No
Certifications: Any one or more of EN50178, 62040, 60950, 61000-2/3/6, EN60529, 50438 or equivalent | Comply and state → | Yes / No
Battery package
Make and model: | Please state →
Capacity: Min. equivalent to hybrid diesel gen set full load - 24 kW - for 1 hour = 80 kWh. | Comply and state→ | Yes / No
Battery type: LiFePo4 | Comply and state→ | Yes / No
Certifications,: Any one or more of UL1642, IEC62133, 61000-6-3 or equivalent | Comply and state→ | Yes / No
PV panel racks, brackets, cables, fittings etc. | Comply and state→
PV panels racks for sloped roof mount included for all included PV panels, if not attached to the Hybrid Gen set system itself (permanently or fold-out system etc). | Comply and state→ | Yes / No
All cables, junctions, contacts, breakers, earthing spears, fittings, screws, nut and bots etc included | Comply and state → | Yes / No
Installation
The system must be plug and play. Inverter, charge controller, battery package, battery charger must be pre-installed and wired either inside one common Hybrid system cage or in a separate cabinet, in order to easily connect the PV array and the local installation. All cables for establishing the PV array must be readily available with pre-installed connections and clearly marked in a way that no mistakes can occur. | Comply and state → | Yes / No
Other
Lifting points for handling | Comply and state → | Yes / No
Installation instructions, drawings, photos, brochures etc. English/French/Spanish | Comply and state → | Yes / No
Operators and maintenance manual, English/French/Spanish | Comply and state → | Yes / No
Tool kit | Comply and state → | Yes / No
Basic maintenance kit, engine: Min. 4 x oil filters, 2 x air filters, 2 x fuel filters | Comply and state → | Yes / No
Dimensions, L x W x H, mm | Please state →
Weight, dry, entire hybrid system incl. Battery package and all PV panels, cables, brackets etc etc.: kg: | Please state →
WARRANTY
Diesel Generator set: 2 years/2500 hours of operation which ever occur first. PV panels: Min. 10 years. Min. 90% performance guarantee at 10 years. Min. 80% performance guarantee at 20 years. Battery package: Min. 5 years. Inverter/charge controller/charger: Min. 4 years. Other equipment: Min. 2 years | Comply and state → | Yes / No
Sustainability
The bidder must demonstrate that its organisation has an environmental management system in place which as a minimum shall submit at least one or more of the following : the environmental policy principles of the organisation; the management measures and procedures taken or that will be taken to assess, monitor, measure and mitigate environmental impacts of the business processes/products associated with the execution of the contract; how attention is paid to the awareness and training/competency of employee(s) and supplier(s) with regard to dealing with the environmental aspects relevant to this bid; and that compliance with the environmental legislation applicable to the required performance(s) is guaranteed, ISO 14001 certificate, EMAS or an equivalent certificate | Comply and state → | Yes / No
The bidder shall provide documentation which outlines their approach to ensuring equal opportunity, diversity and inclusion within their organisation (e.g. equal pay policy, parental leave, ratio of females/males employees, % of female in management positions, grievances disaggregated by gender, transparency of promotion criteria, sexual harassment policies) | Comply and state → | Yes / No
Mandatory Options
Diesel engine spare parts & maintenance kit for min. 2500 hours of operation | Mandatory | enter prices on Form C: Price Schedule
Sound insolating and water proof canopy (max. 70 dB(A) at 7 m) | Mandatory | enter prices on Form C: Price Schedule
Work shop manual | Mandatory | enter prices on Form C: Price Schedule
Spare parts catalogue | Mandatory | enter prices on Form C: Price Schedule
60 Hz version of Generator set, please enter any surcharge to the std 50 Hz version offered above | Mandatory | enter prices on Form C: Price Schedule
Suggested Options
Heavy duty air filter for dusty conditions | Please provide price or state STD→ | Submit other option prices on a separate form
Heavy duty fuel filter/additional fuel filter in line with original | Please provide price or state STD→ | Submit other option prices on a separate form
Additional silencer, state dB(A) at 1 m and/or 7 m | Please provide price or state STD→ | Submit other option prices on a separate form
High chimney for exhaust, state height and materials | Please provide price or state STD→ | Submit other option prices on a separate form
(ATS) Automatic Transfer Switch | Please provide price or state STD→ | Submit other option prices on a separate form
Over speed protection | Please provide price or state STD→ | Submit other option prices on a separate form
Manual transfer switch | Please provide price or state STD→ | Submit other option prices on a separate form
External fuel tank with pipes including min.. 10 meter non-corrosive material and fittings, state volume of tank and material | Please provide price or state STD→ | Submit other option prices on a separate form
Slow moving trolley/trailer | Please provide price or state STD→ | Submit other option prices on a separate form
(AMF) Automatic Mains Failure Power generation set | Please provide price or state STD→ | Submit other option prices on a separate form
Automatic main circuit breaker | Please provide price or state STD→ | Submit other option prices on a separate form
Installation instructions and eventual. drawings, other languages | Please provide price or state STD→ | Submit other option prices on a separate form
Change over switch positions for: 1) Mains 2) Off 3) GENERATOR SET | Please provide price or state STD→ | Submit other option prices on a separate form
Automatic main circuit breaker | Please provide price or state STD→ | Submit other option prices on a separate form
Operators and maintenance manual, other languages | Please provide price or state STD→ | Submit other option prices on a separate form

## Lot 22 100 kVA PV 10% Ground
Bidder name:
Make and model:
Lot 22. 100 kVA PV 10% Ground or flat roof mounted
HYBRID PV SOLAR/DIESEL GENERATOR SET SPECS | UNOPS REQUIREMENTS | Bidder: Compliant/Non-compliant to UNOPS requirements? Please mark YES/NO in this coloumn. Not indicating YES/NO in this column may render your bid non-compliant. | Bidders are required to provide information in this column on the specifications of their bid to demonstrate compliance to set specifications. Not providing specifications under this column may render your bid non-compliant.
Complete Hybrid PV solar/diesel generator set for autonomous operation, including PV solar power array, battery package, inverter and charge controller. Diesel engine, alternator, control panel with monitoring gauges/indicators, starting equipment, fuel tank as well as other accessories. Charger to charge battery package by diesel gen set and PV solar system interface between diesel gen set and PV solar power unit for a smooth operation for the two energy sources in conjunction, automatically without any manual intervention. Factory test certificates must be included and must be in accordance to internationally recognised standards. Suitable for tropical conditions. | Comply and state → | Yes / No
KEY DATA
Make | Please state →
Model | Please state →
Country of origin | Please state →
DIESEL GEN SET
Rated power output, min. 100 kVA | Comply and state → | Yes / No
Power factor: 0.8 | Comply and state → | Yes / No
Rated power output, 80 kW, min. | Comply and state → | Yes / No
Voltage, 220/230/240 and 380/400 V | Comply and state → | Yes / No
Phase: 1 and 3 | Comply and state → | Yes / No
AC frequency, 50/60 Hz | Comply and state → | Yes / No
Speed: rpm 1500 or 3000 or other | Please state →
Prime power according to ISO 8528 or equivalent, i.e. power available at variable load with no limitations on hours of operation and capable of min. 10% overload for min. 1 hour in any 12 hours. | Comply and state → | Yes / No
Prime rating of min. the stated output rating at Normal Temperature and Pressure conditions (NTP). Please state | Comply and state → | Yes / No
Derating information (temperature, altitude and humidity), please state | Please state →
Engine
Make | Please state →
Model | Please state →
Engine power output, kW at rpm: | Please state →
Fuel: Diesel | Comply and state → | Yes / No
Cooling, liquid or air or combined, suitable for tropical conditions | Please state →
Speed governor, state type | Please state →
Exhaust with suitable piping and residential silencer | Comply and state → | Yes / No
Noise level, dB(A) at 1 m (silencer fitted) | Please state →
Fuel consumption at 75% load: L/hour | Please state →
CO2 emissions at 75% load: g/hour | Please state →
Mounted on anti-vibration mounts | Comply and state → | Yes / No
ENVIRONMENTAL
EU Non-road emissions regulations schedule, e.g. EU STAGE II, III A, III B, IV. US Non-road and stationary emissions regulations to Tier 1,2,3,4 or equivalent. Please state. | Comply and state → | Yes / No
Alternator
Make: | Please state →
Model: | Please state →
Brushless type | Comply and state → | Yes / No
Cooling, liquid, air, other | Please state →
Protection class min. IP 23 | Comply and state → | Yes / No
Suitable AC power outlets protected by circuit breaker (state type) | Comply and state → | Yes / No
Insulation to min. IEC 60085 - >155 ° C - (F) or equivalent | Comply and state → | Yes / No
Voltage regulator | Comply and state → | Yes / No
Standard accessories
Fuel tank. Integrated or separate, suitable for continuous operation of min. 8 hours at rated capacity. State capacity, litres. Fuel level gauge. Including all necessary pipework, connections etc. Possibility for connection to external tank. | Comply and state→ | Yes / No
Low oil pressure protection, automatic shut down | Comply and state → | Yes / No
Over heating protection | Comply and state → | Yes / No
Overload protection | Comply and state → | Yes / No
Emergency stop | Comply and state → | Yes / No
Electric starter with key and battery | Comply and state → | Yes / No
Min. Voltmeter, ammeter, hour meter, Hz meter, water temp gauge/indicator (where applicable) | Comply and state → | Yes / No
Earthing/grounding facility | Comply and state → | Yes / No
PV SOLAR POWER SYSTEM STANDARD ARRAY NOMINAL MIN. 8.0 kWp. Battery pack 80 kWh. For Ground or flat roof mount
PV solar array
Make and model: | Please state →
Array kWp, min 10% of diesel generator set max output which is 100 kVA/80kW, hence = 8.0 kWp min. | Comply and state→ | Yes / No
PV panels, total surface covering, m2 | Please state →
Nominal power output each panel, kWp | Please state →
Isc array, A (Amp) | Please state →
Certifications: Any one or more of IEC61215, UL1703 or equivalent | Comply and state → | Yes / No
Charge controller
Make and model: | Please state →
Type: MTTP | Comply and state → | Yes / No
Certifications. Any one or more of EN60730-1/2-11, 55022, 61000-4-27374/5/6 or equivalent | Comply and state→ | Yes / No
Capacity: Isc array +20%, min. | Comply and state→ | Yes / No
Inverter
Make and model: | Please state →
Capacity, A (Amp): Min. equivalent to max load | Comply and state→ | Yes / No
Pure sine curve | Comply and state → | Yes / No
Certifications: Any one or more of EN50178, 62040, 60950, 61000-2/3/6, EN60529, 50438 or equivalent | Comply and state → | Yes / No
Battery package
Make and model: | Please state →
Capacity: Min. equivalent to hybrid diesel gen set full load - 24 kW - for 1 hour = 80 kWh. | Comply and state→ | Yes / No
Battery type: LiFePo4 | Comply and state→ | Yes / No
Certifications,: Any one or more of UL1642, IEC62133, 61000-6-3 or equivalent | Comply and state→ | Yes / No
PV panel racks, brackets, cables, fittings etc.
PV panels racks for Ground or flat roof mount. | Comply and state→ | Yes / No
All cables, junctions, contacts, breakers, earthing spears, fittings, screws, nut and bots etc included | Comply and state → | Yes / No
Installation
The system must be plug and play. Inverter, charge controller, battery package, battery charger must be pre-installed and wired either inside one common Hybrid system cage or in a separate cabinet, in order to easily connect the PV array and the local installation. All cables for establishing the PV array must be readily available with pre-installed connections and clearly marked in a way that no mistakes can occur. | Comply and state → | Yes / No
Other
Lifting points for handling | Comply and state → | Yes / No
Installation instructions, drawings, photos, brochures etc. English/French/Spanish | Comply and state → | Yes / No
Operators and maintenance manual, English/French/Spanish | Comply and state → | Yes / No
Tool kit | Comply and state → | Yes / No
Basic maintenance kit, engine: Min. 4 x oil filters, 2 x air filters, 2 x fuel filters | Comply and state → | Yes / No
Dimensions, L x W x H, mm | Please state →
Weight, dry, entire hybrid system incl. Battery package and all PV panels, cables, brackets etc etc.: kg: | Please state →
WARRANTY
Diesel Generator set: 2 years/2500 hours of operation which ever occur first. PV panels: Min. 10 years. Min. 90% performance guarantee at 10 years. Min. 80% performance guarantee at 20 years. Battery package: Min. 5 years. Inverter/charge controller/charger: Min. 4 years. Other equipment: Min. 2 years | Comply and state → | Yes / No
Sustainability
The bidder must demonstrate that its organisation has an environmental management system in place which as a minimum shall submit at least one or more of the following : the environmental policy principles of the organisation; the management measures and procedures taken or that will be taken to assess, monitor, measure and mitigate environmental impacts of the business processes/products associated with the execution of the contract; how attention is paid to the awareness and training/competency of employee(s) and supplier(s) with regard to dealing with the environmental aspects relevant to this bid; and that compliance with the environmental legislation applicable to the required performance(s) is guaranteed, ISO 14001 certificate, EMAS or an equivalent certificate | Comply and state → | Yes / No
The bidder shall provide documentation which outlines their approach to ensuring equal opportunity, diversity and inclusion within their organisation (e.g. equal pay policy, parental leave, ratio of females/males employees, % of female in management positions, grievances disaggregated by gender, transparency of promotion criteria, sexual harassment policies) | Comply and state → | Yes / No
Mandatory Options
Diesel engine spare parts & maintenance kit for min. 2500 hours of operation | Mandatory | enter prices on Form C: Price Schedule
Sound insolating and water proof canopy (max. 70 dB(A) at 7 m) | Mandatory | enter prices on Form C: Price Schedule
Work shop manual | Mandatory | enter prices on Form C: Price Schedule
Spare parts catalogue | Mandatory | enter prices on Form C: Price Schedule
60 Hz version of Generator set, please enter any surcharge to the std 50 Hz version offered above | Mandatory | enter prices on Form C: Price Schedule
Suggested Options
Heavy duty air filter for dusty conditions | Please provide price or state STD→ | Submit other option prices on a separate form
Heavy duty fuel filter/additional fuel filter in line with original | Please provide price or state STD→ | Submit other option prices on a separate form
Additional silencer, state dB(A) at 1 m and/or 7 m | Please provide price or state STD→ | Submit other option prices on a separate form
High chimney for exhaust, state height and materials | Please provide price or state STD→ | Submit other option prices on a separate form
(ATS) Automatic Transfer Switch | Please provide price or state STD→ | Submit other option prices on a separate form
Over speed protection | Please provide price or state STD→ | Submit other option prices on a separate form
Manual transfer switch | Please provide price or state STD→ | Submit other option prices on a separate form
External fuel tank with pipes including min.. 10 meter non-corrosive material and fittings, state volume of tank and material | Please provide price or state STD→ | Submit other option prices on a separate form
Slow moving trolley/trailer | Please provide price or state STD→ | Submit other option prices on a separate form
(AMF) Automatic Mains Failure Power generation set | Please provide price or state STD→ | Submit other option prices on a separate form
Automatic main circuit breaker | Please provide price or state STD→ | Submit other option prices on a separate form
Installation instructions and eventual. drawings, other languages | Please provide price or state STD→ | Submit other option prices on a separate form
Change over switch positions for: 1) Mains 2) Off 3) GENERATOR SET | Please provide price or state STD→ | Submit other option prices on a separate form
Automatic main circuit breaker | Please provide price or state STD→ | Submit other option prices on a separate form
Operators and maintenance manual, other languages | Please provide price or state STD→ | Submit other option prices on a separate form

## Lot 23 100 kVA PV 20% Ground
Bidder name:
Make and model:
Lot 23. 100 kVA PV 20% Ground or flat roof mounted
HYBRID PV SOLAR/DIESEL GENERATOR SET SPECS | UNOPS REQUIREMENTS | Bidder: Compliant/Non-compliant to UNOPS requirements? Please mark YES/NO in this coloumn. Not indicating YES/NO in this column may render your bid non-compliant. | Bidders are required to provide information in this column on the specifications of their bid to demonstrate compliance to set specifications. Not providing specifications under this column may render your bid non-compliant.
Complete Hybrid PV solar/diesel generator set for autonomous operation, including PV solar power array, battery package, inverter and charge controller. Diesel engine, alternator, control panel with monitoring gauges/indicators, starting equipment, fuel tank as well as other accessories. Charger to charge battery package by diesel gen set and PV solar system interface between diesel gen set and PV solar power unit for a smooth operation for the two energy sources in conjunction, automatically without any manual intervention. Factory test certificates must be included and must be in accordance to internationally recognised standards. Suitable for tropical conditions. | Comply and state → | Yes / No
KEY DATA
Make | Please state →
Model | Please state →
Country of origin | Please state →
DIESEL GEN SET
Rated power output, min. 100 kVA | Comply and state → | Yes / No
Power factor: 0.8 | Comply and state → | Yes / No
Rated power output, 80 kW, min. | Comply and state → | Yes / No
Voltage, 220/230/240 and 380/400 V | Comply and state → | Yes / No
Phase: 1 and 3 | Comply and state → | Yes / No
AC frequency, 50/60 Hz | Comply and state → | Yes / No
Speed: rpm 1500 or 3000 or other | Please state →
Prime power according to ISO 8528 or equivalent, i.e. power available at variable load with no limitations on hours of operation and capable of min. 10% overload for min. 1 hour in any 12 hours. | Comply and state → | Yes / No
Prime rating of min. the stated output rating at Normal Temperature and Pressure conditions (NTP). Please state | Comply and state → | Yes / No
Derating information (temperature, altitude and humidity), please state | Please state →
Engine
Make | Please state →
Model | Please state →
Engine power output, kW at rpm: | Please state →
Fuel: Diesel | Comply and state → | Yes / No
Cooling, liquid or air or combined, suitable for tropical conditions | Please state →
Speed governor, state type | Please state →
Exhaust with suitable piping and residential silencer | Comply and state → | Yes / No
Noise level, dB(A) at 1 m (silencer fitted) | Please state →
Fuel consumption at 75% load: L/hour | Please state →
CO2 emissions at 75% load: g/hour | Please state →
Mounted on anti-vibration mounts | Comply and state → | Yes / No
ENVIRONMENTAL
EU Non-road emissions regulations schedule, e.g. EU STAGE II, III A, III B, IV. US Non-road and stationary emissions regulations to Tier 1,2,3,4 or equivalent. Please state. | Comply and state → | Yes / No
Alternator
Make: | Please state →
Model: | Please state →
Brushless type | Comply and state → | Yes / No
Cooling, liquid, air, other | Please state →
Protection class min. IP 23 | Comply and state → | Yes / No
Suitable AC power outlets protected by circuit breaker (state type) | Comply and state → | Yes / No
Insulation to min. IEC 60085 - >155 ° C - (F) or equivalent | Comply and state → | Yes / No
Voltage regulator | Comply and state → | Yes / No
Standard accessories
Fuel tank. Integrated or separate, suitable for continuous operation of min. 8 hours at rated capacity. State capacity, litres. Fuel level gauge. Including all necessary pipework, connections etc. Possibility for connection to external tank. | Comply and state→ | Yes / No
Low oil pressure protection, automatic shut down | Comply and state → | Yes / No
Over heating protection | Comply and state → | Yes / No
Overload protection | Comply and state → | Yes / No
Emergency stop | Comply and state → | Yes / No
Electric starter with key and battery | Comply and state → | Yes / No
Min. Voltmeter, ammeter, hour meter, Hz meter, water temp gauge/indicator (where applicable) | Comply and state → | Yes / No
Earthing/grounding facility | Comply and state → | Yes / No
PV SOLAR POWER SYSTEM STANDARD ARRAY NOMINAL MIN. 16.0 kWp. Battery pack 80 kWh. For Ground or flat roof mount
PV solar array
Make and model: | Please state →
Array kWp, min 20 % of diesel generator set max output which is 100 kVA/80kW, hence = 16.0 kWp min. | Comply and state→ | Yes / No
PV panels, total surface covering, m2 | Please state →
Nominal power output each panel, kWp | Please state →
Isc array, A (Amp) | Please state →
Certifications: Any one or more of IEC61215, UL1703 or equivalent | Comply and state → | Yes / No
Charge controller
Make and model: | Please state →
Type: MTTP | Comply and state → | Yes / No
Certifications. Any one or more of EN60730-1/2-11, 55022, 61000-4-27374/5/6 or equivalent | Comply and state→ | Yes / No
Capacity: Isc array +20%, min. | Comply and state→ | Yes / No
Inverter
Make and model: | Please state →
Capacity, A (Amp): Min. equivalent to max load | Comply and state→ | Yes / No
Pure sine curve | Comply and state → | Yes / No
Certifications: Any one or more of EN50178, 62040, 60950, 61000-2/3/6, EN60529, 50438 or equivalent | Comply and state → | Yes / No
Battery package
Make and model: | Please state →
Capacity: Min. equivalent to hybrid diesel gen set full load - 24 kW - for 1 hour = 80 kWh. | Comply and state→ | Yes / No
Battery type: LiFePo4 | Comply and state→ | Yes / No
Certifications,: Any one or more of UL1642, IEC62133, 61000-6-3 or equivalent | Comply and state→ | Yes / No
PV panel racks, brackets, cables, fittings etc.
PV panels racks for Ground or flat roof mount. | Comply and state→ | Yes / No
All cables, junctions, contacts, breakers, earthing spears, fittings, screws, nut and bots etc included | Comply and state → | Yes / No
Installation
The system must be plug and play. Inverter, charge controller, battery package, battery charger must be pre-installed and wired either inside one common Hybrid system cage or in a separate cabinet, in order to easily connect the PV array and the local installation. All cables for establishing the PV array must be readily available with pre-installed connections and clearly marked in a way that no mistakes can occur. | Comply and state → | Yes / No
Other
Lifting points for handling | Comply and state → | Yes / No
Installation instructions, drawings, photos, brochures etc. English/French/Spanish | Comply and state → | Yes / No
Operators and maintenance manual, English/French/Spanish | Comply and state → | Yes / No
Tool kit | Comply and state → | Yes / No
Basic maintenance kit, engine: Min. 4 x oil filters, 2 x air filters, 2 x fuel filters | Comply and state → | Yes / No
Dimensions, L x W x H, mm | Please state →
Weight, dry, entire hybrid system incl. Battery package and all PV panels, cables, brackets etc etc.: kg: | Please state →
WARRANTY
Diesel Generator set: 2 years/2500 hours of operation which ever occur first. PV panels: Min. 10 years. Min. 90% performance guarantee at 10 years. Min. 80% performance guarantee at 20 years. Battery package: Min. 5 years. Inverter/charge controller/charger: Min. 4 years. Other equipment: Min. 2 years | Comply and state → | Yes / No
Sustainability
The bidder must demonstrate that its organisation has an environmental management system in place which as a minimum shall submit at least one or more of the following : the environmental policy principles of the organisation; the management measures and procedures taken or that will be taken to assess, monitor, measure and mitigate environmental impacts of the business processes/products associated with the execution of the contract; how attention is paid to the awareness and training/competency of employee(s) and supplier(s) with regard to dealing with the environmental aspects relevant to this bid; and that compliance with the environmental legislation applicable to the required performance(s) is guaranteed, ISO 14001 certificate, EMAS or an equivalent certificate | Comply and state → | Yes / No
The bidder shall provide documentation which outlines their approach to ensuring equal opportunity, diversity and inclusion within their organisation (e.g. equal pay policy, parental leave, ratio of females/males employees, % of female in management positions, grievances disaggregated by gender, transparency of promotion criteria, sexual harassment policies) | Comply and state → | Yes / No
Mandatory Options
Diesel engine spare parts & maintenance kit for min. 2500 hours of operation | Mandatory | enter prices on Form C: Price Schedule
Sound insolating and water proof canopy (max. 70 dB(A) at 7 m) | Mandatory | enter prices on Form C: Price Schedule
Work shop manual | Mandatory | enter prices on Form C: Price Schedule
Spare parts catalogue | Mandatory | enter prices on Form C: Price Schedule
60 Hz version of Generator set, please enter any surcharge to the std 50 Hz version offered above | Mandatory | enter prices on Form C: Price Schedule
Suggested Options
Heavy duty air filter for dusty conditions | Please provide price or state STD→ | Submit other option prices on a separate form
Heavy duty fuel filter/additional fuel filter in line with original | Please provide price or state STD→ | Submit other option prices on a separate form
Additional silencer, state dB(A) at 1 m and/or 7 m | Please provide price or state STD→ | Submit other option prices on a separate form
High chimney for exhaust, state height and materials | Please provide price or state STD→ | Submit other option prices on a separate form
(ATS) Automatic Transfer Switch | Please provide price or state STD→ | Submit other option prices on a separate form
Over speed protection | Please provide price or state STD→ | Submit other option prices on a separate form
Manual transfer switch | Please provide price or state STD→ | Submit other option prices on a separate form
External fuel tank with pipes including min.. 10 meter non-corrosive material and fittings, state volume of tank and material | Please provide price or state STD→ | Submit other option prices on a separate form
Slow moving trolley/trailer | Please provide price or state STD→ | Submit other option prices on a separate form
(AMF) Automatic Mains Failure Power generation set | Please provide price or state STD→ | Submit other option prices on a separate form
Automatic main circuit breaker | Please provide price or state STD→ | Submit other option prices on a separate form
Installation instructions and eventual. drawings, other languages | Please provide price or state STD→ | Submit other option prices on a separate form
Change over switch positions for: 1) Mains 2) Off 3) GENERATOR SET | Please provide price or state STD→ | Submit other option prices on a separate form
Automatic main circuit breaker | Please provide price or state STD→ | Submit other option prices on a separate form
Operators and maintenance manual, other languages | Please provide price or state STD→ | Submit other option prices on a separate form

## Lot 24 100 kVA PV 40% Ground
Bidder name:
Make and model:
Lot 24. 100 kVA PV 40% Ground or flat roof mounted
HYBRID PV SOLAR/DIESEL GENERATOR SET SPECS | UNOPS REQUIREMENTS | Bidder: Compliant/Non-compliant to UNOPS requirements? Please mark YES/NO in this coloumn. Not indicating YES/NO in this column may render your bid non-compliant. | Bidders are required to provide information in this column on the specifications of their bid to demonstrate compliance to set specifications. Not providing specifications under this column may render your bid non-compliant.
Complete Hybrid PV solar/diesel generator set for autonomous operation, including PV solar power array, battery package, inverter and charge controller. Diesel engine, alternator, control panel with monitoring gauges/indicators, starting equipment, fuel tank as well as other accessories. Charger to charge battery package by diesel gen set and PV solar system interface between diesel gen set and PV solar power unit for a smooth operation for the two energy sources in conjunction, automatically without any manual intervention. Factory test certificates must be included and must be in accordance to internationally recognised standards. Suitable for tropical conditions. | Comply and state → | Yes / No
KEY DATA
Make | Please state →
Model | Please state →
Country of origin | Please state →
DIESEL GEN SET
Rated power output, min. 100 kVA | Comply and state → | Yes / No
Power factor: 0.8 | Comply and state → | Yes / No
Rated power output, 80 kW, min. | Comply and state → | Yes / No
Voltage, 220/230/240 and 380/400 V | Comply and state → | Yes / No
Phase: 1 and 3 | Comply and state → | Yes / No
AC frequency, 50/60 Hz | Comply and state → | Yes / No
Speed: rpm 1500 or 3000 or other | Please state →
Prime power according to ISO 8528 or equivalent, i.e. power available at variable load with no limitations on hours of operation and capable of min. 10% overload for min. 1 hour in any 12 hours. | Comply and state → | Yes / No
Prime rating of min. the stated output rating at Normal Temperature and Pressure conditions (NTP). Please state | Comply and state → | Yes / No
Derating information (temperature, altitude and humidity), please state | Please state →
Engine
Make | Please state →
Model | Please state →
Engine power output, kW at rpm: | Please state →
Fuel: Diesel | Comply and state → | Yes / No
Cooling, liquid or air or combined, suitable for tropical conditions | Please state →
Speed governor, state type | Please state →
Exhaust with suitable piping and residential silencer | Comply and state → | Yes / No
Noise level, dB(A) at 1 m (silencer fitted) | Please state →
Fuel consumption at 75% load: L/hour | Please state →
CO2 emissions at 75% load: g/hour | Please state →
Mounted on anti-vibration mounts | Comply and state → | Yes / No
ENVIRONMENTAL
EU Non-road emissions regulations schedule, e.g. EU STAGE II, III A, III B, IV. US Non-road and stationary emissions regulations to Tier 1,2,3,4 or equivalent. Please state. | Comply and state → | Yes / No
Alternator
Make: | Please state →
Model: | Please state →
Brushless type | Comply and state → | Yes / No
Cooling, liquid, air, other | Please state →
Protection class min. IP 23 | Comply and state → | Yes / No
Suitable AC power outlets protected by circuit breaker (state type) | Comply and state → | Yes / No
Insulation to min. IEC 60085 - >155 ° C - (F) or equivalent | Comply and state → | Yes / No
Voltage regulator | Comply and state → | Yes / No
Standard accessories
Fuel tank. Integrated or separate, suitable for continuous operation of min. 8 hours at rated capacity. State capacity, litres. Fuel level gauge. Including all necessary pipework, connections etc. Possibility for connection to external tank. | Comply and state→ | Yes / No
Low oil pressure protection, automatic shut down | Comply and state → | Yes / No
Over heating protection | Comply and state → | Yes / No
Overload protection | Comply and state → | Yes / No
Emergency stop | Comply and state → | Yes / No
Electric starter with key and battery | Comply and state → | Yes / No
Min. Voltmeter, ammeter, hour meter, Hz meter, water temp gauge/indicator (where applicable) | Comply and state → | Yes / No
Earthing/grounding facility | Comply and state → | Yes / No
PV SOLAR POWER SYSTEM STANDARD ARRAY NOMINAL MIN. 32.0 kWp. Battery pack 80 kWh. For Ground or flat roof mount
PV solar array
Make and model: | Please state →
Array kWp, min 40% of diesel generator set max output which is 100 kVA/80kW, hence = 32.0 kWp min. | Comply and state→ | Yes / No
PV panels, total surface covering, m2 | Please state →
Nominal power output each panel, kWp | Please state →
Isc array, A (Amp) | Please state →
Certifications: Any one or more of IEC61215, UL1703 or equivalent | Comply and state → | Yes / No
Charge controller
Make and model: | Please state →
Type: MTTP | Comply and state → | Yes / No
Certifications. Any one or more of EN60730-1/2-11, 55022, 61000-4-27374/5/6 or equivalent | Comply and state→ | Yes / No
Capacity: Isc array +20%, min. | Comply and state→ | Yes / No
Inverter
Make and model: | Please state →
Capacity, A (Amp): Min. equivalent to max load | Comply and state→ | Yes / No
Pure sine curve | Comply and state → | Yes / No
Certifications: Any one or more of EN50178, 62040, 60950, 61000-2/3/6, EN60529, 50438 or equivalent | Comply and state → | Yes / No
Battery package
Make and model: | Please state →
Capacity: Min. equivalent to hybrid diesel gen set full load - 24 kW - for 1 hour = 80 kWh. | Comply and state→ | Yes / No
Battery type: LiFePo4 | Comply and state→ | Yes / No
Certifications,: Any one or more of UL1642, IEC62133, 61000-6-3 or equivalent | Comply and state→ | Yes / No
PV panel racks, brackets, cables, fittings etc.
PV panels racks for Ground or flat roof mount. | Comply and state→ | Yes / No
All cables, junctions, contacts, breakers, earthing spears, fittings, screws, nut and bots etc included | Comply and state → | Yes / No
Installation
The system must be plug and play. Inverter, charge controller, battery package, battery charger must be pre-installed and wired either inside one common Hybrid system cage or in a separate cabinet, in order to easily connect the PV array and the local installation. All cables for establishing the PV array must be readily available with pre-installed connections and clearly marked in a way that no mistakes can occur. | Comply and state → | Yes / No
Other
Lifting points for handling | Comply and state → | Yes / No
Installation instructions, drawings, photos, brochures etc. English/French/Spanish | Comply and state → | Yes / No
Operators and maintenance manual, English/French/Spanish | Comply and state → | Yes / No
Tool kit | Comply and state → | Yes / No
Basic maintenance kit, engine: Min. 4 x oil filters, 2 x air filters, 2 x fuel filters | Comply and state → | Yes / No
Dimensions, L x W x H, mm | Please state →
Weight, dry, entire hybrid system incl. Battery package and all PV panels, cables, brackets etc etc.: kg: | Please state →
WARRANTY
Diesel Generator set: 2 years/2500 hours of operation which ever occur first. PV panels: Min. 10 years. Min. 90% performance guarantee at 10 years. Min. 80% performance guarantee at 20 years. Battery package: Min. 5 years. Inverter/charge controller/charger: Min. 4 years. Other equipment: Min. 2 years | Comply and state → | Yes / No
Sustainability
The bidder must demonstrate that its organisation has an environmental management system in place which as a minimum shall submit at least one or more of the following : the environmental policy principles of the organisation; the management measures and procedures taken or that will be taken to assess, monitor, measure and mitigate environmental impacts of the business processes/products associated with the execution of the contract; how attention is paid to the awareness and training/competency of employee(s) and supplier(s) with regard to dealing with the environmental aspects relevant to this bid; and that compliance with the environmental legislation applicable to the required performance(s) is guaranteed, ISO 14001 certificate, EMAS or an equivalent certificate | Comply and state → | Yes / No
The bidder shall provide documentation which outlines their approach to ensuring equal opportunity, diversity and inclusion within their organisation (e.g. equal pay policy, parental leave, ratio of females/males employees, % of female in management positions, grievances disaggregated by gender, transparency of promotion criteria, sexual harassment policies) | Comply and state → | Yes / No
Mandatory Options
Diesel engine spare parts & maintenance kit for min. 2500 hours of operation | Mandatory | enter prices on Form C: Price Schedule
Sound insolating and water proof canopy (max. 70 dB(A) at 7 m) | Mandatory | enter prices on Form C: Price Schedule
Work shop manual | Mandatory | enter prices on Form C: Price Schedule
Spare parts catalogue | Mandatory | enter prices on Form C: Price Schedule
60 Hz version of Generator set, please enter any surcharge to the std 50 Hz version offered above | Mandatory | enter prices on Form C: Price Schedule
Suggested Options
Heavy duty air filter for dusty conditions | Please provide price or state STD→ | Submit other option prices on a separate form
Heavy duty fuel filter/additional fuel filter in line with original | Please provide price or state STD→ | Submit other option prices on a separate form
Additional silencer, state dB(A) at 1 m and/or 7 m | Please provide price or state STD→ | Submit other option prices on a separate form
High chimney for exhaust, state height and materials | Please provide price or state STD→ | Submit other option prices on a separate form
(ATS) Automatic Transfer Switch | Please provide price or state STD→ | Submit other option prices on a separate form
Over speed protection | Please provide price or state STD→ | Submit other option prices on a separate form
Manual transfer switch | Please provide price or state STD→ | Submit other option prices on a separate form
External fuel tank with pipes including min.. 10 meter non-corrosive material and fittings, state volume of tank and material | Please provide price or state STD→ | Submit other option prices on a separate form
Slow moving trolley/trailer | Please provide price or state STD→ | Submit other option prices on a separate form
(AMF) Automatic Mains Failure Power generation set | Please provide price or state STD→ | Submit other option prices on a separate form
Automatic main circuit breaker | Please provide price or state STD→ | Submit other option prices on a separate form
Installation instructions and eventual. drawings, other languages | Please provide price or state STD→ | Submit other option prices on a separate form
Change over switch positions for: 1) Mains 2) Off 3) GENERATOR SET | Please provide price or state STD→ | Submit other option prices on a separate form
Automatic main circuit breaker | Please provide price or state STD→ | Submit other option prices on a separate form
Operators and maintenance manual, other languages | Please provide price or state STD→ | Submit other option prices on a separate form

## Lot 25 150 kVA PV 10% Roof
Bidder name:
Make and model:
Lot 25 150 kVA PV 10% Sloped Roof or Gen set mount.
HYBRID PV SOLAR/DIESEL GENERATOR SET SPECS | UNOPS REQUIREMENTS | Bidder: Compliant/Non-compliant to UNOPS requirements? Please mark YES/NO in this coloumn. Not indicating YES/NO in this column may render your bid non-compliant. | Bidders are required to provide information in this column on the specifications of their bid to demonstrate compliance to set specifications. Not providing specifications under this column may render your bid non-compliant.
Complete Hybrid PV solar/diesel generator set for autonomous operation, including PV solar power array, battery package, inverter and charge controller. Diesel engine, alternator, control panel with monitoring gauges/indicators, starting equipment, fuel tank as well as other accessories. Charger to charge battery package by diesel gen set and PV solar system interface between diesel gen set and PV solar power unit for a smooth operation for the two energy sources in conjunction, automatically without any manual intervention. Factory test certificates must be included and must be in accordance to internationally recognised standards. Suitable for tropical conditions. | Comply and state → | Yes / No
KEY DATA
Make | Please state →
Model | Please state →
Country of origin | Please state →
DIESEL GEN SET
Rated power output, min. 150 kVA | Comply and state → | Yes / No
Power factor: 0.8 | Comply and state → | Yes / No
Rated power output, 120 kW, min. | Comply and state → | Yes / No
Voltage, 220/230/240 and 380/400 V | Comply and state → | Yes / No
Phase: 1 and 3 | Comply and state → | Yes / No
AC frequency, 50/60 Hz | Comply and state → | Yes / No
Speed: rpm 1500 or 3000 or other | Please state →
Prime power according to ISO 8528 or equivalent, i.e. power available at variable load with no limitations on hours of operation and capable of min. 10% overload for min. 1 hour in any 12 hours. | Comply and state → | Yes / No
Prime rating of min. the stated output rating at Normal Temperature and Pressure conditions (NTP). Please state | Comply and state → | Yes / No
Derating information (temperature, altitude and humidity), please state | Please state →
Engine
Make | Please state →
Model | Please state →
Engine power output, kW at rpm: | Please state →
Fuel: Diesel | Comply and state → | Yes / No
Cooling, liquid or air or combined, suitable for tropical conditions | Please state →
Speed governor, state type | Please state →
Exhaust with suitable piping and residential silencer | Comply and state → | Yes / No
Noise level, dB(A) at 1 m (silencer fitted) | Please state →
Fuel consumption at 75% load: L/hour | Please state →
CO2 emissions at 75% load: g/hour | Please state →
Mounted on anti-vibration mounts | Comply and state → | Yes / No
ENVIRONMENTAL
EU Non-road emissions regulations schedule, e.g. EU STAGE II, III A, III B, IV. US Non-road and stationary emissions regulations to Tier 1,2,3,4 or equivalent. Please state. | Comply and state → | Yes / No
Alternator
Make: | Please state →
Model: | Please state →
Brushless type | Comply and state → | Yes / No
Cooling, liquid, air, other | Please state →
Protection class min. IP 23 | Comply and state → | Yes / No
Suitable AC power outlets protected by circuit breaker (state type) | Comply and state → | Yes / No
Insulation to min. IEC 60085 - >155 ° C - (F) or equivalent | Comply and state → | Yes / No
Voltage regulator | Comply and state → | Yes / No
Standard accessories
Fuel tank. Integrated or separate, suitable for continuous operation of min. 8 hours at rated capacity. State capacity, litres. Fuel level gauge. Including all necessary pipework, connections etc. Possibility for connection to external tank. | Comply and state→ | Yes / No
Low oil pressure protection, automatic shut down | Comply and state → | Yes / No
Over heating protection | Comply and state → | Yes / No
Overload protection | Comply and state → | Yes / No
Emergency stop | Comply and state → | Yes / No
Electric starter with key and battery | Comply and state → | Yes / No
Min. Voltmeter, ammeter, hour meter, Hz meter, water temp gauge/indicator (where applicable) | Comply and state → | Yes / No
Earthing/grounding facility | Comply and state → | Yes / No
PV SOLAR POWER SYSTEM STANDARD ARRAY NOMINAL MIN. 12.0 kWp. Battery pack 120 kWh. For Sloped Roof or Gen set mount.
PV solar array
Make and model: | Please state →
Array kWp, min 10% of diesel generator set max output which is 150 kVA/120kW, hence = 12.0kWp min. | Comply and state→ | Yes / No
PV panels, total surface covering, m2 | Please state →
Nominal power output each panel, kWp | Please state →
Isc array, A (Amp) | Please state →
Certifications: Any one or more of IEC61215, UL1703 or equivalent | Comply and state → | Yes / No
Charge controller
Make and model: | Please state →
Type: MTTP | Comply and state → | Yes / No
Certifications. Any one or more of EN60730-1/2-11, 55022, 61000-4-27374/5/6 or equivalent | Comply and state→ | Yes / No
Capacity: Isc array +20%, min. | Comply and state→ | Yes / No
Inverter
Make and model: | Please state →
Capacity, A (Amp): Min. equivalent to max load | Comply and state→ | Yes / No
Pure sine curve | Comply and state → | Yes / No
Certifications: Any one or more of EN50178, 62040, 60950, 61000-2/3/6, EN60529, 50438 or equivalent | Comply and state → | Yes / No
Battery package
Make and model: | Please state →
Capacity: Min. equivalent to hybrid diesel gen set full load - 24 kW - for 1 hour = 120kWh. | Comply and state→ | Yes / No
Battery type: LiFePo4 | Comply and state→ | Yes / No
Certifications,: Any one or more of UL1642, IEC62133, 61000-6-3 or equivalent | Comply and state→ | Yes / No
PV panel racks, brackets, cables, fittings etc. | Comply and state→
PV panels racks for sloped roof mount included for all included PV panels, if not attached to the Hybrid Gen set system itself (permanently or fold-out system etc). | Comply and state→ | Yes / No
All cables, junctions, contacts, breakers, earthing spears, fittings, screws, nut and bots etc included | Comply and state → | Yes / No
Installation
The system must be plug and play. Inverter, charge controller, battery package, battery charger must be pre-installed and wired either inside one common Hybrid system cage or in a separate cabinet, in order to easily connect the PV array and the local installation. All cables for establishing the PV array must be readily available with pre-installed connections and clearly marked in a way that no mistakes can occur. | Comply and state → | Yes / No
Other
Lifting points for handling | Comply and state → | Yes / No
Installation instructions, drawings, photos, brochures etc. English/French/Spanish | Comply and state → | Yes / No
Operators and maintenance manual, English/French/Spanish | Comply and state → | Yes / No
Tool kit | Comply and state → | Yes / No
Basic maintenance kit, engine: Min. 4 x oil filters, 2 x air filters, 2 x fuel filters | Comply and state → | Yes / No
Dimensions, L x W x H, mm | Please state →
Weight, dry, entire hybrid system incl. Battery package and all PV panels, cables, brackets etc etc.: kg: | Please state →
WARRANTY
Diesel Generator set: 2 years/2500 hours of operation which ever occur first. PV panels: Min. 10 years. Min. 90% performance guarantee at 10 years. Min. 80% performance guarantee at 20 years. Battery package: Min. 5 years. Inverter/charge controller/charger: Min. 4 years. Other equipment: Min. 2 years | Comply and state → | Yes / No
Sustainability
The bidder must demonstrate that its organisation has an environmental management system in place which as a minimum shall submit at least one or more of the following : the environmental policy principles of the organisation; the management measures and procedures taken or that will be taken to assess, monitor, measure and mitigate environmental impacts of the business processes/products associated with the execution of the contract; how attention is paid to the awareness and training/competency of employee(s) and supplier(s) with regard to dealing with the environmental aspects relevant to this bid; and that compliance with the environmental legislation applicable to the required performance(s) is guaranteed, ISO 14001 certificate, EMAS or an equivalent certificate | Comply and state → | Yes / No
The bidder shall provide documentation which outlines their approach to ensuring equal opportunity, diversity and inclusion within their organisation (e.g. equal pay policy, parental leave, ratio of females/males employees, % of female in management positions, grievances disaggregated by gender, transparency of promotion criteria, sexual harassment policies) | Comply and state → | Yes / No
Mandatory Options
Diesel engine spare parts & maintenance kit for min. 2500 hours of operation | Mandatory | enter prices on Form C: Price Schedule
Sound insolating and water proof canopy (max. 70 dB(A) at 7 m) | Mandatory | enter prices on Form C: Price Schedule
Work shop manual | Mandatory | enter prices on Form C: Price Schedule
Spare parts catalogue | Mandatory | enter prices on Form C: Price Schedule
60 Hz version of Generator set, please enter any surcharge to the std 50 Hz version offered above | Mandatory | enter prices on Form C: Price Schedule
Suggested Options
Heavy duty air filter for dusty conditions | Please provide price or state STD→ | Submit other option prices on a separate form
Heavy duty fuel filter/additional fuel filter in line with original | Please provide price or state STD→ | Submit other option prices on a separate form
Additional silencer, state dB(A) at 1 m and/or 7 m | Please provide price or state STD→ | Submit other option prices on a separate form
High chimney for exhaust, state height and materials | Please provide price or state STD→ | Submit other option prices on a separate form
(ATS) Automatic Transfer Switch | Please provide price or state STD→ | Submit other option prices on a separate form
Over speed protection | Please provide price or state STD→ | Submit other option prices on a separate form
Manual transfer switch | Please provide price or state STD→ | Submit other option prices on a separate form
External fuel tank with pipes including min.. 10 meter non-corrosive material and fittings, state volume of tank and material | Please provide price or state STD→ | Submit other option prices on a separate form
Slow moving trolley/trailer | Please provide price or state STD→ | Submit other option prices on a separate form
(AMF) Automatic Mains Failure Power generation set | Please provide price or state STD→ | Submit other option prices on a separate form
Automatic main circuit breaker | Please provide price or state STD→ | Submit other option prices on a separate form
Installation instructions and eventual. drawings, other languages | Please provide price or state STD→ | Submit other option prices on a separate form
Change over switch positions for: 1) Mains 2) Off 3) GENERATOR SET | Please provide price or state STD→ | Submit other option prices on a separate form
Automatic main circuit breaker | Please provide price or state STD→ | Submit other option prices on a separate form
Operators and maintenance manual, other languages | Please provide price or state STD→ | Submit other option prices on a separate form

## Lot 26 150 kVA PV 20% Roof
Bidder name:
Make and model:
Lot 26 150 kVA PV 20% Sloped Roof or Gen set mount.
HYBRID PV SOLAR/DIESEL GENERATOR SET SPECS | UNOPS REQUIREMENTS | Bidder: Compliant/Non-compliant to UNOPS requirements? Please mark YES/NO in this coloumn. Not indicating YES/NO in this column may render your bid non-compliant. | Bidders are required to provide information in this column on the specifications of their bid to demonstrate compliance to set specifications. Not providing specifications under this column may render your bid non-compliant.
Complete Hybrid PV solar/diesel generator set for autonomous operation, including PV solar power array, battery package, inverter and charge controller. Diesel engine, alternator, control panel with monitoring gauges/indicators, starting equipment, fuel tank as well as other accessories. Charger to charge battery package by diesel gen set and PV solar system interface between diesel gen set and PV solar power unit for a smooth operation for the two energy sources in conjunction, automatically without any manual intervention. Factory test certificates must be included and must be in accordance to internationally recognised standards. Suitable for tropical conditions. | Comply and state → | Yes / No
KEY DATA
Make | Please state →
Model | Please state →
Country of origin | Please state →
DIESEL GEN SET
Rated power output, min. 150 kVA | Comply and state → | Yes / No
Power factor: 0.8 | Comply and state → | Yes / No
Rated power output, 120 kW, min. | Comply and state → | Yes / No
Voltage, 220/230/240 and 380/400 V | Comply and state → | Yes / No
Phase: 1 and 3 | Comply and state → | Yes / No
AC frequency, 50/60 Hz | Comply and state → | Yes / No
Speed: rpm 1500 or 3000 or other | Please state →
Prime power according to ISO 8528 or equivalent, i.e. power available at variable load with no limitations on hours of operation and capable of min. 10% overload for min. 1 hour in any 12 hours. | Comply and state → | Yes / No
Prime rating of min. the stated output rating at Normal Temperature and Pressure conditions (NTP). Please state | Comply and state → | Yes / No
Derating information (temperature, altitude and humidity), please state | Please state →
Engine
Make | Please state →
Model | Please state →
Engine power output, kW at rpm: | Please state →
Fuel: Diesel | Comply and state → | Yes / No
Cooling, liquid or air or combined, suitable for tropical conditions | Please state →
Speed governor, state type | Please state →
Exhaust with suitable piping and residential silencer | Comply and state → | Yes / No
Noise level, dB(A) at 1 m (silencer fitted) | Please state →
Fuel consumption at 75% load: L/hour | Please state →
CO2 emissions at 75% load: g/hour | Please state →
Mounted on anti-vibration mounts | Comply and state → | Yes / No
ENVIRONMENTAL
EU Non-road emissions regulations schedule, e.g. EU STAGE II, III A, III B, IV. US Non-road and stationary emissions regulations to Tier 1,2,3,4 or equivalent. Please state. | Comply and state → | Yes / No
Alternator
Make: | Please state →
Model: | Please state →
Brushless type | Comply and state → | Yes / No
Cooling, liquid, air, other | Please state →
Protection class min. IP 23 | Comply and state → | Yes / No
Suitable AC power outlets protected by circuit breaker (state type) | Comply and state → | Yes / No
Insulation to min. IEC 60085 - >155 ° C - (F) or equivalent | Comply and state → | Yes / No
Voltage regulator | Comply and state → | Yes / No
Standard accessories
Fuel tank. Integrated or separate, suitable for continuous operation of min. 8 hours at rated capacity. State capacity, litres. Fuel level gauge. Including all necessary pipework, connections etc. Possibility for connection to external tank. | Comply and state→ | Yes / No
Low oil pressure protection, automatic shut down | Comply and state → | Yes / No
Over heating protection | Comply and state → | Yes / No
Overload protection | Comply and state → | Yes / No
Emergency stop | Comply and state → | Yes / No
Electric starter with key and battery | Comply and state → | Yes / No
Min. Voltmeter, ammeter, hour meter, Hz meter, water temp gauge/indicator (where applicable) | Comply and state → | Yes / No
Earthing/grounding facility | Comply and state → | Yes / No
PV SOLAR POWER SYSTEM STANDARD ARRAY NOMINAL MIN.24.0 kWp. Battery pack 120 kWh. For Sloped Roof or Gen set mount.
PV solar array
Make and model: | Please state →
Array kWp, min 20 % of diesel generator set max output which is 150 kVA/120kW, hence = 24.0kWp min. | Comply and state→ | Yes / No
PV panels, total surface covering, m2 | Please state →
Nominal power output each panel, kWp | Please state →
Isc array, A (Amp) | Please state →
Certifications: Any one or more of IEC61215, UL1703 or equivalent | Comply and state → | Yes / No
Charge controller
Make and model: | Please state →
Type: MTTP | Comply and state → | Yes / No
Certifications. Any one or more of EN60730-1/2-11, 55022, 61000-4-27374/5/6 or equivalent | Comply and state→ | Yes / No
Capacity: Isc array +20%, min. | Comply and state→ | Yes / No
Inverter
Make and model: | Please state →
Capacity, A (Amp): Min. equivalent to max load | Comply and state→ | Yes / No
Pure sine curve | Comply and state → | Yes / No
Certifications: Any one or more of EN50178, 62040, 60950, 61000-2/3/6, EN60529, 50438 or equivalent | Comply and state → | Yes / No
Battery package
Make and model: | Please state →
Capacity: Min. equivalent to hybrid diesel gen set full load - 24 kW - for 1 hour = 120kWh. | Comply and state→ | Yes / No
Battery type: LiFePo4 | Comply and state→ | Yes / No
Certifications,: Any one or more of UL1642, IEC62133, 61000-6-3 or equivalent | Comply and state→ | Yes / No
PV panel racks, brackets, cables, fittings etc.
PV panels racks for sloped roof mount included for all included PV panels, if not attached to the Hybrid Gen set system itself (permanently or fold-out system etc). | Comply and state→ | Yes / No
All cables, junctions, contacts, breakers, earthing spears, fittings, screws, nut and bots etc included | Comply and state → | Yes / No
Installation
The system must be plug and play. Inverter, charge controller, battery package, battery charger must be pre-installed and wired either inside one common Hybrid system cage or in a separate cabinet, in order to easily connect the PV array and the local installation. All cables for establishing the PV array must be readily available with pre-installed connections and clearly marked in a way that no mistakes can occur. | Comply and state → | Yes / No
Other
Lifting points for handling | Comply and state → | Yes / No
Installation instructions, drawings, photos, brochures etc. English/French/Spanish | Comply and state → | Yes / No
Operators and maintenance manual, English/French/Spanish | Comply and state → | Yes / No
Tool kit | Comply and state → | Yes / No
Basic maintenance kit, engine: Min. 4 x oil filters, 2 x air filters, 2 x fuel filters | Comply and state → | Yes / No
Dimensions, L x W x H, mm | Please state →
Weight, dry, entire hybrid system incl. Battery package and all PV panels, cables, brackets etc etc.: kg: | Please state →
WARRANTY
Diesel Generator set: 2 years/2500 hours of operation which ever occur first. PV panels: Min. 10 years. Min. 90% performance guarantee at 10 years. Min. 80% performance guarantee at 20 years. Battery package: Min. 5 years. Inverter/charge controller/charger: Min. 4 years. Other equipment: Min. 2 years | Comply and state → | Yes / No
Sustainability
The bidder must demonstrate that its organisation has an environmental management system in place which as a minimum shall submit at least one or more of the following : the environmental policy principles of the organisation; the management measures and procedures taken or that will be taken to assess, monitor, measure and mitigate environmental impacts of the business processes/products associated with the execution of the contract; how attention is paid to the awareness and training/competency of employee(s) and supplier(s) with regard to dealing with the environmental aspects relevant to this bid; and that compliance with the environmental legislation applicable to the required performance(s) is guaranteed, ISO 14001 certificate, EMAS or an equivalent certificate | Comply and state → | Yes / No
The bidder shall provide documentation which outlines their approach to ensuring equal opportunity, diversity and inclusion within their organisation (e.g. equal pay policy, parental leave, ratio of females/males employees, % of female in management positions, grievances disaggregated by gender, transparency of promotion criteria, sexual harassment policies) | Comply and state → | Yes / No
Mandatory Options
Diesel engine spare parts & maintenance kit for min. 2500 hours of operation | Mandatory | enter prices on Form C: Price Schedule
Sound insolating and water proof canopy (max. 70 dB(A) at 7 m) | Mandatory | enter prices on Form C: Price Schedule
Work shop manual | Mandatory | enter prices on Form C: Price Schedule
Spare parts catalogue | Mandatory | enter prices on Form C: Price Schedule
60 Hz version of Generator set, please enter any surcharge to the std 50 Hz version offered above | Mandatory | enter prices on Form C: Price Schedule
Suggested Options
Heavy duty air filter for dusty conditions | Please provide price or state STD→ | Submit other option prices on a separate form
Heavy duty fuel filter/additional fuel filter in line with original | Please provide price or state STD→ | Submit other option prices on a separate form
Additional silencer, state dB(A) at 1 m and/or 7 m | Please provide price or state STD→ | Submit other option prices on a separate form
High chimney for exhaust, state height and materials | Please provide price or state STD→ | Submit other option prices on a separate form
(ATS) Automatic Transfer Switch | Please provide price or state STD→ | Submit other option prices on a separate form
Over speed protection | Please provide price or state STD→ | Submit other option prices on a separate form
Manual transfer switch | Please provide price or state STD→ | Submit other option prices on a separate form
External fuel tank with pipes including min.. 10 meter non-corrosive material and fittings, state volume of tank and material | Please provide price or state STD→ | Submit other option prices on a separate form
Slow moving trolley/trailer | Please provide price or state STD→ | Submit other option prices on a separate form
(AMF) Automatic Mains Failure Power generation set | Please provide price or state STD→ | Submit other option prices on a separate form
Automatic main circuit breaker | Please provide price or state STD→ | Submit other option prices on a separate form
Installation instructions and eventual. drawings, other languages | Please provide price or state STD→ | Submit other option prices on a separate form
Change over switch positions for: 1) Mains 2) Off 3) GENERATOR SET | Please provide price or state STD→ | Submit other option prices on a separate form
Automatic main circuit breaker | Please provide price or state STD→ | Submit other option prices on a separate form
Operators and maintenance manual, other languages | Please provide price or state STD→ | Submit other option prices on a separate form

## Lot 27 150 kVA PV 40% Roof
Bidder name:
Make and model:
Lot 27 150 kVA PV 40% Sloped Roof or Gen set mount.
HYBRID PV SOLAR/DIESEL GENERATOR SET SPECS | UNOPS REQUIREMENTS | Bidder: Compliant/Non-compliant to UNOPS requirements? Please mark YES/NO in this coloumn. Not indicating YES/NO in this column may render your bid non-compliant. | Bidders are required to provide information in this column on the specifications of their bid to demonstrate compliance to set specifications. Not providing specifications under this column may render your bid non-compliant.
Complete Hybrid PV solar/diesel generator set for autonomous operation, including PV solar power array, battery package, inverter and charge controller. Diesel engine, alternator, control panel with monitoring gauges/indicators, starting equipment, fuel tank as well as other accessories. Charger to charge battery package by diesel gen set and PV solar system interface between diesel gen set and PV solar power unit for a smooth operation for the two energy sources in conjunction, automatically without any manual intervention. Factory test certificates must be included and must be in accordance to internationally recognised standards. Suitable for tropical conditions. | Comply and state → | Yes / No
KEY DATA
Make | Please state →
Model | Please state →
Country of origin | Please state →
DIESEL GEN SET
Rated power output, min. 150 kVA | Comply and state → | Yes / No
Power factor: 0.8 | Comply and state → | Yes / No
Rated power output, 120 kW, min. | Comply and state → | Yes / No
Voltage, 220/230/240 and 380/400 V | Comply and state → | Yes / No
Phase: 1 and 3 | Comply and state → | Yes / No
AC frequency, 50/60 Hz | Comply and state → | Yes / No
Speed: rpm 1500 or 3000 or other | Please state →
Prime power according to ISO 8528 or equivalent, i.e. power available at variable load with no limitations on hours of operation and capable of min. 10% overload for min. 1 hour in any 12 hours. | Comply and state → | Yes / No
Prime rating of min. the stated output rating at Normal Temperature and Pressure conditions (NTP). Please state | Comply and state → | Yes / No
Derating information (temperature, altitude and humidity), please state | Please state →
Engine
Make | Please state →
Model | Please state →
Engine power output, kW at rpm: | Please state →
Fuel: Diesel | Comply and state → | Yes / No
Cooling, liquid or air or combined, suitable for tropical conditions | Please state →
Speed governor, state type | Please state →
Exhaust with suitable piping and residential silencer | Comply and state → | Yes / No
Noise level, dB(A) at 1 m (silencer fitted) | Please state →
Fuel consumption at 75% load: L/hour | Please state →
CO2 emissions at 75% load: g/hour | Please state →
Mounted on anti-vibration mounts | Comply and state → | Yes / No
ENVIRONMENTAL
EU Non-road emissions regulations schedule, e.g. EU STAGE II, III A, III B, IV. US Non-road and stationary emissions regulations to Tier 1,2,3,4 or equivalent. Please state. | Comply and state → | Yes / No
Alternator
Make: | Please state →
Model: | Please state →
Brushless type | Comply and state → | Yes / No
Cooling, liquid, air, other | Please state →
Protection class min. IP 23 | Comply and state → | Yes / No
Suitable AC power outlets protected by circuit breaker (state type) | Comply and state → | Yes / No
Insulation to min. IEC 60085 - >155 ° C - (F) or equivalent | Comply and state → | Yes / No
Voltage regulator | Comply and state → | Yes / No
Standard accessories
Fuel tank. Integrated or separate, suitable for continuous operation of min. 8 hours at rated capacity. State capacity, litres. Fuel level gauge. Including all necessary pipework, connections etc. Possibility for connection to external tank. | Comply and state→ | Yes / No
Low oil pressure protection, automatic shut down | Comply and state → | Yes / No
Over heating protection | Comply and state → | Yes / No
Overload protection | Comply and state → | Yes / No
Emergency stop | Comply and state → | Yes / No
Electric starter with key and battery | Comply and state → | Yes / No
Min. Voltmeter, ammeter, hour meter, Hz meter, water temp gauge/indicator (where applicable) | Comply and state → | Yes / No
Earthing/grounding facility | Comply and state → | Yes / No
PV SOLAR POWER SYSTEM STANDARD ARRAY NOMINAL MIN.48.0 kWp. Battery pack 120 kWh. For Sloped Roof or Gen set mount.
PV solar array
Make and model: | Please state →
Array kWp, min 40 % of diesel generator set max output which is 150 kVA/120kW, hence = 48.0kWp min. | Comply and state→ | Yes / No
PV panels, total surface covering, m2 | Please state →
Nominal power output each panel, kWp | Please state →
Isc array, A (Amp) | Please state →
Certifications: Any one or more of IEC61215, UL1703 or equivalent | Comply and state → | Yes / No
Charge controller
Make and model: | Please state →
Type: MTTP | Comply and state → | Yes / No
Certifications. Any one or more of EN60730-1/2-11, 55022, 61000-4-27374/5/6 or equivalent | Comply and state→ | Yes / No
Capacity: Isc array +20%, min. | Comply and state→ | Yes / No
Inverter
Make and model: | Please state →
Capacity, A (Amp): Min. equivalent to max load | Comply and state→ | Yes / No
Pure sine curve | Comply and state → | Yes / No
Certifications: Any one or more of EN50178, 62040, 60950, 61000-2/3/6, EN60529, 50438 or equivalent | Comply and state → | Yes / No
Battery package
Make and model: | Please state →
Capacity: Min. equivalent to hybrid diesel gen set full load - 24 kW - for 1 hour = 120kWh. | Comply and state→ | Yes / No
Battery type: LiFePo4 | Comply and state→ | Yes / No
Certifications,: Any one or more of UL1642, IEC62133, 61000-6-3 or equivalent | Comply and state→ | Yes / No
PV panel racks, brackets, cables, fittings etc.
PV panels racks for sloped roof mount included for all included PV panels, if not attached to the Hybrid Gen set system itself (permanently or fold-out system etc). | Comply and state→ | Yes / No
All cables, junctions, contacts, breakers, earthing spears, fittings, screws, nut and bots etc included | Comply and state → | Yes / No
Installation
The system must be plug and play. Inverter, charge controller, battery package, battery charger must be pre-installed and wired either inside one common Hybrid system cage or in a separate cabinet, in order to easily connect the PV array and the local installation. All cables for establishing the PV array must be readily available with pre-installed connections and clearly marked in a way that no mistakes can occur. | Comply and state → | Yes / No
Other
Lifting points for handling | Comply and state → | Yes / No
Installation instructions, drawings, photos, brochures etc. English/French/Spanish | Comply and state → | Yes / No
Operators and maintenance manual, English/French/Spanish | Comply and state → | Yes / No
Tool kit | Comply and state → | Yes / No
Basic maintenance kit, engine: Min. 4 x oil filters, 2 x air filters, 2 x fuel filters | Comply and state → | Yes / No
Dimensions, L x W x H, mm | Please state →
Weight, dry, entire hybrid system incl. Battery package and all PV panels, cables, brackets etc etc.: kg: | Please state →
WARRANTY
Diesel Generator set: 2 years/2500 hours of operation which ever occur first. PV panels: Min. 10 years. Min. 90% performance guarantee at 10 years. Min. 80% performance guarantee at 20 years. Battery package: Min. 5 years. Inverter/charge controller/charger: Min. 4 years. Other equipment: Min. 2 years | Comply and state → | Yes / No
Sustainability
The bidder must demonstrate that its organisation has an environmental management system in place which as a minimum shall submit at least one or more of the following : the environmental policy principles of the organisation; the management measures and procedures taken or that will be taken to assess, monitor, measure and mitigate environmental impacts of the business processes/products associated with the execution of the contract; how attention is paid to the awareness and training/competency of employee(s) and supplier(s) with regard to dealing with the environmental aspects relevant to this bid; and that compliance with the environmental legislation applicable to the required performance(s) is guaranteed, ISO 14001 certificate, EMAS or an equivalent certificate | Comply and state → | Yes / No
The bidder shall provide documentation which outlines their approach to ensuring equal opportunity, diversity and inclusion within their organisation (e.g. equal pay policy, parental leave, ratio of females/males employees, % of female in management positions, grievances disaggregated by gender, transparency of promotion criteria, sexual harassment policies) | Comply and state → | Yes / No
Mandatory Options
Diesel engine spare parts & maintenance kit for min. 2500 hours of operation | Mandatory | enter prices on Form C: Price Schedule
Sound insolating and water proof canopy (max. 70 dB(A) at 7 m) | Mandatory | enter prices on Form C: Price Schedule
Work shop manual | Mandatory | enter prices on Form C: Price Schedule
Spare parts catalogue | Mandatory | enter prices on Form C: Price Schedule
60 Hz version of Generator set, please enter any surcharge to the std 50 Hz version offered above | Mandatory | enter prices on Form C: Price Schedule
Suggested Options
Heavy duty air filter for dusty conditions | Please provide price or state STD→ | Submit other option prices on a separate form
Heavy duty fuel filter/additional fuel filter in line with original | Please provide price or state STD→ | Submit other option prices on a separate form
Additional silencer, state dB(A) at 1 m and/or 7 m | Please provide price or state STD→ | Submit other option prices on a separate form
High chimney for exhaust, state height and materials | Please provide price or state STD→ | Submit other option prices on a separate form
(ATS) Automatic Transfer Switch | Please provide price or state STD→ | Submit other option prices on a separate form
Over speed protection | Please provide price or state STD→ | Submit other option prices on a separate form
Manual transfer switch | Please provide price or state STD→ | Submit other option prices on a separate form
External fuel tank with pipes including min.. 10 meter non-corrosive material and fittings, state volume of tank and material | Please provide price or state STD→ | Submit other option prices on a separate form
Slow moving trolley/trailer | Please provide price or state STD→ | Submit other option prices on a separate form
(AMF) Automatic Mains Failure Power generation set | Please provide price or state STD→ | Submit other option prices on a separate form
Automatic main circuit breaker | Please provide price or state STD→ | Submit other option prices on a separate form
Installation instructions and eventual. drawings, other languages | Please provide price or state STD→ | Submit other option prices on a separate form
Change over switch positions for: 1) Mains 2) Off 3) GENERATOR SET | Please provide price or state STD→ | Submit other option prices on a separate form
Automatic main circuit breaker | Please provide price or state STD→ | Submit other option prices on a separate form
Operators and maintenance manual, other languages | Please provide price or state STD→ | Submit other option prices on a separate form

## Lot 28 150 kVA PV 10% Ground
Bidder name:
Make and model:
Lot 28. 150 kVA PV 10% Ground or flat roof mounted
HYBRID PV SOLAR/DIESEL GENERATOR SET SPECS | UNOPS REQUIREMENTS | Bidder: Compliant/Non-compliant to UNOPS requirements? Please mark YES/NO in this coloumn. Not indicating YES/NO in this column may render your bid non-compliant. | Bidders are required to provide information in this column on the specifications of their bid to demonstrate compliance to set specifications. Not providing specifications under this column may render your bid non-compliant.
Complete Hybrid PV solar/diesel generator set for autonomous operation, including PV solar power array, battery package, inverter and charge controller. Diesel engine, alternator, control panel with monitoring gauges/indicators, starting equipment, fuel tank as well as other accessories. Charger to charge battery package by diesel gen set and PV solar system interface between diesel gen set and PV solar power unit for a smooth operation for the two energy sources in conjunction, automatically without any manual intervention. Factory test certificates must be included and must be in accordance to internationally recognised standards. Suitable for tropical conditions. | Comply and state → | Yes / No
KEY DATA
Make | Please state →
Model | Please state →
Country of origin | Please state →
DIESEL GEN SET
Rated power output, min. 150 kVA | Comply and state → | Yes / No
Power factor: 0.8 | Comply and state → | Yes / No
Rated power output, 120 kW, min. | Comply and state → | Yes / No
Voltage, 220/230/240 and 380/400 V | Comply and state → | Yes / No
Phase: 1 and 3 | Comply and state → | Yes / No
AC frequency, 50/60 Hz | Comply and state → | Yes / No
Speed: rpm 1500 or 3000 or other | Please state →
Prime power according to ISO 8528 or equivalent, i.e. power available at variable load with no limitations on hours of operation and capable of min. 10% overload for min. 1 hour in any 12 hours. | Comply and state → | Yes / No
Prime rating of min. the stated output rating at Normal Temperature and Pressure conditions (NTP). Please state | Comply and state → | Yes / No
Derating information (temperature, altitude and humidity), please state | Please state →
Engine
Make | Please state →
Model | Please state →
Engine power output, kW at rpm: | Please state →
Fuel: Diesel | Comply and state → | Yes / No
Cooling, liquid or air or combined, suitable for tropical conditions | Please state →
Speed governor, state type | Please state →
Exhaust with suitable piping and residential silencer | Comply and state → | Yes / No
Noise level, dB(A) at 1 m (silencer fitted) | Please state →
Fuel consumption at 75% load: L/hour | Please state →
CO2 emissions at 75% load: g/hour | Please state →
Mounted on anti-vibration mounts | Comply and state → | Yes / No
ENVIRONMENTAL
EU Non-road emissions regulations schedule, e.g. EU STAGE II, III A, III B, IV. US Non-road and stationary emissions regulations to Tier 1,2,3,4 or equivalent. Please state. | Comply and state → | Yes / No
Alternator
Make: | Please state →
Model: | Please state →
Brushless type | Comply and state → | Yes / No
Cooling, liquid, air, other | Please state →
Protection class min. IP 23 | Comply and state → | Yes / No
Suitable AC power outlets protected by circuit breaker (state type) | Comply and state → | Yes / No
Insulation to min. IEC 60085 - >155 ° C - (F) or equivalent | Comply and state → | Yes / No
Voltage regulator | Comply and state → | Yes / No
Standard accessories
Fuel tank. Integrated or separate, suitable for continuous operation of min. 8 hours at rated capacity. State capacity, litres. Fuel level gauge. Including all necessary pipework, connections etc. Possibility for connection to external tank. | Comply and state→ | Yes / No
Low oil pressure protection, automatic shut down | Comply and state → | Yes / No
Over heating protection | Comply and state → | Yes / No
Overload protection | Comply and state → | Yes / No
Emergency stop | Comply and state → | Yes / No
Electric starter with key and battery | Comply and state → | Yes / No
Min. Voltmeter, ammeter, hour meter, Hz meter, water temp gauge/indicator (where applicable) | Comply and state → | Yes / No
Earthing/grounding facility | Comply and state → | Yes / No
PV SOLAR POWER SYSTEM STANDARD ARRAY NOMINAL MIN. 12.0 kWp. Battery pack 120 kWh. For Ground or flat roof mount
PV solar array
Make and model: | Please state →
Array kWp, min 10% of diesel generator set max output which is 150kVA/120kW, hence = 12.0kWp min. | Comply and state→ | Yes / No
PV panels, total surface covering, m2 | Please state →
Nominal power output each panel, kWp | Please state →
Isc array, A (Amp) | Please state →
Certifications: Any one or more of IEC61215, UL1703 or equivalent | Comply and state → | Yes / No
Charge controller
Make and model: | Please state →
Type: MTTP | Comply and state → | Yes / No
Certifications. Any one or more of EN60730-1/2-11, 55022, 61000-4-27374/5/6 or equivalent | Comply and state→ | Yes / No
Capacity: Isc array +20%, min. | Comply and state→ | Yes / No
Inverter
Make and model: | Please state →
Capacity, A (Amp): Min. equivalent to max load | Comply and state→ | Yes / No
Pure sine curve | Comply and state → | Yes / No
Certifications: Any one or more of EN50178, 62040, 60950, 61000-2/3/6, EN60529, 50438 or equivalent | Comply and state → | Yes / No
Battery package
Make and model: | Please state →
Capacity: Min. equivalent to hybrid diesel gen set full load - 24 kW - for 1 hour = 120 kWh. | Comply and state→ | Yes / No
Battery type: LiFePo4 | Comply and state→ | Yes / No
Certifications,: Any one or more of UL1642, IEC62133, 61000-6-3 or equivalent | Comply and state→ | Yes / No
PV panel racks, brackets, cables, fittings etc.
PV panels racks for Ground or flat roof mount. | Comply and state→ | Yes / No
All cables, junctions, contacts, breakers, earthing spears, fittings, screws, nut and bots etc included | Comply and state → | Yes / No
Installation
The system must be plug and play. Inverter, charge controller, battery package, battery charger must be pre-installed and wired either inside one common Hybrid system cage or in a separate cabinet, in order to easily connect the PV array and the local installation. All cables for establishing the PV array must be readily available with pre-installed connections and clearly marked in a way that no mistakes can occur. | Comply and state → | Yes / No
Other
Lifting points for handling | Comply and state → | Yes / No
Installation instructions, drawings, photos, brochures etc. English/French/Spanish | Comply and state → | Yes / No
Operators and maintenance manual, English/French/Spanish | Comply and state → | Yes / No
Tool kit | Comply and state → | Yes / No
Basic maintenance kit, engine: Min. 4 x oil filters, 2 x air filters, 2 x fuel filters | Comply and state → | Yes / No
Dimensions, L x W x H, mm | Please state →
Weight, dry, entire hybrid system incl. Battery package and all PV panels, cables, brackets etc etc.: kg: | Please state →
WARRANTY
Diesel Generator set: 2 years/2500 hours of operation which ever occur first. PV panels: Min. 10 years. Min. 90% performance guarantee at 10 years. Min. 80% performance guarantee at 20 years. Battery package: Min. 5 years. Inverter/charge controller/charger: Min. 4 years. Other equipment: Min. 2 years | Comply and state → | Yes / No
Sustainability
The bidder must demonstrate that its organisation has an environmental management system in place which as a minimum shall submit at least one or more of the following : the environmental policy principles of the organisation; the management measures and procedures taken or that will be taken to assess, monitor, measure and mitigate environmental impacts of the business processes/products associated with the execution of the contract; how attention is paid to the awareness and training/competency of employee(s) and supplier(s) with regard to dealing with the environmental aspects relevant to this bid; and that compliance with the environmental legislation applicable to the required performance(s) is guaranteed, ISO 14001 certificate, EMAS or an equivalent certificate | Comply and state → | Yes / No
The bidder shall provide documentation which outlines their approach to ensuring equal opportunity, diversity and inclusion within their organisation (e.g. equal pay policy, parental leave, ratio of females/males employees, % of female in management positions, grievances disaggregated by gender, transparency of promotion criteria, sexual harassment policies) | Comply and state → | Yes / No
Mandatory Options
Diesel engine spare parts & maintenance kit for min. 2500 hours of operation | Mandatory | enter prices on Form C: Price Schedule
Sound insolating and water proof canopy (max. 70 dB(A) at 7 m) | Mandatory | enter prices on Form C: Price Schedule
Work shop manual | Mandatory | enter prices on Form C: Price Schedule
Spare parts catalogue | Mandatory | enter prices on Form C: Price Schedule
60 Hz version of Generator set, please enter any surcharge to the std 50 Hz version offered above | Mandatory | enter prices on Form C: Price Schedule
Suggested Options
Heavy duty air filter for dusty conditions | Please provide price or state STD→ | Submit other option prices on a separate form
Heavy duty fuel filter/additional fuel filter in line with original | Please provide price or state STD→ | Submit other option prices on a separate form
Additional silencer, state dB(A) at 1 m and/or 7 m | Please provide price or state STD→ | Submit other option prices on a separate form
High chimney for exhaust, state height and materials | Please provide price or state STD→ | Submit other option prices on a separate form
(ATS) Automatic Transfer Switch | Please provide price or state STD→ | Submit other option prices on a separate form
Over speed protection | Please provide price or state STD→ | Submit other option prices on a separate form
Manual transfer switch | Please provide price or state STD→ | Submit other option prices on a separate form
External fuel tank with pipes including min.. 10 meter non-corrosive material and fittings, state volume of tank and material | Please provide price or state STD→ | Submit other option prices on a separate form
Slow moving trolley/trailer | Please provide price or state STD→ | Submit other option prices on a separate form
(AMF) Automatic Mains Failure Power generation set | Please provide price or state STD→ | Submit other option prices on a separate form
Automatic main circuit breaker | Please provide price or state STD→ | Submit other option prices on a separate form
Installation instructions and eventual. drawings, other languages | Please provide price or state STD→ | Submit other option prices on a separate form
Change over switch positions for: 1) Mains 2) Off 3) GENERATOR SET | Please provide price or state STD→ | Submit other option prices on a separate form
Automatic main circuit breaker | Please provide price or state STD→ | Submit other option prices on a separate form
Operators and maintenance manual, other languages | Please provide price or state STD→ | Submit other option prices on a separate form

## Lot 29 150 kVA PV 20% Ground
Bidder name:
Make and model:
Lot 29. 150 kVA PV 20% Ground or flat roof mounted
HYBRID PV SOLAR/DIESEL GENERATOR SET SPECS | UNOPS REQUIREMENTS | Bidder: Compliant/Non-compliant to UNOPS requirements? Please mark YES/NO in this coloumn. Not indicating YES/NO in this column may render your bid non-compliant. | Bidders are required to provide information in this column on the specifications of their bid to demonstrate compliance to set specifications. Not providing specifications under this column may render your bid non-compliant.
Complete Hybrid PV solar/diesel generator set for autonomous operation, including PV solar power array, battery package, inverter and charge controller. Diesel engine, alternator, control panel with monitoring gauges/indicators, starting equipment, fuel tank as well as other accessories. Charger to charge battery package by diesel gen set and PV solar system interface between diesel gen set and PV solar power unit for a smooth operation for the two energy sources in conjunction, automatically without any manual intervention. Factory test certificates must be included and must be in accordance to internationally recognised standards. Suitable for tropical conditions. | Comply and state → | Yes / No
KEY DATA
Make | Please state →
Model | Please state →
Country of origin | Please state →
DIESEL GEN SET
Rated power output, min. 150 kVA | Comply and state → | Yes / No
Power factor: 0.8 | Comply and state → | Yes / No
Rated power output, 120 kW, min. | Comply and state → | Yes / No
Voltage, 220/230/240 and 380/400 V | Comply and state → | Yes / No
Phase: 1 and 3 | Comply and state → | Yes / No
AC frequency, 50/60 Hz | Comply and state → | Yes / No
Speed: rpm 1500 or 3000 or other | Please state →
Prime power according to ISO 8528 or equivalent, i.e. power available at variable load with no limitations on hours of operation and capable of min. 10% overload for min. 1 hour in any 12 hours. | Comply and state → | Yes / No
Prime rating of min. the stated output rating at Normal Temperature and Pressure conditions (NTP). Please state | Comply and state → | Yes / No
Derating information (temperature, altitude and humidity), please state | Please state →
Engine
Make | Please state →
Model | Please state →
Engine power output, kW at rpm: | Please state →
Fuel: Diesel | Comply and state → | Yes / No
Cooling, liquid or air or combined, suitable for tropical conditions | Please state →
Speed governor, state type | Please state →
Exhaust with suitable piping and residential silencer | Comply and state → | Yes / No
Noise level, dB(A) at 1 m (silencer fitted) | Please state →
Fuel consumption at 75% load: L/hour | Please state →
CO2 emissions at 75% load: g/hour | Please state →
Mounted on anti-vibration mounts | Comply and state → | Yes / No
ENVIRONMENTAL
EU Non-road emissions regulations schedule, e.g. EU STAGE II, III A, III B, IV. US Non-road and stationary emissions regulations to Tier 1,2,3,4 or equivalent. Please state. | Comply and state → | Yes / No
Alternator
Make: | Please state →
Model: | Please state →
Brushless type | Comply and state → | Yes / No
Cooling, liquid, air, other | Please state →
Protection class min. IP 23 | Comply and state → | Yes / No
Suitable AC power outlets protected by circuit breaker (state type) | Comply and state → | Yes / No
Insulation to min. IEC 60085 - >155 ° C - (F) or equivalent | Comply and state → | Yes / No
Voltage regulator | Comply and state → | Yes / No
Standard accessories
Fuel tank. Integrated or separate, suitable for continuous operation of min. 8 hours at rated capacity. State capacity, litres. Fuel level gauge. Including all necessary pipework, connections etc. Possibility for connection to external tank. | Comply and state→ | Yes / No
Low oil pressure protection, automatic shut down | Comply and state → | Yes / No
Over heating protection | Comply and state → | Yes / No
Overload protection | Comply and state → | Yes / No
Emergency stop | Comply and state → | Yes / No
Electric starter with key and battery | Comply and state → | Yes / No
Min. Voltmeter, ammeter, hour meter, Hz meter, water temp gauge/indicator (where applicable) | Comply and state → | Yes / No
Earthing/grounding facility | Comply and state → | Yes / No
PV SOLAR POWER SYSTEM STANDARD ARRAY NOMINAL MIN. 24.0 kWp. Battery pack 120 kWh. For Ground or flat roof mount
PV solar array
Make and model: | Please state →
Array kWp, min 20% of diesel generator set max output which is 150kVA/120kW, hence = 24.0kWp min. | Comply and state→ | Yes / No
PV panels, total surface covering, m2 | Please state →
Nominal power output each panel, kWp | Please state →
Isc array, A (Amp) | Please state →
Certifications: Any one or more of IEC61215, UL1703 or equivalent | Comply and state → | Yes / No
Charge controller
Make and model: | Please state →
Type: MTTP | Comply and state → | Yes / No
Certifications. Any one or more of EN60730-1/2-11, 55022, 61000-4-27374/5/6 or equivalent | Comply and state→ | Yes / No
Capacity: Isc array +20%, min. | Comply and state→ | Yes / No
Inverter
Make and model: | Please state →
Capacity, A (Amp): Min. equivalent to max load | Comply and state→ | Yes / No
Pure sine curve | Comply and state → | Yes / No
Certifications: Any one or more of EN50178, 62040, 60950, 61000-2/3/6, EN60529, 50438 or equivalent | Comply and state → | Yes / No
Battery package
Make and model: | Please state →
Capacity: Min. equivalent to hybrid diesel gen set full load - 24 kW - for 1 hour = 120 kWh. | Comply and state→ | Yes / No
Battery type: LiFePo4 | Comply and state→ | Yes / No
Certifications,: Any one or more of UL1642, IEC62133, 61000-6-3 or equivalent | Comply and state→ | Yes / No
PV panel racks, brackets, cables, fittings etc.
PV panels racks for Ground or flat roof mount. | Comply and state→ | Yes / No
All cables, junctions, contacts, breakers, earthing spears, fittings, screws, nut and bots etc included | Comply and state → | Yes / No
Installation
The system must be plug and play. Inverter, charge controller, battery package, battery charger must be pre-installed and wired either inside one common Hybrid system cage or in a separate cabinet, in order to easily connect the PV array and the local installation. All cables for establishing the PV array must be readily available with pre-installed connections and clearly marked in a way that no mistakes can occur. | Comply and state → | Yes / No
Other
Lifting points for handling | Comply and state → | Yes / No
Installation instructions, drawings, photos, brochures etc. English/French/Spanish | Comply and state → | Yes / No
Operators and maintenance manual, English/French/Spanish | Comply and state → | Yes / No
Tool kit | Comply and state → | Yes / No
Basic maintenance kit, engine: Min. 4 x oil filters, 2 x air filters, 2 x fuel filters | Comply and state → | Yes / No
Dimensions, L x W x H, mm | Please state →
Weight, dry, entire hybrid system incl. Battery package and all PV panels, cables, brackets etc etc.: kg: | Please state →
WARRANTY
Diesel Generator set: 2 years/2500 hours of operation which ever occur first. PV panels: Min. 10 years. Min. 90% performance guarantee at 10 years. Min. 80% performance guarantee at 20 years. Battery package: Min. 5 years. Inverter/charge controller/charger: Min. 4 years. Other equipment: Min. 2 years | Comply and state → | Yes / No
Sustainability
The bidder must demonstrate that its organisation has an environmental management system in place which as a minimum shall submit at least one or more of the following : the environmental policy principles of the organisation; the management measures and procedures taken or that will be taken to assess, monitor, measure and mitigate environmental impacts of the business processes/products associated with the execution of the contract; how attention is paid to the awareness and training/competency of employee(s) and supplier(s) with regard to dealing with the environmental aspects relevant to this bid; and that compliance with the environmental legislation applicable to the required performance(s) is guaranteed, ISO 14001 certificate, EMAS or an equivalent certificate | Comply and state → | Yes / No
The bidder shall provide documentation which outlines their approach to ensuring equal opportunity, diversity and inclusion within their organisation (e.g. equal pay policy, parental leave, ratio of females/males employees, % of female in management positions, grievances disaggregated by gender, transparency of promotion criteria, sexual harassment policies) | Comply and state → | Yes / No
Mandatory Options
Diesel engine spare parts & maintenance kit for min. 2500 hours of operation | Mandatory | enter prices on Form C: Price Schedule
Sound insolating and water proof canopy (max. 70 dB(A) at 7 m) | Mandatory | enter prices on Form C: Price Schedule
Work shop manual | Mandatory | enter prices on Form C: Price Schedule
Spare parts catalogue | Mandatory | enter prices on Form C: Price Schedule
60 Hz version of Generator set, please enter any surcharge to the std 50 Hz version offered above | Mandatory | enter prices on Form C: Price Schedule
Suggested Options
Heavy duty air filter for dusty conditions | Please provide price or state STD→ | Submit other option prices on a separate form
Heavy duty fuel filter/additional fuel filter in line with original | Please provide price or state STD→ | Submit other option prices on a separate form
Additional silencer, state dB(A) at 1 m and/or 7 m | Please provide price or state STD→ | Submit other option prices on a separate form
High chimney for exhaust, state height and materials | Please provide price or state STD→ | Submit other option prices on a separate form
(ATS) Automatic Transfer Switch | Please provide price or state STD→ | Submit other option prices on a separate form
Over speed protection | Please provide price or state STD→ | Submit other option prices on a separate form
Manual transfer switch | Please provide price or state STD→ | Submit other option prices on a separate form
External fuel tank with pipes including min.. 10 meter non-corrosive material and fittings, state volume of tank and material | Please provide price or state STD→ | Submit other option prices on a separate form
Slow moving trolley/trailer | Please provide price or state STD→ | Submit other option prices on a separate form
(AMF) Automatic Mains Failure Power generation set | Please provide price or state STD→ | Submit other option prices on a separate form
Automatic main circuit breaker | Please provide price or state STD→ | Submit other option prices on a separate form
Installation instructions and eventual. drawings, other languages | Please provide price or state STD→ | Submit other option prices on a separate form
Change over switch positions for: 1) Mains 2) Off 3) GENERATOR SET | Please provide price or state STD→ | Submit other option prices on a separate form
Automatic main circuit breaker | Please provide price or state STD→ | Submit other option prices on a separate form
Operators and maintenance manual, other languages | Please provide price or state STD→ | Submit other option prices on a separate form

## Lot 30 150 kVA PV 40% Ground
Bidder name:
Make and model:
Lot 30. 150 kVA PV 40% Ground or flat roof mounted
HYBRID PV SOLAR/DIESEL GENERATOR SET SPECS | UNOPS REQUIREMENTS | Bidder: Compliant/Non-compliant to UNOPS requirements? Please mark YES/NO in this coloumn. Not indicating YES/NO in this column may render your bid non-compliant. | Bidders are required to provide information in this column on the specifications of their bid to demonstrate compliance to set specifications. Not providing specifications under this column may render your bid non-compliant.
Complete Hybrid PV solar/diesel generator set for autonomous operation, including PV solar power array, battery package, inverter and charge controller. Diesel engine, alternator, control panel with monitoring gauges/indicators, starting equipment, fuel tank as well as other accessories. Charger to charge battery package by diesel gen set and PV solar system interface between diesel gen set and PV solar power unit for a smooth operation for the two energy sources in conjunction, automatically without any manual intervention. Factory test certificates must be included and must be in accordance to internationally recognised standards. Suitable for tropical conditions. | Comply and state → | Yes / No
KEY DATA
Make | Please state →
Model | Please state →
Country of origin | Please state →
DIESEL GEN SET
Rated power output, min. 150 kVA | Comply and state → | Yes / No
Power factor: 0.8 | Comply and state → | Yes / No
Rated power output, 120 kW, min. | Comply and state → | Yes / No
Voltage, 220/230/240 and 380/400 V | Comply and state → | Yes / No
Phase: 1 and 3 | Comply and state → | Yes / No
AC frequency, 50/60 Hz | Comply and state → | Yes / No
Speed: rpm 1500 or 3000 or other | Please state →
Prime power according to ISO 8528 or equivalent, i.e. power available at variable load with no limitations on hours of operation and capable of min. 10% overload for min. 1 hour in any 12 hours. | Comply and state → | Yes / No
Prime rating of min. the stated output rating at Normal Temperature and Pressure conditions (NTP). Please state | Comply and state → | Yes / No
Derating information (temperature, altitude and humidity), please state | Please state →
Engine
Make | Please state →
Model | Please state →
Engine power output, kW at rpm: | Please state →
Fuel: Diesel | Comply and state → | Yes / No
Cooling, liquid or air or combined, suitable for tropical conditions | Please state →
Speed governor, state type | Please state →
Exhaust with suitable piping and residential silencer | Comply and state → | Yes / No
Noise level, dB(A) at 1 m (silencer fitted) | Please state →
Fuel consumption at 75% load: L/hour | Please state →
CO2 emissions at 75% load: g/hour | Please state →
Mounted on anti-vibration mounts | Comply and state → | Yes / No
ENVIRONMENTAL
EU Non-road emissions regulations schedule, e.g. EU STAGE II, III A, III B, IV. US Non-road and stationary emissions regulations to Tier 1,2,3,4 or equivalent. Please state. | Comply and state → | Yes / No
Alternator
Make: | Please state →
Model: | Please state →
Brushless type | Comply and state → | Yes / No
Cooling, liquid, air, other | Please state →
Protection class min. IP 23 | Comply and state → | Yes / No
Suitable AC power outlets protected by circuit breaker (state type) | Comply and state → | Yes / No
Insulation to min. IEC 60085 - >155 ° C - (F) or equivalent | Comply and state → | Yes / No
Voltage regulator | Comply and state → | Yes / No
Standard accessories
Fuel tank. Integrated or separate, suitable for continuous operation of min. 8 hours at rated capacity. State capacity, litres. Fuel level gauge. Including all necessary pipework, connections etc. Possibility for connection to external tank. | Comply and state→ | Yes / No
Low oil pressure protection, automatic shut down | Comply and state → | Yes / No
Over heating protection | Comply and state → | Yes / No
Overload protection | Comply and state → | Yes / No
Emergency stop | Comply and state → | Yes / No
Electric starter with key and battery | Comply and state → | Yes / No
Min. Voltmeter, ammeter, hour meter, Hz meter, water temp gauge/indicator (where applicable) | Comply and state → | Yes / No
Earthing/grounding facility | Comply and state → | Yes / No
PV SOLAR POWER SYSTEM STANDARD ARRAY NOMINAL MIN. 48.0 kWp. Battery pack 120 kWh. For Ground or flat roof mount
PV solar array
Make and model: | Please state →
Array kWp, min 40% of diesel generator set max output which is 150kVA/120kW, hence = 48.0kWp min. | Comply and state→ | Yes / No
PV panels, total surface covering, m2 | Please state →
Nominal power output each panel, kWp | Please state →
Isc array, A (Amp) | Please state →
Certifications: Any one or more of IEC61215, UL1703 or equivalent | Comply and state → | Yes / No
Charge controller
Make and model: | Please state →
Type: MTTP | Comply and state → | Yes / No
Certifications. Any one or more of EN60730-1/2-11, 55022, 61000-4-27374/5/6 or equivalent | Comply and state→ | Yes / No
Capacity: Isc array +20%, min. | Comply and state→ | Yes / No
Inverter
Make and model: | Please state →
Capacity, A (Amp): Min. equivalent to max load | Comply and state→ | Yes / No
Pure sine curve | Comply and state → | Yes / No
Certifications: Any one or more of EN50178, 62040, 60950, 61000-2/3/6, EN60529, 50438 or equivalent | Comply and state → | Yes / No
Battery package
Make and model: | Please state →
Capacity: Min. equivalent to hybrid diesel gen set full load - 24 kW - for 1 hour = 120 kWh. | Comply and state→ | Yes / No
Battery type: LiFePo4 | Comply and state→ | Yes / No
Certifications,: Any one or more of UL1642, IEC62133, 61000-6-3 or equivalent | Comply and state→ | Yes / No
PV panel racks, brackets, cables, fittings etc.
PV panels racks for Ground or flat roof mount. | Comply and state→ | Yes / No
All cables, junctions, contacts, breakers, earthing spears, fittings, screws, nut and bots etc included | Comply and state → | Yes / No
Installation
The system must be plug and play. Inverter, charge controller, battery package, battery charger must be pre-installed and wired either inside one common Hybrid system cage or in a separate cabinet, in order to easily connect the PV array and the local installation. All cables for establishing the PV array must be readily available with pre-installed connections and clearly marked in a way that no mistakes can occur. | Comply and state → | Yes / No
Other
Lifting points for handling | Comply and state → | Yes / No
Installation instructions, drawings, photos, brochures etc. English/French/Spanish | Comply and state → | Yes / No
Operators and maintenance manual, English/French/Spanish | Comply and state → | Yes / No
Tool kit | Comply and state → | Yes / No
Basic maintenance kit, engine: Min. 4 x oil filters, 2 x air filters, 2 x fuel filters | Comply and state → | Yes / No
Dimensions, L x W x H, mm | Please state →
Weight, dry, entire hybrid system incl. Battery package and all PV panels, cables, brackets etc etc.: kg: | Please state →
WARRANTY
Diesel Generator set: 2 years/2500 hours of operation which ever occur first. PV panels: Min. 10 years. Min. 90% performance guarantee at 10 years. Min. 80% performance guarantee at 20 years. Battery package: Min. 5 years. Inverter/charge controller/charger: Min. 4 years. Other equipment: Min. 2 years | Comply and state → | Yes / No
Sustainability
The bidder must demonstrate that its organisation has an environmental management system in place which as a minimum shall submit at least one or more of the following : the environmental policy principles of the organisation; the management measures and procedures taken or that will be taken to assess, monitor, measure and mitigate environmental impacts of the business processes/products associated with the execution of the contract; how attention is paid to the awareness and training/competency of employee(s) and supplier(s) with regard to dealing with the environmental aspects relevant to this bid; and that compliance with the environmental legislation applicable to the required performance(s) is guaranteed, ISO 14001 certificate, EMAS or an equivalent certificate | Comply and state → | Yes / No
The bidder shall provide documentation which outlines their approach to ensuring equal opportunity, diversity and inclusion within their organisation (e.g. equal pay policy, parental leave, ratio of females/males employees, % of female in management positions, grievances disaggregated by gender, transparency of promotion criteria, sexual harassment policies) | Comply and state → | Yes / No
Mandatory Options
Diesel engine spare parts & maintenance kit for min. 2500 hours of operation | Mandatory | enter prices on Form C: Price Schedule
Sound insolating and water proof canopy (max. 70 dB(A) at 7 m) | Mandatory | enter prices on Form C: Price Schedule
Work shop manual | Mandatory | enter prices on Form C: Price Schedule
Spare parts catalogue | Mandatory | enter prices on Form C: Price Schedule
60 Hz version of Generator set, please enter any surcharge to the std 50 Hz version offered above | Mandatory | enter prices on Form C: Price Schedule
Suggested Options
Heavy duty air filter for dusty conditions | Please provide price or state STD→ | Submit other option prices on a separate form
Heavy duty fuel filter/additional fuel filter in line with original | Please provide price or state STD→ | Submit other option prices on a separate form
Additional silencer, state dB(A) at 1 m and/or 7 m | Please provide price or state STD→ | Submit other option prices on a separate form
High chimney for exhaust, state height and materials | Please provide price or state STD→ | Submit other option prices on a separate form
(ATS) Automatic Transfer Switch | Please provide price or state STD→ | Submit other option prices on a separate form
Over speed protection | Please provide price or state STD→ | Submit other option prices on a separate form
Manual transfer switch | Please provide price or state STD→ | Submit other option prices on a separate form
External fuel tank with pipes including min.. 10 meter non-corrosive material and fittings, state volume of tank and material | Please provide price or state STD→ | Submit other option prices on a separate form
Slow moving trolley/trailer | Please provide price or state STD→ | Submit other option prices on a separate form
(AMF) Automatic Mains Failure Power generation set | Please provide price or state STD→ | Submit other option prices on a separate form
Automatic main circuit breaker | Please provide price or state STD→ | Submit other option prices on a separate form
Installation instructions and eventual. drawings, other languages | Please provide price or state STD→ | Submit other option prices on a separate form
Change over switch positions for: 1) Mains 2) Off 3) GENERATOR SET | Please provide price or state STD→ | Submit other option prices on a separate form
Automatic main circuit breaker | Please provide price or state STD→ | Submit other option prices on a separate form
Operators and maintenance manual, other languages | Please provide price or state STD→ | Submit other option prices on a separate form

## Lot 31 200 kVA PV 10% Roof
Bidder name:
Make and model:
Lot 31 200 kVA PV 10% Sloped Roof or Gen set mount.
HYBRID PV SOLAR/DIESEL GENERATOR SET SPECS | UNOPS REQUIREMENTS | Bidder: Compliant/Non-compliant to UNOPS requirements? Please mark YES/NO in this coloumn. Not indicating YES/NO in this column may render your bid non-compliant. | Bidders are required to provide information in this column on the specifications of their bid to demonstrate compliance to set specifications. Not providing specifications under this column may render your bid non-compliant.
Complete Hybrid PV solar/diesel generator set for autonomous operation, including PV solar power array, battery package, inverter and charge controller. Diesel engine, alternator, control panel with monitoring gauges/indicators, starting equipment, fuel tank as well as other accessories. Charger to charge battery package by diesel gen set and PV solar system interface between diesel gen set and PV solar power unit for a smooth operation for the two energy sources in conjunction, automatically without any manual intervention. Factory test certificates must be included and must be in accordance to internationally recognised standards. Suitable for tropical conditions. | Comply and state → | Yes / No
KEY DATA
Make | Please state →
Model | Please state →
Country of origin | Please state →
DIESEL GEN SET
Rated power output, min. 200 kVA | Comply and state → | Yes / No
Power factor: 0.8 | Comply and state → | Yes / No
Rated power output, 160 kW, min. | Comply and state → | Yes / No
Voltage, 220/230/240 and 380/400 V | Comply and state → | Yes / No
Phase: 1 and 3 | Comply and state → | Yes / No
AC frequency, 50/60 Hz | Comply and state → | Yes / No
Speed: rpm 1500 or 3000 or other | Please state →
Prime power according to ISO 8528 or equivalent, i.e. power available at variable load with no limitations on hours of operation and capable of min. 10% overload for min. 1 hour in any 12 hours. | Comply and state → | Yes / No
Prime rating of min. the stated output rating at Normal Temperature and Pressure conditions (NTP). Please state | Comply and state → | Yes / No
Derating information (temperature, altitude and humidity), please state | Please state →
Engine
Make | Please state →
Model | Please state →
Engine power output, kW at rpm: | Please state →
Fuel: Diesel | Comply and state → | Yes / No
Cooling, liquid or air or combined, suitable for tropical conditions | Please state →
Speed governor, state type | Please state →
Exhaust with suitable piping and residential silencer | Comply and state → | Yes / No
Noise level, dB(A) at 1 m (silencer fitted) | Please state →
Fuel consumption at 75% load: L/hour | Please state →
CO2 emissions at 75% load: g/hour | Please state →
Mounted on anti-vibration mounts | Comply and state → | Yes / No
ENVIRONMENTAL
EU Non-road emissions regulations schedule, e.g. EU STAGE II, III A, III B, IV. US Non-road and stationary emissions regulations to Tier 1,2,3,4 or equivalent. Please state. | Comply and state → | Yes / No
Alternator
Make: | Please state →
Model: | Please state →
Brushless type | Comply and state → | Yes / No
Cooling, liquid, air, other | Please state →
Protection class min. IP 23 | Comply and state → | Yes / No
Suitable AC power outlets protected by circuit breaker (state type) | Comply and state → | Yes / No
Insulation to min. IEC 60085 - >155 ° C - (F) or equivalent | Comply and state → | Yes / No
Voltage regulator | Comply and state → | Yes / No
Standard accessories
Fuel tank. Integrated or separate, suitable for continuous operation of min. 8 hours at rated capacity. State capacity, litres. Fuel level gauge. Including all necessary pipework, connections etc. Possibility for connection to external tank. | Comply and state→ | Yes / No
Low oil pressure protection, automatic shut down | Comply and state → | Yes / No
Over heating protection | Comply and state → | Yes / No
Overload protection | Comply and state → | Yes / No
Emergency stop | Comply and state → | Yes / No
Electric starter with key and battery | Comply and state → | Yes / No
Min. Voltmeter, ammeter, hour meter, Hz meter, water temp gauge/indicator (where applicable) | Comply and state → | Yes / No
Earthing/grounding facility | Comply and state → | Yes / No
PV SOLAR POWER SYSTEM STANDARD ARRAY NOMINAL MIN. 16.0 kWp. Battery pack 160 kWh. For Sloped Roof or Gen set mount.
PV solar array
Make and model: | Please state →
Array kWp, min 10% of diesel generator set max output which is 200 kVA/160kW, hence = 16.0kWp min. | Comply and state→ | Yes / No
PV panels, total surface covering, m2 | Please state →
Nominal power output each panel, kWp | Please state →
Isc array, A (Amp) | Please state →
Certifications: Any one or more of IEC61215, UL1703 or equivalent | Comply and state → | Yes / No
Charge controller
Make and model: | Please state →
Type: MTTP | Comply and state → | Yes / No
Certifications. Any one or more of EN60730-1/2-11, 55022, 61000-4-27374/5/6 or equivalent | Comply and state→ | Yes / No
Capacity: Isc array +20%, min. | Comply and state→ | Yes / No
Inverter
Make and model: | Please state →
Capacity, A (Amp): Min. equivalent to max load | Comply and state→ | Yes / No
Pure sine curve | Comply and state → | Yes / No
Certifications: Any one or more of EN50178, 62040, 60950, 61000-2/3/6, EN60529, 50438 or equivalent | Comply and state → | Yes / No
Battery package
Make and model: | Please state →
Capacity: Min. equivalent to hybrid diesel gen set full load - 24 kW - for 1 hour = 160kWh. | Comply and state→ | Yes / No
Battery type: LiFePo4 | Comply and state→ | Yes / No
Certifications,: Any one or more of UL1642, IEC62133, 61000-6-3 or equivalent | Comply and state→ | Yes / No
PV panel racks, brackets, cables, fittings etc.
PV panels racks for sloped roof mount included for all included PV panels, if not attached to the Hybrid Gen set system itself (permanently or fold-out system etc). | Comply and state→ | Yes / No
All cables, junctions, contacts, breakers, earthing spears, fittings, screws, nut and bots etc included | Comply and state → | Yes / No
Installation
The system must be plug and play. Inverter, charge controller, battery package, battery charger must be pre-installed and wired either inside one common Hybrid system cage or in a separate cabinet, in order to easily connect the PV array and the local installation. All cables for establishing the PV array must be readily available with pre-installed connections and clearly marked in a way that no mistakes can occur. | Comply and state → | Yes / No
Other
Lifting points for handling | Comply and state → | Yes / No
Installation instructions, drawings, photos, brochures etc. English/French/Spanish | Comply and state → | Yes / No
Operators and maintenance manual, English/French/Spanish | Comply and state → | Yes / No
Tool kit | Comply and state → | Yes / No
Basic maintenance kit, engine: Min. 4 x oil filters, 2 x air filters, 2 x fuel filters | Comply and state → | Yes / No
Dimensions, L x W x H, mm | Please state →
Weight, dry, entire hybrid system incl. Battery package and all PV panels, cables, brackets etc etc.: kg: | Please state →
WARRANTY
Diesel Generator set: 2 years/2500 hours of operation which ever occur first. PV panels: Min. 10 years. Min. 90% performance guarantee at 10 years. Min. 80% performance guarantee at 20 years. Battery package: Min. 5 years. Inverter/charge controller/charger: Min. 4 years. Other equipment: Min. 2 years | Comply and state → | Yes / No
Sustainability
The bidder must demonstrate that its organisation has an environmental management system in place which as a minimum shall submit at least one or more of the following : the environmental policy principles of the organisation; the management measures and procedures taken or that will be taken to assess, monitor, measure and mitigate environmental impacts of the business processes/products associated with the execution of the contract; how attention is paid to the awareness and training/competency of employee(s) and supplier(s) with regard to dealing with the environmental aspects relevant to this bid; and that compliance with the environmental legislation applicable to the required performance(s) is guaranteed, ISO 14001 certificate, EMAS or an equivalent certificate | Comply and state → | Yes / No
The bidder shall provide documentation which outlines their approach to ensuring equal opportunity, diversity and inclusion within their organisation (e.g. equal pay policy, parental leave, ratio of females/males employees, % of female in management positions, grievances disaggregated by gender, transparency of promotion criteria, sexual harassment policies) | Comply and state → | Yes / No
Mandatory Options
Diesel engine spare parts & maintenance kit for min. 2500 hours of operation | Mandatory | enter prices on Form C: Price Schedule
Sound insolating and water proof canopy (max. 70 dB(A) at 7 m) | Mandatory | enter prices on Form C: Price Schedule
Work shop manual | Mandatory | enter prices on Form C: Price Schedule
Spare parts catalogue | Mandatory | enter prices on Form C: Price Schedule
60 Hz version of Generator set, please enter any surcharge to the std 50 Hz version offered above | Mandatory | enter prices on Form C: Price Schedule
Suggested Options
Heavy duty air filter for dusty conditions | Please provide price or state STD→ | Submit other option prices on a separate form
Heavy duty fuel filter/additional fuel filter in line with original | Please provide price or state STD→ | Submit other option prices on a separate form
Additional silencer, state dB(A) at 1 m and/or 7 m | Please provide price or state STD→ | Submit other option prices on a separate form
High chimney for exhaust, state height and materials | Please provide price or state STD→ | Submit other option prices on a separate form
(ATS) Automatic Transfer Switch | Please provide price or state STD→ | Submit other option prices on a separate form
Over speed protection | Please provide price or state STD→ | Submit other option prices on a separate form
Manual transfer switch | Please provide price or state STD→ | Submit other option prices on a separate form
External fuel tank with pipes including min.. 10 meter non-corrosive material and fittings, state volume of tank and material | Please provide price or state STD→ | Submit other option prices on a separate form
Slow moving trolley/trailer | Please provide price or state STD→ | Submit other option prices on a separate form
(AMF) Automatic Mains Failure Power generation set | Please provide price or state STD→ | Submit other option prices on a separate form
Automatic main circuit breaker | Please provide price or state STD→ | Submit other option prices on a separate form
Installation instructions and eventual. drawings, other languages | Please provide price or state STD→ | Submit other option prices on a separate form
Change over switch positions for: 1) Mains 2) Off 3) GENERATOR SET | Please provide price or state STD→ | Submit other option prices on a separate form
Automatic main circuit breaker | Please provide price or state STD→ | Submit other option prices on a separate form
Operators and maintenance manual, other languages | Please provide price or state STD→ | Submit other option prices on a separate form

## Lot 32 200 kVA PV 20% Roof
Bidder name:
Make and model:
Lot 32 200 kVA PV 20% Sloped Roof or Gen set mount.
HYBRID PV SOLAR/DIESEL GENERATOR SET SPECS | UNOPS REQUIREMENTS | Bidder: Compliant/Non-compliant to UNOPS requirements? Please mark YES/NO in this coloumn. Not indicating YES/NO in this column may render your bid non-compliant. | Bidders are required to provide information in this column on the specifications of their bid to demonstrate compliance to set specifications. Not providing specifications under this column may render your bid non-compliant.
Complete Hybrid PV solar/diesel generator set for autonomous operation, including PV solar power array, battery package, inverter and charge controller. Diesel engine, alternator, control panel with monitoring gauges/indicators, starting equipment, fuel tank as well as other accessories. Charger to charge battery package by diesel gen set and PV solar system interface between diesel gen set and PV solar power unit for a smooth operation for the two energy sources in conjunction, automatically without any manual intervention. Factory test certificates must be included and must be in accordance to internationally recognised standards. Suitable for tropical conditions. | Comply and state → | Yes / No
KEY DATA
Make | Please state →
Model | Please state →
Country of origin | Please state →
DIESEL GEN SET
Rated power output, min. 200 kVA | Comply and state → | Yes / No
Power factor: 0.8 | Comply and state → | Yes / No
Rated power output, 160 kW, min. | Comply and state → | Yes / No
Voltage, 220/230/240 and 380/400 V | Comply and state → | Yes / No
Phase: 1 and 3 | Comply and state → | Yes / No
AC frequency, 50/60 Hz | Comply and state → | Yes / No
Speed: rpm 1500 or 3000 or other | Please state →
Prime power according to ISO 8528 or equivalent, i.e. power available at variable load with no limitations on hours of operation and capable of min. 10% overload for min. 1 hour in any 12 hours. | Comply and state → | Yes / No
Prime rating of min. the stated output rating at Normal Temperature and Pressure conditions (NTP). Please state | Comply and state → | Yes / No
Derating information (temperature, altitude and humidity), please state | Please state →
Engine
Make | Please state →
Model | Please state →
Engine power output, kW at rpm: | Please state →
Fuel: Diesel | Comply and state → | Yes / No
Cooling, liquid or air or combined, suitable for tropical conditions | Please state →
Speed governor, state type | Please state →
Exhaust with suitable piping and residential silencer | Comply and state → | Yes / No
Noise level, dB(A) at 1 m (silencer fitted) | Please state →
Fuel consumption at 75% load: L/hour | Please state →
CO2 emissions at 75% load: g/hour | Please state →
Mounted on anti-vibration mounts | Comply and state → | Yes / No
ENVIRONMENTAL
EU Non-road emissions regulations schedule, e.g. EU STAGE II, III A, III B, IV. US Non-road and stationary emissions regulations to Tier 1,2,3,4 or equivalent. Please state. | Comply and state → | Yes / No
Alternator
Make: | Please state →
Model: | Please state →
Brushless type | Comply and state → | Yes / No
Cooling, liquid, air, other | Please state →
Protection class min. IP 23 | Comply and state → | Yes / No
Suitable AC power outlets protected by circuit breaker (state type) | Comply and state → | Yes / No
Insulation to min. IEC 60085 - >155 ° C - (F) or equivalent | Comply and state → | Yes / No
Voltage regulator | Comply and state → | Yes / No
Standard accessories
Fuel tank. Integrated or separate, suitable for continuous operation of min. 8 hours at rated capacity. State capacity, litres. Fuel level gauge. Including all necessary pipework, connections etc. Possibility for connection to external tank. | Comply and state→ | Yes / No
Low oil pressure protection, automatic shut down | Comply and state → | Yes / No
Over heating protection | Comply and state → | Yes / No
Overload protection | Comply and state → | Yes / No
Emergency stop | Comply and state → | Yes / No
Electric starter with key and battery | Comply and state → | Yes / No
Min. Voltmeter, ammeter, hour meter, Hz meter, water temp gauge/indicator (where applicable) | Comply and state → | Yes / No
Earthing/grounding facility | Comply and state → | Yes / No
PV SOLAR POWER SYSTEM STANDARD ARRAY NOMINAL MIN. 32.0 kWp. Battery pack 160 kWh. For Sloped Roof or Gen set mount.
PV solar array
Make and model: | Please state →
Array kWp, min 20% of diesel generator set max output which is 200 kVA/160kW, hence = 32.0kWp min. | Comply and state→ | Yes / No
PV panels, total surface covering, m2 | Please state →
Nominal power output each panel, kWp | Please state →
Isc array, A (Amp) | Please state →
Certifications: Any one or more of IEC61215, UL1703 or equivalent | Comply and state → | Yes / No
Charge controller
Make and model: | Please state →
Type: MTTP | Comply and state → | Yes / No
Certifications. Any one or more of EN60730-1/2-11, 55022, 61000-4-27374/5/6 or equivalent | Comply and state→ | Yes / No
Capacity: Isc array +20%, min. | Comply and state→ | Yes / No
Inverter
Make and model: | Please state →
Capacity, A (Amp): Min. equivalent to max load | Comply and state→ | Yes / No
Pure sine curve | Comply and state → | Yes / No
Certifications: Any one or more of EN50178, 62040, 60950, 61000-2/3/6, EN60529, 50438 or equivalent | Comply and state → | Yes / No
Battery package
Make and model: | Please state →
Capacity: Min. equivalent to hybrid diesel gen set full load - 24 kW - for 1 hour = 160kWh. | Comply and state→ | Yes / No
Battery type: LiFePo4 | Comply and state→ | Yes / No
Certifications,: Any one or more of UL1642, IEC62133, 61000-6-3 or equivalent | Comply and state→ | Yes / No
PV panel racks, brackets, cables, fittings etc. | Comply and state→
PV panels racks for sloped roof mount included for all included PV panels, if not attached to the Hybrid Gen set system itself (permanently or fold-out system etc). | Comply and state→ | Yes / No
All cables, junctions, contacts, breakers, earthing spears, fittings, screws, nut and bots etc included | Comply and state → | Yes / No
Installation
The system must be plug and play. Inverter, charge controller, battery package, battery charger must be pre-installed and wired either inside one common Hybrid system cage or in a separate cabinet, in order to easily connect the PV array and the local installation. All cables for establishing the PV array must be readily available with pre-installed connections and clearly marked in a way that no mistakes can occur. | Comply and state → | Yes / No
Other
Lifting points for handling | Comply and state → | Yes / No
Installation instructions, drawings, photos, brochures etc. English/French/Spanish | Comply and state → | Yes / No
Operators and maintenance manual, English/French/Spanish | Comply and state → | Yes / No
Tool kit | Comply and state → | Yes / No
Basic maintenance kit, engine: Min. 4 x oil filters, 2 x air filters, 2 x fuel filters | Comply and state → | Yes / No
Dimensions, L x W x H, mm | Please state →
Weight, dry, entire hybrid system incl. Battery package and all PV panels, cables, brackets etc etc.: kg: | Please state →
WARRANTY
Diesel Generator set: 2 years/2500 hours of operation which ever occur first. PV panels: Min. 10 years. Min. 90% performance guarantee at 10 years. Min. 80% performance guarantee at 20 years. Battery package: Min. 5 years. Inverter/charge controller/charger: Min. 4 years. Other equipment: Min. 2 years | Comply and state → | Yes / No
Sustainability
The bidder must demonstrate that its organisation has an environmental management system in place which as a minimum shall submit at least one or more of the following : the environmental policy principles of the organisation; the management measures and procedures taken or that will be taken to assess, monitor, measure and mitigate environmental impacts of the business processes/products associated with the execution of the contract; how attention is paid to the awareness and training/competency of employee(s) and supplier(s) with regard to dealing with the environmental aspects relevant to this bid; and that compliance with the environmental legislation applicable to the required performance(s) is guaranteed, ISO 14001 certificate, EMAS or an equivalent certificate | Comply and state → | Yes / No
The bidder shall provide documentation which outlines their approach to ensuring equal opportunity, diversity and inclusion within their organisation (e.g. equal pay policy, parental leave, ratio of females/males employees, % of female in management positions, grievances disaggregated by gender, transparency of promotion criteria, sexual harassment policies) | Comply and state → | Yes / No
Mandatory Options
Diesel engine spare parts & maintenance kit for min. 2500 hours of operation | Mandatory | enter prices on Form C: Price Schedule
Sound insolating and water proof canopy (max. 70 dB(A) at 7 m) | Mandatory | enter prices on Form C: Price Schedule
Work shop manual | Mandatory | enter prices on Form C: Price Schedule
Spare parts catalogue | Mandatory | enter prices on Form C: Price Schedule
60 Hz version of Generator set, please enter any surcharge to the std 50 Hz version offered above | Mandatory | enter prices on Form C: Price Schedule
Suggested Options
Heavy duty air filter for dusty conditions | Please provide price or state STD→ | Submit other option prices on a separate form
Heavy duty fuel filter/additional fuel filter in line with original | Please provide price or state STD→ | Submit other option prices on a separate form
Additional silencer, state dB(A) at 1 m and/or 7 m | Please provide price or state STD→ | Submit other option prices on a separate form
High chimney for exhaust, state height and materials | Please provide price or state STD→ | Submit other option prices on a separate form
(ATS) Automatic Transfer Switch | Please provide price or state STD→ | Submit other option prices on a separate form
Over speed protection | Please provide price or state STD→ | Submit other option prices on a separate form
Manual transfer switch | Please provide price or state STD→ | Submit other option prices on a separate form
External fuel tank with pipes including min.. 10 meter non-corrosive material and fittings, state volume of tank and material | Please provide price or state STD→ | Submit other option prices on a separate form
Slow moving trolley/trailer | Please provide price or state STD→ | Submit other option prices on a separate form
(AMF) Automatic Mains Failure Power generation set | Please provide price or state STD→ | Submit other option prices on a separate form
Automatic main circuit breaker | Please provide price or state STD→ | Submit other option prices on a separate form
Installation instructions and eventual. drawings, other languages | Please provide price or state STD→ | Submit other option prices on a separate form
Change over switch positions for: 1) Mains 2) Off 3) GENERATOR SET | Please provide price or state STD→ | Submit other option prices on a separate form
Automatic main circuit breaker | Please provide price or state STD→ | Submit other option prices on a separate form
Operators and maintenance manual, other languages | Please provide price or state STD→ | Submit other option prices on a separate form

## Lot 33 200 kVA PV 40% Roof
Bidder name:
Make and model:
Lot 33 200 kVA PV 40% Sloped Roof or Gen set mount.
HYBRID PV SOLAR/DIESEL GENERATOR SET SPECS | UNOPS REQUIREMENTS | Bidder: Compliant/Non-compliant to UNOPS requirements? Please mark YES/NO in this coloumn. Not indicating YES/NO in this column may render your bid non-compliant. | Bidders are required to provide information in this column on the specifications of their bid to demonstrate compliance to set specifications. Not providing specifications under this column may render your bid non-compliant.
Complete Hybrid PV solar/diesel generator set for autonomous operation, including PV solar power array, battery package, inverter and charge controller. Diesel engine, alternator, control panel with monitoring gauges/indicators, starting equipment, fuel tank as well as other accessories. Charger to charge battery package by diesel gen set and PV solar system interface between diesel gen set and PV solar power unit for a smooth operation for the two energy sources in conjunction, automatically without any manual intervention. Factory test certificates must be included and must be in accordance to internationally recognised standards. Suitable for tropical conditions. | Comply and state → | Yes / No
KEY DATA
Make | Please state →
Model | Please state →
Country of origin | Please state →
DIESEL GEN SET
Rated power output, min. 200 kVA | Comply and state → | Yes / No
Power factor: 0.8 | Comply and state → | Yes / No
Rated power output, 160 kW, min. | Comply and state → | Yes / No
Voltage, 220/230/240 and 380/400 V | Comply and state → | Yes / No
Phase: 1 and 3 | Comply and state → | Yes / No
AC frequency, 50/60 Hz | Comply and state → | Yes / No
Speed: rpm 1500 or 3000 or other | Please state →
Prime power according to ISO 8528 or equivalent, i.e. power available at variable load with no limitations on hours of operation and capable of min. 10% overload for min. 1 hour in any 12 hours. | Comply and state → | Yes / No
Prime rating of min. the stated output rating at Normal Temperature and Pressure conditions (NTP). Please state | Comply and state → | Yes / No
Derating information (temperature, altitude and humidity), please state | Please state →
Engine
Make | Please state →
Model | Please state →
Engine power output, kW at rpm: | Please state →
Fuel: Diesel | Comply and state → | Yes / No
Cooling, liquid or air or combined, suitable for tropical conditions | Please state →
Speed governor, state type | Please state →
Exhaust with suitable piping and residential silencer | Comply and state → | Yes / No
Noise level, dB(A) at 1 m (silencer fitted) | Please state →
Fuel consumption at 75% load: L/hour | Please state →
CO2 emissions at 75% load: g/hour | Please state →
Mounted on anti-vibration mounts | Comply and state → | Yes / No
ENVIRONMENTAL
EU Non-road emissions regulations schedule, e.g. EU STAGE II, III A, III B, IV. US Non-road and stationary emissions regulations to Tier 1,2,3,4 or equivalent. Please state. | Comply and state → | Yes / No
Alternator
Make: | Please state →
Model: | Please state →
Brushless type | Comply and state → | Yes / No
Cooling, liquid, air, other | Please state →
Protection class min. IP 23 | Comply and state → | Yes / No
Suitable AC power outlets protected by circuit breaker (state type) | Comply and state → | Yes / No
Insulation to min. IEC 60085 - >155 ° C - (F) or equivalent | Comply and state → | Yes / No
Voltage regulator | Comply and state → | Yes / No
Standard accessories
Fuel tank. Integrated or separate, suitable for continuous operation of min. 8 hours at rated capacity. State capacity, litres. Fuel level gauge. Including all necessary pipework, connections etc. Possibility for connection to external tank. | Comply and state→ | Yes / No
Low oil pressure protection, automatic shut down | Comply and state → | Yes / No
Over heating protection | Comply and state → | Yes / No
Overload protection | Comply and state → | Yes / No
Emergency stop | Comply and state → | Yes / No
Electric starter with key and battery | Comply and state → | Yes / No
Min. Voltmeter, ammeter, hour meter, Hz meter, water temp gauge/indicator (where applicable) | Comply and state → | Yes / No
Earthing/grounding facility | Comply and state → | Yes / No
PV SOLAR POWER SYSTEM STANDARD ARRAY NOMINAL MIN. 64.0kWp. Battery pack 160 kWh. For Sloped Roof or Gen set mount.
PV solar array
Make and model: | Please state →
Array kWp, min 40% of diesel generator set max output which is 200 kVA/160kW, hence = 64.0kWp min. | Comply and state→ | Yes / No
PV panels, total surface covering, m2 | Please state →
Nominal power output each panel, kWp | Please state →
Isc array, A (Amp) | Please state →
Certifications: Any one or more of IEC61215, UL1703 or equivalent | Comply and state → | Yes / No
Charge controller
Make and model: | Please state →
Type: MTTP | Comply and state → | Yes / No
Certifications. Any one or more of EN60730-1/2-11, 55022, 61000-4-27374/5/6 or equivalent | Comply and state→ | Yes / No
Capacity: Isc array +20%, min. | Comply and state→ | Yes / No
Inverter
Make and model: | Please state →
Capacity, A (Amp): Min. equivalent to max load | Comply and state→ | Yes / No
Pure sine curve | Comply and state → | Yes / No
Certifications: Any one or more of EN50178, 62040, 60950, 61000-2/3/6, EN60529, 50438 or equivalent | Comply and state → | Yes / No
Battery package
Make and model: | Please state →
Capacity: Min. equivalent to hybrid diesel gen set full load - 24 kW - for 1 hour = 160kWh. | Comply and state→ | Yes / No
Battery type: LiFePo4 | Comply and state→ | Yes / No
Certifications,: Any one or more of UL1642, IEC62133, 61000-6-3 or equivalent | Comply and state→ | Yes / No
PV panel racks, brackets, cables, fittings etc. | Comply and state→
PV panels racks for sloped roof mount included for all included PV panels, if not attached to the Hybrid Gen set system itself (permanently or fold-out system etc). | Comply and state→ | Yes / No
All cables, junctions, contacts, breakers, earthing spears, fittings, screws, nut and bots etc included | Comply and state → | Yes / No
Installation
The system must be plug and play. Inverter, charge controller, battery package, battery charger must be pre-installed and wired either inside one common Hybrid system cage or in a separate cabinet, in order to easily connect the PV array and the local installation. All cables for establishing the PV array must be readily available with pre-installed connections and clearly marked in a way that no mistakes can occur. | Comply and state → | Yes / No
Other
Lifting points for handling | Comply and state → | Yes / No
Installation instructions, drawings, photos, brochures etc. English/French/Spanish | Comply and state → | Yes / No
Operators and maintenance manual, English/French/Spanish | Comply and state → | Yes / No
Tool kit | Comply and state → | Yes / No
Basic maintenance kit, engine: Min. 4 x oil filters, 2 x air filters, 2 x fuel filters | Comply and state → | Yes / No
Dimensions, L x W x H, mm | Please state →
Weight, dry, entire hybrid system incl. Battery package and all PV panels, cables, brackets etc etc.: kg: | Please state →
WARRANTY
Diesel Generator set: 2 years/2500 hours of operation which ever occur first. PV panels: Min. 10 years. Min. 90% performance guarantee at 10 years. Min. 80% performance guarantee at 20 years. Battery package: Min. 5 years. Inverter/charge controller/charger: Min. 4 years. Other equipment: Min. 2 years | Comply and state → | Yes / No
Sustainability
The bidder must demonstrate that its organisation has an environmental management system in place which as a minimum shall submit at least one or more of the following : the environmental policy principles of the organisation; the management measures and procedures taken or that will be taken to assess, monitor, measure and mitigate environmental impacts of the business processes/products associated with the execution of the contract; how attention is paid to the awareness and training/competency of employee(s) and supplier(s) with regard to dealing with the environmental aspects relevant to this bid; and that compliance with the environmental legislation applicable to the required performance(s) is guaranteed, ISO 14001 certificate, EMAS or an equivalent certificate | Comply and state → | Yes / No
The bidder shall provide documentation which outlines their approach to ensuring equal opportunity, diversity and inclusion within their organisation (e.g. equal pay policy, parental leave, ratio of females/males employees, % of female in management positions, grievances disaggregated by gender, transparency of promotion criteria, sexual harassment policies) | Comply and state → | Yes / No
Mandatory Options
Diesel engine spare parts & maintenance kit for min. 2500 hours of operation | Mandatory | enter prices on Form C: Price Schedule
Sound insolating and water proof canopy (max. 70 dB(A) at 7 m) | Mandatory | enter prices on Form C: Price Schedule
Work shop manual | Mandatory | enter prices on Form C: Price Schedule
Spare parts catalogue | Mandatory | enter prices on Form C: Price Schedule
60 Hz version of Generator set, please enter any surcharge to the std 50 Hz version offered above | Mandatory | enter prices on Form C: Price Schedule
Suggested Options
Heavy duty air filter for dusty conditions | Please provide price or state STD→ | Submit other option prices on a separate form
Heavy duty fuel filter/additional fuel filter in line with original | Please provide price or state STD→ | Submit other option prices on a separate form
Additional silencer, state dB(A) at 1 m and/or 7 m | Please provide price or state STD→ | Submit other option prices on a separate form
High chimney for exhaust, state height and materials | Please provide price or state STD→ | Submit other option prices on a separate form
(ATS) Automatic Transfer Switch | Please provide price or state STD→ | Submit other option prices on a separate form
Over speed protection | Please provide price or state STD→ | Submit other option prices on a separate form
Manual transfer switch | Please provide price or state STD→ | Submit other option prices on a separate form
External fuel tank with pipes including min.. 10 meter non-corrosive material and fittings, state volume of tank and material | Please provide price or state STD→ | Submit other option prices on a separate form
Slow moving trolley/trailer | Please provide price or state STD→ | Submit other option prices on a separate form
(AMF) Automatic Mains Failure Power generation set | Please provide price or state STD→ | Submit other option prices on a separate form
Automatic main circuit breaker | Please provide price or state STD→ | Submit other option prices on a separate form
Installation instructions and eventual. drawings, other languages | Please provide price or state STD→ | Submit other option prices on a separate form
Change over switch positions for: 1) Mains 2) Off 3) GENERATOR SET | Please provide price or state STD→ | Submit other option prices on a separate form
Automatic main circuit breaker | Please provide price or state STD→ | Submit other option prices on a separate form
Operators and maintenance manual, other languages | Please provide price or state STD→ | Submit other option prices on a separate form

## Lot 34 200 kVA PV 10% Ground
Bidder name:
Make and model:
Lot 34. 200 kVA PV 10% Ground or flat roof mounted
HYBRID PV SOLAR/DIESEL GENERATOR SET SPECS | UNOPS REQUIREMENTS | Bidder: Compliant/Non-compliant to UNOPS requirements? Please mark YES/NO in this coloumn. Not indicating YES/NO in this column may render your bid non-compliant. | Bidders are required to provide information in this column on the specifications of their bid to demonstrate compliance to set specifications. Not providing specifications under this column may render your bid non-compliant.
Complete Hybrid PV solar/diesel generator set for autonomous operation, including PV solar power array, battery package, inverter and charge controller. Diesel engine, alternator, control panel with monitoring gauges/indicators, starting equipment, fuel tank as well as other accessories. Charger to charge battery package by diesel gen set and PV solar system interface between diesel gen set and PV solar power unit for a smooth operation for the two energy sources in conjunction, automatically without any manual intervention. Factory test certificates must be included and must be in accordance to internationally recognised standards. Suitable for tropical conditions. | Comply and state → | Yes / No
KEY DATA
Make | Please state →
Model | Please state →
Country of origin | Please state →
DIESEL GEN SET
Rated power output, min. 200 kVA | Comply and state → | Yes / No
Power factor: 0.8 | Comply and state → | Yes / No
Rated power output, 160 kW, min. | Comply and state → | Yes / No
Voltage, 220/230/240 and 380/400 V | Comply and state → | Yes / No
Phase: 1 and 3 | Comply and state → | Yes / No
AC frequency, 50/60 Hz | Comply and state → | Yes / No
Speed: rpm 1500 or 3000 or other | Please state →
Prime power according to ISO 8528 or equivalent, i.e. power available at variable load with no limitations on hours of operation and capable of min. 10% overload for min. 1 hour in any 12 hours. | Comply and state → | Yes / No
Prime rating of min. the stated output rating at Normal Temperature and Pressure conditions (NTP). Please state | Comply and state → | Yes / No
Derating information (temperature, altitude and humidity), please state | Please state →
Engine
Make | Please state →
Model | Please state →
Engine power output, kW at rpm: | Please state →
Fuel: Diesel | Comply and state → | Yes / No
Cooling, liquid or air or combined, suitable for tropical conditions | Please state →
Speed governor, state type | Please state →
Exhaust with suitable piping and residential silencer | Comply and state → | Yes / No
Noise level, dB(A) at 1 m (silencer fitted) | Please state →
Fuel consumption at 75% load: L/hour | Please state →
CO2 emissions at 75% load: g/hour | Please state →
Mounted on anti-vibration mounts | Comply and state → | Yes / No
ENVIRONMENTAL
EU Non-road emissions regulations schedule, e.g. EU STAGE II, III A, III B, IV. US Non-road and stationary emissions regulations to Tier 1,2,3,4 or equivalent. Please state. | Comply and state → | Yes / No
Alternator
Make: | Please state →
Model: | Please state →
Brushless type | Comply and state → | Yes / No
Cooling, liquid, air, other | Please state →
Protection class min. IP 23 | Comply and state → | Yes / No
Suitable AC power outlets protected by circuit breaker (state type) | Comply and state → | Yes / No
Insulation to min. IEC 60085 - >155 ° C - (F) or equivalent | Comply and state → | Yes / No
Voltage regulator | Comply and state → | Yes / No
Standard accessories
Fuel tank. Integrated or separate, suitable for continuous operation of min. 8 hours at rated capacity. State capacity, litres. Fuel level gauge. Including all necessary pipework, connections etc. Possibility for connection to external tank. | Comply and state→ | Yes / No
Low oil pressure protection, automatic shut down | Comply and state → | Yes / No
Over heating protection | Comply and state → | Yes / No
Overload protection | Comply and state → | Yes / No
Emergency stop | Comply and state → | Yes / No
Electric starter with key and battery | Comply and state → | Yes / No
Min. Voltmeter, ammeter, hour meter, Hz meter, water temp gauge/indicator (where applicable) | Comply and state → | Yes / No
Earthing/grounding facility | Comply and state → | Yes / No
PV SOLAR POWER SYSTEM STANDARD ARRAY NOMINAL MIN. 16.0 kWp. Battery pack 160 kWh. For Ground or flat roof mount
PV solar array
Make and model: | Please state →
Array kWp, min 10% of diesel generator set max output which is 200kVA/160kW, hence = 16.0kWp min. | Comply and state→ | Yes / No
PV panels, total surface covering, m2 | Please state →
Nominal power output each panel, kWp | Please state →
Isc array, A (Amp) | Please state →
Certifications: Any one or more of IEC61215, UL1703 or equivalent | Comply and state → | Yes / No
Charge controller
Make and model: | Please state →
Type: MTTP | Comply and state → | Yes / No
Certifications. Any one or more of EN60730-1/2-11, 55022, 61000-4-27374/5/6 or equivalent | Comply and state→ | Yes / No
Capacity: Isc array +20%, min. | Comply and state→ | Yes / No
Inverter
Make and model: | Please state →
Capacity, A (Amp): Min. equivalent to max load | Comply and state→ | Yes / No
Pure sine curve | Comply and state → | Yes / No
Certifications: Any one or more of EN50178, 62040, 60950, 61000-2/3/6, EN60529, 50438 or equivalent | Comply and state → | Yes / No
Battery package
Make and model: | Please state →
Capacity: Min. equivalent to hybrid diesel gen set full load - 24 kW - for 1 hour = 160 kWh. | Comply and state→ | Yes / No
Battery type: LiFePo4 | Comply and state→ | Yes / No
Certifications,: Any one or more of UL1642, IEC62133, 61000-6-3 or equivalent | Comply and state→ | Yes / No
PV panel racks, brackets, cables, fittings etc.
PV panels racks for Ground or flat roof mount. | Comply and state→ | Yes / No
All cables, junctions, contacts, breakers, earthing spears, fittings, screws, nut and bots etc included | Comply and state → | Yes / No
Installation
The system must be plug and play. Inverter, charge controller, battery package, battery charger must be pre-installed and wired either inside one common Hybrid system cage or in a separate cabinet, in order to easily connect the PV array and the local installation. All cables for establishing the PV array must be readily available with pre-installed connections and clearly marked in a way that no mistakes can occur. | Comply and state → | Yes / No
Other
Lifting points for handling | Comply and state → | Yes / No
Installation instructions, drawings, photos, brochures etc. English/French/Spanish | Comply and state → | Yes / No
Operators and maintenance manual, English/French/Spanish | Comply and state → | Yes / No
Tool kit | Comply and state → | Yes / No
Basic maintenance kit, engine: Min. 4 x oil filters, 2 x air filters, 2 x fuel filters | Comply and state → | Yes / No
Dimensions, L x W x H, mm | Please state →
Weight, dry, entire hybrid system incl. Battery package and all PV panels, cables, brackets etc etc.: kg: | Please state →
WARRANTY
Diesel Generator set: 2 years/2500 hours of operation which ever occur first. PV panels: Min. 10 years. Min. 90% performance guarantee at 10 years. Min. 80% performance guarantee at 20 years. Battery package: Min. 5 years. Inverter/charge controller/charger: Min. 4 years. Other equipment: Min. 2 years | Comply and state → | Yes / No
Sustainability
The bidder must demonstrate that its organisation has an environmental management system in place which as a minimum shall submit at least one or more of the following : the environmental policy principles of the organisation; the management measures and procedures taken or that will be taken to assess, monitor, measure and mitigate environmental impacts of the business processes/products associated with the execution of the contract; how attention is paid to the awareness and training/competency of employee(s) and supplier(s) with regard to dealing with the environmental aspects relevant to this bid; and that compliance with the environmental legislation applicable to the required performance(s) is guaranteed, ISO 14001 certificate, EMAS or an equivalent certificate | Comply and state → | Yes / No
The bidder shall provide documentation which outlines their approach to ensuring equal opportunity, diversity and inclusion within their organisation (e.g. equal pay policy, parental leave, ratio of females/males employees, % of female in management positions, grievances disaggregated by gender, transparency of promotion criteria, sexual harassment policies) | Comply and state → | Yes / No
Mandatory Options
Diesel engine spare parts & maintenance kit for min. 2500 hours of operation | Mandatory | enter prices on Form C: Price Schedule
Sound insolating and water proof canopy (max. 70 dB(A) at 7 m) | Mandatory | enter prices on Form C: Price Schedule
Work shop manual | Mandatory | enter prices on Form C: Price Schedule
Spare parts catalogue | Mandatory | enter prices on Form C: Price Schedule
60 Hz version of Generator set, please enter any surcharge to the std 50 Hz version offered above | Mandatory | enter prices on Form C: Price Schedule
Suggested Options
Heavy duty air filter for dusty conditions | Please provide price or state STD→ | Submit other option prices on a separate form
Heavy duty fuel filter/additional fuel filter in line with original | Please provide price or state STD→ | Submit other option prices on a separate form
Additional silencer, state dB(A) at 1 m and/or 7 m | Please provide price or state STD→ | Submit other option prices on a separate form
High chimney for exhaust, state height and materials | Please provide price or state STD→ | Submit other option prices on a separate form
(ATS) Automatic Transfer Switch | Please provide price or state STD→ | Submit other option prices on a separate form
Over speed protection | Please provide price or state STD→ | Submit other option prices on a separate form
Manual transfer switch | Please provide price or state STD→ | Submit other option prices on a separate form
External fuel tank with pipes including min.. 10 meter non-corrosive material and fittings, state volume of tank and material | Please provide price or state STD→ | Submit other option prices on a separate form
Slow moving trolley/trailer | Please provide price or state STD→ | Submit other option prices on a separate form
(AMF) Automatic Mains Failure Power generation set | Please provide price or state STD→ | Submit other option prices on a separate form
Automatic main circuit breaker | Please provide price or state STD→ | Submit other option prices on a separate form
Installation instructions and eventual. drawings, other languages | Please provide price or state STD→ | Submit other option prices on a separate form
Change over switch positions for: 1) Mains 2) Off 3) GENERATOR SET | Please provide price or state STD→ | Submit other option prices on a separate form
Automatic main circuit breaker | Please provide price or state STD→ | Submit other option prices on a separate form
Operators and maintenance manual, other languages | Please provide price or state STD→ | Submit other option prices on a separate form

## Lot 35 200 kVA 20% Ground
Bidder name:
Make and model:
Lot 35. 200 kVA PV 20% Ground or flat roof mounted
HYBRID PV SOLAR/DIESEL GENERATOR SET SPECS | UNOPS REQUIREMENTS | Bidder: Compliant/Non-compliant to UNOPS requirements? Please mark YES/NO in this coloumn. Not indicating YES/NO in this column may render your bid non-compliant. | Bidders are required to provide information in this column on the specifications of their bid to demonstrate compliance to set specifications. Not providing specifications under this column may render your bid non-compliant.
Complete Hybrid PV solar/diesel generator set for autonomous operation, including PV solar power array, battery package, inverter and charge controller. Diesel engine, alternator, control panel with monitoring gauges/indicators, starting equipment, fuel tank as well as other accessories. Charger to charge battery package by diesel gen set and PV solar system interface between diesel gen set and PV solar power unit for a smooth operation for the two energy sources in conjunction, automatically without any manual intervention. Factory test certificates must be included and must be in accordance to internationally recognised standards. Suitable for tropical conditions. | Comply and state → | Yes / No
KEY DATA
Make | Please state →
Model | Please state →
Country of origin | Please state →
DIESEL GEN SET
Rated power output, min. 200 kVA | Comply and state → | Yes / No
Power factor: 0.8 | Comply and state → | Yes / No
Rated power output, 160 kW, min. | Comply and state → | Yes / No
Voltage, 220/230/240 and 380/400 V | Comply and state → | Yes / No
Phase: 1 and 3 | Comply and state → | Yes / No
AC frequency, 50/60 Hz | Comply and state → | Yes / No
Speed: rpm 1500 or 3000 or other | Please state →
Prime power according to ISO 8528 or equivalent, i.e. power available at variable load with no limitations on hours of operation and capable of min. 10% overload for min. 1 hour in any 12 hours. | Comply and state → | Yes / No
Prime rating of min. the stated output rating at Normal Temperature and Pressure conditions (NTP). Please state | Comply and state → | Yes / No
Derating information (temperature, altitude and humidity), please state | Please state →
Engine
Make | Please state →
Model | Please state →
Engine power output, kW at rpm: | Please state →
Fuel: Diesel | Comply and state → | Yes / No
Cooling, liquid or air or combined, suitable for tropical conditions | Please state →
Speed governor, state type | Please state →
Exhaust with suitable piping and residential silencer | Comply and state → | Yes / No
Noise level, dB(A) at 1 m (silencer fitted) | Please state →
Fuel consumption at 75% load: L/hour | Please state →
CO2 emissions at 75% load: g/hour | Please state →
Mounted on anti-vibration mounts | Comply and state → | Yes / No
ENVIRONMENTAL
EU Non-road emissions regulations schedule, e.g. EU STAGE II, III A, III B, IV. US Non-road and stationary emissions regulations to Tier 1,2,3,4 or equivalent. Please state. | Comply and state → | Yes / No
Alternator
Make: | Please state →
Model: | Please state →
Brushless type | Comply and state → | Yes / No
Cooling, liquid, air, other | Please state →
Protection class min. IP 23 | Comply and state → | Yes / No
Suitable AC power outlets protected by circuit breaker (state type) | Comply and state → | Yes / No
Insulation to min. IEC 60085 - >155 ° C - (F) or equivalent | Comply and state → | Yes / No
Voltage regulator | Comply and state → | Yes / No
Standard accessories
Fuel tank. Integrated or separate, suitable for continuous operation of min. 8 hours at rated capacity. State capacity, litres. Fuel level gauge. Including all necessary pipework, connections etc. Possibility for connection to external tank. | Comply and state→ | Yes / No
Low oil pressure protection, automatic shut down | Comply and state → | Yes / No
Over heating protection | Comply and state → | Yes / No
Overload protection | Comply and state → | Yes / No
Emergency stop | Comply and state → | Yes / No
Electric starter with key and battery | Comply and state → | Yes / No
Min. Voltmeter, ammeter, hour meter, Hz meter, water temp gauge/indicator (where applicable) | Comply and state → | Yes / No
Earthing/grounding facility | Comply and state → | Yes / No
PV SOLAR POWER SYSTEM STANDARD ARRAY NOMINAL MIN. 32.0 kWp. Battery pack 160 kWh. For Ground or flat roof mount
PV solar array
Make and model: | Please state →
Array kWp, min 20% of diesel generator set max output which is 200kVA/160kW, hence = 32.0kWp min. | Comply and state→ | Yes / No
PV panels, total surface covering, m2 | Please state →
Nominal power output each panel, kWp | Please state →
Isc array, A (Amp) | Please state →
Certifications: Any one or more of IEC61215, UL1703 or equivalent | Comply and state → | Yes / No
Charge controller
Make and model: | Please state →
Type: MTTP | Comply and state → | Yes / No
Certifications. Any one or more of EN60730-1/2-11, 55022, 61000-4-27374/5/6 or equivalent | Comply and state→ | Yes / No
Capacity: Isc array +20%, min. | Comply and state→ | Yes / No
Inverter
Make and model: | Please state →
Capacity, A (Amp): Min. equivalent to max load | Comply and state→ | Yes / No
Pure sine curve | Comply and state → | Yes / No
Certifications: Any one or more of EN50178, 62040, 60950, 61000-2/3/6, EN60529, 50438 or equivalent | Comply and state → | Yes / No
Battery package
Make and model: | Please state →
Capacity: Min. equivalent to hybrid diesel gen set full load - 24 kW - for 1 hour = 160 kWh. | Comply and state→ | Yes / No
Battery type: LiFePo4 | Comply and state→ | Yes / No
Certifications,: Any one or more of UL1642, IEC62133, 61000-6-3 or equivalent | Comply and state→ | Yes / No
PV panel racks, brackets, cables, fittings etc.
PV panels racks for Ground or flat roof mount. | Comply and state→ | Yes / No
All cables, junctions, contacts, breakers, earthing spears, fittings, screws, nut and bots etc included | Comply and state → | Yes / No
Installation
The system must be plug and play. Inverter, charge controller, battery package, battery charger must be pre-installed and wired either inside one common Hybrid system cage or in a separate cabinet, in order to easily connect the PV array and the local installation. All cables for establishing the PV array must be readily available with pre-installed connections and clearly marked in a way that no mistakes can occur. | Comply and state → | Yes / No
Other
Lifting points for handling | Comply and state → | Yes / No
Installation instructions, drawings, photos, brochures etc. English/French/Spanish | Comply and state → | Yes / No
Operators and maintenance manual, English/French/Spanish | Comply and state → | Yes / No
Tool kit | Comply and state → | Yes / No
Basic maintenance kit, engine: Min. 4 x oil filters, 2 x air filters, 2 x fuel filters | Comply and state → | Yes / No
Dimensions, L x W x H, mm | Please state →
Weight, dry, entire hybrid system incl. Battery package and all PV panels, cables, brackets etc etc.: kg: | Please state →
WARRANTY
Diesel Generator set: 2 years/2500 hours of operation which ever occur first. PV panels: Min. 10 years. Min. 90% performance guarantee at 10 years. Min. 80% performance guarantee at 20 years. Battery package: Min. 5 years. Inverter/charge controller/charger: Min. 4 years. Other equipment: Min. 2 years | Comply and state → | Yes / No
Sustainability
The bidder must demonstrate that its organisation has an environmental management system in place which as a minimum shall submit at least one or more of the following : the environmental policy principles of the organisation; the management measures and procedures taken or that will be taken to assess, monitor, measure and mitigate environmental impacts of the business processes/products associated with the execution of the contract; how attention is paid to the awareness and training/competency of employee(s) and supplier(s) with regard to dealing with the environmental aspects relevant to this bid; and that compliance with the environmental legislation applicable to the required performance(s) is guaranteed, ISO 14001 certificate, EMAS or an equivalent certificate | Comply and state → | Yes / No
The bidder shall provide documentation which outlines their approach to ensuring equal opportunity, diversity and inclusion within their organisation (e.g. equal pay policy, parental leave, ratio of females/males employees, % of female in management positions, grievances disaggregated by gender, transparency of promotion criteria, sexual harassment policies) | Comply and state → | Yes / No
Mandatory Options
Diesel engine spare parts & maintenance kit for min. 2500 hours of operation | Mandatory | enter prices on Form C: Price Schedule
Sound insolating and water proof canopy (max. 70 dB(A) at 7 m) | Mandatory | enter prices on Form C: Price Schedule
Work shop manual | Mandatory | enter prices on Form C: Price Schedule
Spare parts catalogue | Mandatory | enter prices on Form C: Price Schedule
60 Hz version of Generator set, please enter any surcharge to the std 50 Hz version offered above | Mandatory | enter prices on Form C: Price Schedule
Suggested Options
Heavy duty air filter for dusty conditions | Please provide price or state STD→ | Submit other option prices on a separate form
Heavy duty fuel filter/additional fuel filter in line with original | Please provide price or state STD→ | Submit other option prices on a separate form
Additional silencer, state dB(A) at 1 m and/or 7 m | Please provide price or state STD→ | Submit other option prices on a separate form
High chimney for exhaust, state height and materials | Please provide price or state STD→ | Submit other option prices on a separate form
(ATS) Automatic Transfer Switch | Please provide price or state STD→ | Submit other option prices on a separate form
Over speed protection | Please provide price or state STD→ | Submit other option prices on a separate form
Manual transfer switch | Please provide price or state STD→ | Submit other option prices on a separate form
External fuel tank with pipes including min.. 10 meter non-corrosive material and fittings, state volume of tank and material | Please provide price or state STD→ | Submit other option prices on a separate form
Slow moving trolley/trailer | Please provide price or state STD→ | Submit other option prices on a separate form
(AMF) Automatic Mains Failure Power generation set | Please provide price or state STD→ | Submit other option prices on a separate form
Automatic main circuit breaker | Please provide price or state STD→ | Submit other option prices on a separate form
Installation instructions and eventual. drawings, other languages | Please provide price or state STD→ | Submit other option prices on a separate form
Change over switch positions for: 1) Mains 2) Off 3) GENERATOR SET | Please provide price or state STD→ | Submit other option prices on a separate form
Automatic main circuit breaker | Please provide price or state STD→ | Submit other option prices on a separate form
Operators and maintenance manual, other languages | Please provide price or state STD→ | Submit other option prices on a separate form

## Lot 36 200 kVA 40% Ground
Bidder name:
Make and model:
Lot 36. 200 kVA PV 40 % Ground or flat roof mounted
HYBRID PV SOLAR/DIESEL GENERATOR SET SPECS | UNOPS REQUIREMENTS | Bidder: Compliant/Non-compliant to UNOPS requirements? Please mark YES/NO in this coloumn. Not indicating YES/NO in this column may render your bid non-compliant. | Bidders are required to provide information in this column on the specifications of their bid to demonstrate compliance to set specifications. Not providing specifications under this column may render your bid non-compliant.
Complete Hybrid PV solar/diesel generator set for autonomous operation, including PV solar power array, battery package, inverter and charge controller. Diesel engine, alternator, control panel with monitoring gauges/indicators, starting equipment, fuel tank as well as other accessories. Charger to charge battery package by diesel gen set and PV solar system interface between diesel gen set and PV solar power unit for a smooth operation for the two energy sources in conjunction, automatically without any manual intervention. Factory test certificates must be included and must be in accordance to internationally recognised standards. Suitable for tropical conditions. | Comply and state → | Yes / No
KEY DATA
Make | Please state →
Model | Please state →
Country of origin | Please state →
DIESEL GEN SET
Rated power output, min. 200 kVA | Comply and state → | Yes / No
Power factor: 0.8 | Comply and state → | Yes / No
Rated power output, 160 kW, min. | Comply and state → | Yes / No
Voltage, 220/230/240 and 380/400 V | Comply and state → | Yes / No
Phase: 1 and 3 | Comply and state → | Yes / No
AC frequency, 50/60 Hz | Comply and state → | Yes / No
Speed: rpm 1500 or 3000 or other | Please state →
Prime power according to ISO 8528 or equivalent, i.e. power available at variable load with no limitations on hours of operation and capable of min. 10% overload for min. 1 hour in any 12 hours. | Comply and state → | Yes / No
Prime rating of min. the stated output rating at Normal Temperature and Pressure conditions (NTP). Please state | Comply and state → | Yes / No
Derating information (temperature, altitude and humidity), please state | Please state →
Engine
Make | Please state →
Model | Please state →
Engine power output, kW at rpm: | Please state →
Fuel: Diesel | Comply and state → | Yes / No
Cooling, liquid or air or combined, suitable for tropical conditions | Please state →
Speed governor, state type | Please state →
Exhaust with suitable piping and residential silencer | Comply and state → | Yes / No
Noise level, dB(A) at 1 m (silencer fitted) | Please state →
Fuel consumption at 75% load: L/hour | Please state →
CO2 emissions at 75% load: g/hour | Please state →
Mounted on anti-vibration mounts | Comply and state → | Yes / No
ENVIRONMENTAL
EU Non-road emissions regulations schedule, e.g. EU STAGE II, III A, III B, IV. US Non-road and stationary emissions regulations to Tier 1,2,3,4 or equivalent. Please state. | Comply and state → | Yes / No
Alternator
Make: | Please state →
Model: | Please state →
Brushless type | Comply and state → | Yes / No
Cooling, liquid, air, other | Please state →
Protection class min. IP 23 | Comply and state → | Yes / No
Suitable AC power outlets protected by circuit breaker (state type) | Comply and state → | Yes / No
Insulation to min. IEC 60085 - >155 ° C - (F) or equivalent | Comply and state → | Yes / No
Voltage regulator | Comply and state → | Yes / No
Standard accessories
Fuel tank. Integrated or separate, suitable for continuous operation of min. 8 hours at rated capacity. State capacity, litres. Fuel level gauge. Including all necessary pipework, connections etc. Possibility for connection to external tank. | Comply and state→ | Yes / No
Low oil pressure protection, automatic shut down | Comply and state → | Yes / No
Over heating protection | Comply and state → | Yes / No
Overload protection | Comply and state → | Yes / No
Emergency stop | Comply and state → | Yes / No
Electric starter with key and battery | Comply and state → | Yes / No
Min. Voltmeter, ammeter, hour meter, Hz meter, water temp gauge/indicator (where applicable) | Comply and state → | Yes / No
Earthing/grounding facility | Comply and state → | Yes / No
PV SOLAR POWER SYSTEM STANDARD ARRAY NOMINAL MIN. 64.0 kWp. Battery pack 160 kWh. For Ground or flat roof mount
PV solar array
Make and model: | Please state →
Array kWp, min 40 % of diesel generator set max output which is 200kVA/160kW, hence = 64.0kWp min. | Comply and state→ | Yes / No
PV panels, total surface covering, m2 | Please state →
Nominal power output each panel, kWp | Please state →
Isc array, A (Amp) | Please state →
Certifications: Any one or more of IEC61215, UL1703 or equivalent | Comply and state → | Yes / No
Charge controller
Make and model: | Please state →
Type: MTTP | Comply and state → | Yes / No
Certifications. Any one or more of EN60730-1/2-11, 55022, 61000-4-27374/5/6 or equivalent | Comply and state→ | Yes / No
Capacity: Isc array +20%, min. | Comply and state→ | Yes / No
Inverter
Make and model: | Please state →
Capacity, A (Amp): Min. equivalent to max load | Comply and state→ | Yes / No
Pure sine curve | Comply and state → | Yes / No
Certifications: Any one or more of EN50178, 62040, 60950, 61000-2/3/6, EN60529, 50438 or equivalent | Comply and state → | Yes / No
Battery package
Make and model: | Please state →
Capacity: Min. equivalent to hybrid diesel gen set full load - 24 kW - for 1 hour = 160 kWh. | Comply and state→ | Yes / No
Battery type: LiFePo4 | Comply and state→ | Yes / No
Certifications,: Any one or more of UL1642, IEC62133, 61000-6-3 or equivalent | Comply and state→ | Yes / No
PV panel racks, brackets, cables, fittings etc.
PV panels racks for Ground or flat roof mount. | Comply and state→ | Yes / No
All cables, junctions, contacts, breakers, earthing spears, fittings, screws, nut and bots etc included | Comply and state → | Yes / No
Installation
The system must be plug and play. Inverter, charge controller, battery package, battery charger must be pre-installed and wired either inside one common Hybrid system cage or in a separate cabinet, in order to easily connect the PV array and the local installation. All cables for establishing the PV array must be readily available with pre-installed connections and clearly marked in a way that no mistakes can occur. | Comply and state → | Yes / No
Other
Lifting points for handling | Comply and state → | Yes / No
Installation instructions, drawings, photos, brochures etc. English/French/Spanish | Comply and state → | Yes / No
Operators and maintenance manual, English/French/Spanish | Comply and state → | Yes / No
Tool kit | Comply and state → | Yes / No
Basic maintenance kit, engine: Min. 4 x oil filters, 2 x air filters, 2 x fuel filters | Comply and state → | Yes / No
Dimensions, L x W x H, mm | Please state →
Weight, dry, entire hybrid system incl. Battery package and all PV panels, cables, brackets etc etc.: kg: | Please state →
WARRANTY
Diesel Generator set: 2 years/2500 hours of operation which ever occur first. PV panels: Min. 10 years. Min. 90% performance guarantee at 10 years. Min. 80% performance guarantee at 20 years. Battery package: Min. 5 years. Inverter/charge controller/charger: Min. 4 years. Other equipment: Min. 2 years | Comply and state → | Yes / No
Sustainability
The bidder must demonstrate that its organisation has an environmental management system in place which as a minimum shall submit at least one or more of the following : the environmental policy principles of the organisation; the management measures and procedures taken or that will be taken to assess, monitor, measure and mitigate environmental impacts of the business processes/products associated with the execution of the contract; how attention is paid to the awareness and training/competency of employee(s) and supplier(s) with regard to dealing with the environmental aspects relevant to this bid; and that compliance with the environmental legislation applicable to the required performance(s) is guaranteed, ISO 14001 certificate, EMAS or an equivalent certificate | Comply and state → | Yes / No
The bidder shall provide documentation which outlines their approach to ensuring equal opportunity, diversity and inclusion within their organisation (e.g. equal pay policy, parental leave, ratio of females/males employees, % of female in management positions, grievances disaggregated by gender, transparency of promotion criteria, sexual harassment policies) | Comply and state → | Yes / No
Mandatory Options
Diesel engine spare parts & maintenance kit for min. 2500 hours of operation | Mandatory | enter prices on Form C: Price Schedule
Sound insolating and water proof canopy (max. 70 dB(A) at 7 m) | Mandatory | enter prices on Form C: Price Schedule
Work shop manual | Mandatory | enter prices on Form C: Price Schedule
Spare parts catalogue | Mandatory | enter prices on Form C: Price Schedule
60 Hz version of Generator set, please enter any surcharge to the std 50 Hz version offered above | Mandatory | enter prices on Form C: Price Schedule
Suggested Options
Heavy duty air filter for dusty conditions | Please provide price or state STD→ | Submit other option prices on a separate form
Heavy duty fuel filter/additional fuel filter in line with original | Please provide price or state STD→ | Submit other option prices on a separate form
Additional silencer, state dB(A) at 1 m and/or 7 m | Please provide price or state STD→ | Submit other option prices on a separate form
Emission control installation beyond standard norm, state emission norm (EU, US, other) | Please provide price or state STD→ | Submit other option prices on a separate form
High chimney for exhaust, state height and materials | Please provide price or state STD→ | Submit other option prices on a separate form
(ATS) Automatic Transfer Switch | Please provide price or state STD→ | Submit other option prices on a separate form
Over speed protection | Please provide price or state STD→ | Submit other option prices on a separate form
Manual transfer switch | Please provide price or state STD→ | Submit other option prices on a separate form
External fuel tank with pipes including min.. 10 meter non-corrosive material and fittings, state volume of tank and material | Please provide price or state STD→ | Submit other option prices on a separate form
Slow moving trolley/trailer | Please provide price or state STD→ | Submit other option prices on a separate form
(AMF) Automatic Mains Failure Power generation set | Please provide price or state STD→ | Submit other option prices on a separate form
Automatic main circuit breaker | Please provide price or state STD→ | Submit other option prices on a separate form
Installation instructions and eventual. drawings, other languages | Please provide price or state STD→ | Submit other option prices on a separate form
Change over switch positions for: 1) Mains 2) Off 3) GENERATOR SET | Please provide price or state STD→ | Submit other option prices on a separate form
Automatic main circuit breaker | Please provide price or state STD→ | Submit other option prices on a separate form
Operators and maintenance manual, other languages | Please provide price or state STD→ | Submit other option prices on a separate form