## Title
Republic of Yemen Ministry of Water and Environment
Consultancy Services for the Preparation of a Detailed Engi- neering Design and Technical Tender Documents for the “Aden Wastewater Network Rehabilitation Project’’
PK-I-CRATER
Bill of Quantities

## Contents
PK-I-CRATER
Table of Contents
Preamble ................................................................................................................... | 1
Bill No.1: Preliminary .................................................................................................. | 10
Bill No.2: Force Main Pipeline .................................................................................... | 12
Bill No.3: Crater pump Staion ..................................................................................... | 14
Bill No.4: Facilities Building ..................................................................................... | 30
Bill No.5: Transformer Room ...................................................................................... | 33
Bill No.6: Guard Room ............................................................................................... | 36
Bill No.7: Maintenance Area....................................................................................... | 39
Bill No.8: Store Room................................................................................................. | 42
Bill No. 9 : Yard and Fence ......................................................................................... | 45
Bill No.10: Generator Room........................................................................................ | 50
DAYWORKS .............................................................................................................. | 54
Summary ................................................................................................................... | 57
PREAMBLE
A. GENERAL
1. The general directions and descriptions of work given in the specification and the drawings are not necessarily repeated in the bill of quantities. Reference must be made to the specification and the drawings for such information which shall be deemed to be included in the bill of quantities.
2. The tendered price for each item will be paid only when all the works included and covered by the item is 100% complete, and checked and accepted by the Engineer in writing. The commissioning works, however, will be paid in two parts as noted in the commissioning item clause.
3. The Bill of Quantities is not and does not purport to be exhaustive or explanatory of all the obligations and duties of the Contractor and in making his Bid and in pricing the items of the Bill of Quantities the Contractor must cover himself and will be deemed to have covered himself for:
a. All services and materials which according to the true intent and meaning of the Contract Documents may be reasonably inferred as necessary for the carrying out the Works shown on the Drawings in accordance with the best construction, management and professional practices, whether expressly mentioned therein or not. b. All duties, obligations, liabilities and responsibilities which any of the Contract Documents place upon the Contractor in conjunction with or in relation to this Contract.
4. The Bill of Quantities shall be read and understood in conjunction with this Preamble and all Contract Documents, including the Conditions of Contract, the Specifications and the Drawings.
5. The Contractor shall insert against each item in these Bill of Quantities such rates to cover all requirements indicated in this Preamble. Items against which no price is entered are to be considered as covered by other B.O.Q. items.
6. The quantities given in this Bill of Quantities are approximate. Such quantities shall not be considered as the actual and correct quantities of the Works to be executed by the Contractor in fulfillment of his obligations under the Contract. Actual quantities executed may be greater or less than those in these Bill of Quantities and entire items may be deleted completely.
7. All measurements in this Bill of Quantities are taken strictly net and they will form the basis for payment. No claims for extras based upon other methods of measurement shall be entertained. No allowance shall be made for cutting, waste or bulking of materials.
8. All measurements of the executed work called for in the Contract shall be based on the unit price stated in the Bill of Quantities and made according to the specifications. Any work done the Contractor, but not called for in the Contract or not requested in writing by the Engineer, shall not be included in the measurement.
9. “Supply and Install” or “Supply and Installation of” or similar phrases used in these Bill of Quantities shall include for the provision, hoisting, placing in position, welding, drilling, bolting, jointing materials, shuttering, building in, boxing out, making good, cutting, waste, transport, and incidental work to the items concerned and its surroundings.
10. “Supply” used in these Bill of Quantities means that the Contractor is to provide and deliver the items to the location as directed and supposed necessary to fulfill the Contractor obligation and required by the Contract document.
11. Unless otherwise stated in the description of the items therein after, payment for Lump Sum (L.S.) items shall be made where appropriate by means of installments in the Interim Certificates. The installments shall be assessed by the Engineer, based on the extent to which the works or obligations are carried out by the Contractor in relation to the total extent of the works or obligations covered under a Lump Sum item.
12. In case of discrepancies between the total price and the multiplication of quantity with the unit price, the unit price is deemed correct and the total price will be adjusted.
13. In no case should item(s) be measured under more than one item in this Bill of Quantities.
14. Fixed rate items: for any item designated as fixed rate item, the Contractor is not entitled for any claim due to changes in executed quantities, either increased or decreased than quantities stated in BOQ.
15. “Provisional Sum” means a sum included in the Contract and so designated in the Bill of Quantities for the execution of work or the supply of goods, materials, or services, or for contingencies, which sum may be used, in whole or in part, or not at all, at the direction of the Engineer, who shall consult with the Employer prior/ to the issue of an instruction to this expenditure. The Contract Price shall include only such sums in respect of the work, supply reinstatement or other services to which such Provisional Sums relate as the Engineer shall approve or determine in accordance with the Bill of Quantities items.
The item Contractor's overhead and profit shall be filled by tenderer as an amount forming percentage of total provisional sum and will be paid as percentage of actual work done.
The Employer reserves the right to reject any unit cost which in his opinion and/or the opinion of the Engineer is unreasonable.
Values of the B.O.Q shall be logical, and satisfactory. These values shall reflect the fact that they were evaluated carefully.
The unit rates provided in the B.O.Q shall include the cost of the following:
i. All services and materials which according to the true intent and meaning of the Contract Documents may be reasonably inferred as necessary for carrying out the Works shown on the Drawings and described in the Specifications in accordance with the best construction, management and professional practices.
ii. All duties, obligations, liabilities and responsibilities which any of the Contract Documents place upon the Contractor in conjunction with or in relation to this Contract, and
iii. Provision of materials, hoisting, placing in position, welding, drilling, bolting, jointing materials, shuttering, building in, boxing out, making good, cutting, waste, transport, and incidental work to the items concerned and its surroundings.
iv. Labour, machines, equipment, profit, overhead and all administrative.
16. If the Employer deems it suitable to take-over any excess pipes and fittings at project completion, the Contractor shall be paid the Cost at factory, Insurance and Freight (CIF) price plus 15 per cent of the CIF price for these materials. The Employer reserves the right to reject any CIF rate which in his opinion and/or the opinion of the Engineer is unreasonable. If no agreement is reached, material shall be exported or the Contractor shall pay the customs and tax duties on such material.
17. The unit rates listed in this Bill of Quantities shall be comprehensive and include but not limited to the following:
i. All obligations imposed by the Contract.
ii. All costs in connection with Supervision and Quality Control of the Work.
iii. Labour and all associated costs.
iv. All costs associated with complying with the requirements of the Technical Specifications, Drawings, Including, but not limited to the following:
a. Quality Control of the works as required under the technical Specifications
b. Coordination and liaise with Authorities and the coordination required with Local Water and Sanitation Corporation and all authorities having jurisdiction.
c. Protection of and interference with existing facilities as required in the Technical Specifications.
d. Provision of First Aid supplies Cabinets as required under the Technical Specifications.
e. Temporary Utilities as required under Section 1 of the Technical Specifications.
f. Provision of progress schedule, equipment and materials orders schedule, working drawings, record drawings, shop drawings, layout and installation drawings, certified shop test reports, samples, and operation and maintenance manuals, as required under the Technical Specifications including Section 1-Submittals requirements.
g. Compliance with the requirements of the following sections of the Specifications:
 Division 1- Site Access and Storage.  Division 1- Coordination And liaise with Authorities  Division 1-site access, Traffic Control.
v. All costs associated with compliance with Statutes and Regulations.
vi. Supply of materials and goods, third party testing and certificates transportation, storage, installation, operation, and coordination with all authorities having jurisdiction over the Works or Part of the Works.
vii. Provisions of equipment, tools, and plants.
viii. Losses of materials, tools and plants.
ix. Temporary works such as: diversion of traffic, access roads, de-watering, and cofferdams
x. Overheads and profit.
xi. All costs associated with: Protection of the works, traffic control, maintenance of public and private roads, drying out the works, control of noise, dust and pollution control.
xii. Management, superintendence and associated costs.
xiii. Costs associated with interference with traffic and protection of adjoining properties.
xiv. Identification plates, discs, labels, and key charts both in Arabic and English.
xv. Spare parts as required under the Technical Specifications..
xvi. Testing of the works and commissioning including the provision of Instruments, applicants, and cost associated with the Engineer and /or Employer attendance of such tests.
xvii. Provision of Operation and Maintenance (O&M) Manuals in Arabic and English.
xviii. Protective coatings of pipes and equipment.
xix. Colour coding and marking out.
xx. Assembly, fitting and jointing components.
xxi. Excavation, bedding and backfill for cables, if applicable.
xxii. Coordination and follow up with local electricity corporation regarding power connection to all sites.
xxiii. Confirmation of all geotechnical findings in the geotechnical report for all sites.
xxiv. Associated costs of defect liability period, including cost of repairs, replacing defected materials and equipment and all rectifying works.
xxv. All direct or indirect costs associated with the following items. The listing of these items for Tenderer’s overhead costs shall not be deemed to be complete. Tenderer shall include all hidden and unforeseen expenses, whether they are listed or not in this Bill of Quantities. Contractor shall have no claim to any other direct or indirect cost, whether listed or not.
 Any temporary works necessary to maintain traffic.  Mobilization, demobilization and reinstatement.  Materials, wages, bonus and travel expenses.  Transportation.
 Medical welfare, importation, repatriation, boarding and lodging payments for employees.  Necessary tools, equipment and plant.  Scaffolding and other temporary works for both civil engineering and electro- mechanical works.  Safety measures.  General cleaning and complementary works.  Insurance, bonds and similar expenses.  Supplying of temporary services such as water, drainage, electricity and telephone.  Testing and third party certificate.  Contractor’s general overheads and profit.  Establishment of Contractor’s and sub-Contractor’s temporary site office complex, work yards, stores, project signboards, car-parks and hoarding.  Repair of the works during the maintenance period.  Civil works such as excavation, backfilling, supports, frames, making holes, openings … etc.  The prices of the valves shall include paddle flange, flange adaptor and all necessary fittings.  Chambers and all related accessories.  The prices of the pipes shall include all fittings.  The final dimension of the gates shall be determined by the Contractor.
In case some or all the above listed costs are quoted as a separate item (e.g. "Contractor’s Preliminaries") it shall be clearly shown and specified.
18. The unit prices for all items shall be in USD
B. BILL OF QUANTITIES ITEMS
Mobilization NO SPECIFIC ITEM IN THE B.O.Q. WILL COVER THE MOBILIZATION. THE COST OF MOBILIZATIONSHALL BE INCLUDED IN AND COVERED BY THE LISTED ITEMS’ RATES AND VALUES IN THE B.O.Q. Mobilization will include but not limited the cost of insurance premiums, transporting staff and equipment of the Contractor to the project area, Contractor’s temporary housing, transportation, Contractor’s offices and sheds, temporary storage facilities and containers, installation and testing of equipment, costs associated with starting construction, Performance Bond, Bank Guarantee, Progress Photographs, Construction Video, and Project Signboards, administrative cost, and demobilization, …etc.
1.1 Engineer's Offices This Item will include the cost of mobilization, furnishing, maintenance and cleaning, and demobilization of Engineer’s Site Office complete as required under Division1 of the Technical Specifications, including all equipments, telecommunication including cellular phones and land lines, furniture, providing services, all as specified in the specification. All equipment and appliances, i.e. computers, phones, printers….etc. will be the Client property of the Client at the end of the project. Payment for the Engineer’s Offices will only be made on one payment upon fully mobilizing and furnishing the office, as specified.
1.2 Engineer's Offices Services and Rent This item will include the provision of payment for offices rent, services, water, electric power, air conditiong maintenance, internet, cellular phones, landlines, stationary, drinking water with coolers, beverages and all other consumable items and materials for office equipment and furnishings. Payment for the Engineer’s Offices services will only be made on a monthly basis, upon providing the services for the office, as specified.
1.3 Engineer’s Cars This item will include the provision of two new cars one salon and the other Pickup both of not les 2000 cc airconditioned. The car should be comprehensive insured at registered company against all accedents. At the end of the project the cars will become the Client Property. Payment for the Engineer’s Offices will only be made on one payment upon fully mobilizing the cars, as specified.
1.4 Engineer’s Cars services (two cars) It includes providing required fuel, oil, service, maintenance and cleaning. During the project period. The cars will be comprehensive insured at registered company against all accedents. Payment for the Engineer’s Cars services will be made on a monthly basis.
1.5 Engineer’s Car services (one car) It includes providing required fuel, oil, service, maintenance and cleaning. During the defect laibility period. The car will be comprehensive insured at registered company against all accedents. Payment for the Engineer’s Car services will be made on a monthly basis.
1.6 Training of the Client Staff This item will provision training for the client staff by professional personnel of mechanical and electrical works. The training will include installation, operating, testing, maintaining in theoretical and practical training for all supplied machinary and equipment, i.e. pumps, valves, electrical appliances and boards ……etc.
PIPELINES WORKS
2.1 Supply and install HDPE Pipes The pipes provided under this item will be measured for payment on a unit price basis for each linear meter supplied, installed, tested, and backfilled in the field. The length paid will be the distance measured along the centreline of the pipe, and shall not include the interconnections between new pipelines and existing pipelines. Interconnections will be measured and paid for separately. The stated unit rate for this item shall include, extra over afore mentioned 1 to 15 clauses, the following:
a. Supply of HDPE pipes with jointing by butt fusion, transportation from the project storage yard to site. Survey and layout, Unclassified excavation in any kind of ground surface, saw cutting of asphaltic surfaces and disposal of excavated material, backfilling to existing ground level, shoring. Dewatering and disposal of water, disposal of excavated material, dust and mud control, repair and restoration of damaged existing utilities to the satisfaction of the Engineer and utilities having jurisdiction over the damaged utilities, traffic control, coordination with government and other authorities having jurisdiction over the works or part of the works, shop drawings, as-built drawings, temporary utilities.
b. Supply and installation of required fittings such as Tees, Bends, reducers, collars, adaptors…..etc. as specified in the Technical Specifications.
d. Testing of materials and workmanship including pressure testing.
e. Hydrostatic Pressure testing and water for pressure testing.
f. Reinstatement of pavement layers to their original condition shall include re-cutting existing pavement, supply and compaction of granular subgrade and base course, supply placement and compaction of asphalt concrete binder and wearing courses as specified and shown on the drawings
g. Restoration of demolished median islands sidewalks to their original condition including supply and placement of reinforcement, Class C30 and C20 concrete, concrete tiles and curb stone, expansion joints filler and accessories, top soil, plants, and shrubs. All works of this item shall be as shown on the Drawings and as specified, in the Particular Technical Specifications.
2.2 Remove the Existing Pipeline The work under this item will measured for payment based on unit price, paid when part of line removed from its location and stock at places agreed by the Client. The stated unit rate for this item shall include extra over afore mentioned 1 to 15 clauses the following:  Unclassified excavation, saw cutting of asphaltic surfaces and disposal of excavated asphaltic material, and piling excavated materials on site at agreed areas. Excavation down to the top of the existing pipeline, and exposing the pipes to be ready for cut and removed.  Dewatering of the ground water and shoring the trench sides  Disconnecting the existing line from both side.  Cut the pipeline in suitable lengths and remove out of the trench.
2.3 Supply and install Air Release Valves Air release valves will be measured for payment on a unit price basis per air release valve. The unit price tendered for this item shall include, extra over afore mentioned 1 to 15 clauses, the following: a. unclassified excavation and backfilling b. Supply and installation of the air release valve, complete with gaskets, bolts and accessories. c. Supply and installation the required fittings, Tee, spool pipes and wall pipes with puddle flange. d. Supply and installation of the riser distance piece if needed e. Supply and installation of the Isolation valve f. Testing. g. Ventilation pipe. h. Construction of the chamber including unclassified excavation, backfilling surface reinstatement, supply and placement of Class C30 and C20 concrete for the chamber and supports, formwork to get fair-faced concrete, reinforcement steel, cover and frame, steps and crushed stone or gravel. All works of this item shall be as shown on the Drawings and as specified in the Particular Technical Specifications.
2.4 Concrete anchors, thrust blocks and encasements Concrete anchors, thrust blocks and encasements shall be measured for payment on a Cubic Meter unit price basis for each m3 placed in the field and measured as per approved shop drawings submitted by the Contractor.
The price shall include the supplying, testing, conveying, placing, and finishing of concrete, unclassified excavation, backfilling, bedding and formwork to all surfaces, reinforcing steel, curing concrete, supplying and installing piles.

## ABBREVIATIONS
The work included in this item shall be as shown on the Drawings and as specified in the Particular Technical Specifications.
C. ABBREVIATIONS
The following abbreviations are used in the Bill of Quantities
Abbreviation | Meaning
DI | Ductile Iron
HDPE | High Density Polyethylene Pipe
PN | Nominal Pressure in Bar
Dia. | Diameter
mm | Millimetre
L.M | Linear Meter
m2 | Square Meter
m3 | Cubic Meter
EA. | Each
USD | United States Dollar
L.S. | Lump Sum
No. | Number
B.O.Q | Bill of Quantities
kW | Kilowatt
DWG. | Drawing
P.S | Provisional Sum
CIF | Cost at factory , Insurance and Freight

## PRICE ANALYSIS LISTS
D. PRICE ANALYSIS LISTS (PAL)
1. The Tenderer shall provide the unit rate of all items listed in the BOQ. 2. The unit rates listed in the PRICE ANALYSIS LISTS (PAL) may be considered as the basis for establishing reasonable cost of extra work or deduction for work not done, or reducing lump sum items or change orders. 3. The Employer reserves the right to reject any unit cost which in their opinion and /or the opinion of the Engineer is unreasonable.
This a sample table, the bidder shall add more spaces to insert all items of the BOQ
Item No. | DESCRIPTION | Unit | Excavation including asphalt cut & remove Bedding and Embedment | Pipes & laying & Fittings & But fusion jointing | Dewatering | Shoring | Testing and flushing | Backfilling & Reinstatement of pavement | Overhead & profit | Total
2.1 | Pipelines works
2.1.1 | HDPE Pipelines
| DN560 mm OD | L.M
2.1.3 | Connect with Connection 1 | No
2.1.4 | Connection to Pump station | No
2.2 | Air Release Valves
2.2.1 | Air release Valves
2.3 | On 560 mm OD | No
| Concrete Encasement | M3
E. BILL OF QUANTITIES
The following forms include the Bill of Quantities that shall be used in bidding this contract.

## Bill 2
Bill No.2 : Force Main Pipeline
Item No. | Description | Unit | Quantity | Unit Rate USD | Total Amount USD
2.1 | Force Main Pipeline:
2.1.1 | HDPE Pipelines PE100
Supply and Install PN-10, SDR-17 HDPE Pipes all to the approval of the Engineer, in accordance with the Drawings, Specifications and set out in the BOQ preamble.
a. | DN 560mm OD at average depth 2.2 m | L.M | 3500
2.1.2 | Remove Existing Pipeline (Fixed Rate)
Remove the existing Ductile pipeline to replace it by the new pipeline of HDPE. As per the BOQ preamble and specification.
| DN 500 mm | L.M | 100
2.1.3 | Connect to Connection 1
| Connect the pipeline of PE of 560 mm OD with pipeline of PE of 710mm OD at (Connection 1) including flanges, colors, as per Drawings and Specifications. | No. | 1
2.1.4 | Connect to Crater Pump Station
| Connect the pipeline of PE of 560 mm OD with the pump station outlet including the flanges, colors, as per Drawings and Specifications | No. | 1
Sub-total Carried Forward
Sub-total Brought Forward
2.2 | Air Release Valves:
2.2.1 | Air Release Valves (PN10)
Supply, storage, Installation on pipelines, testing and commissioning of air release valves including valves, Construction of valve's chamber, in accordance with the preamble, Specifications, and Drawings and complete the work properly subject to the approval and satisfaction of the Engineer.
a | DN 100 mm double orifice air valve on PE lines of DN560mm | No. | 9
2.3 | Concrete Encasement
supply and cast concrete encasement at location shown on Drawings, this to include, excavation, providing all materials including concrete, steel reinforcement, forms, …etc. and manpower, machinery to complete the works as per Specifications and Drawings.
2.3.1 | Concrete type A (250kg/cm2) | M3 | 4
2.3.2 | Concrete type C (150kg/cm2) | M3 | 0.6
2.4 | The Signboard of the Project Supply and installation of a metal plate that will be fixed on a concrete layer on the nearest asphalt road, the signboard should list the project’s name, the name and logo of the donor and UWSSP, according to the drawings, specifications, and as instructed by the supervising engineer. | No. | 1
Subtotal of Bill No. 2 Carried to Summary

## Bill 3
Bill No.3 : Crater Pump Station
Item No. | Description | Unit | Quantity | Unit Rate USD | Total Amount USD
important notes | A. The Contractor has to visit the site and examine the situation of all structures, both from inside and outside, and be fully aware of the works to be done in terms of nature, quantities, dimensions, and be aware of the existing facilities and equipment that may has affect on efforts to execute the works.
B. If in opinion of the Engineer/Client Drawings or method statement or both are needed for certain works, the Contractor shall prepare them and get the approval of the Engineer/Client before executing the works.
C. The items listed hereunder will be in lump sum and the Contractor is not entitled for any claim raise due to that in regard to quantities, nature, dimensions of works to be executed.
A. | Civil & Architectural Works:
3.1. | Collect and Remove from all structures and yard all scrap pieces of pipes, fitting, pumps, rails, screens...etc. and handed to the Client at places of his choice. | L.S | 1
3.2 | Clean up inlet channel and wet well by removing & collecting all rubbish & wastes then dispose and transport it out of the site to places accepted by local authorities. | L.S | 1
Sub-total Carried Forward
Sub-total Brought Forward
3.3 | clean up of all concrete walls , floors and ceiling removing all existing ceramic tiles, dust, mud, grease, oil, stains ….etc. of the basement and ground floor rooms, and wet well and disposing it out of site , then repair any damages, provide and apply epoxy paint as per Specifications provide and apply 4mm damp proof torch applied membrane wet well base and 2 m above it on walls and base.
3.3.1 | Epoxy paint at Basement Room floor, walls | M2 | 330
3.3.2 | Epoxy paint at Ground Floor Room floor and walls | M2 | 230
3.3.3 | 4mm Damp Proof Torch applied membrane at Wet Well base and walls | M2 | 60
3.4 | Remove all doors, gates, windows, louvers and replace them with new ones of the same sizes and material except the windows and louvers will be of aluminum including repairing the concrete opening and make it neat to receive the metal work as per Specifications .
3.4.1 | SD01 Steel Door | No. | 2
3.4.2 | WD01 Window | No. | 6
Sub-total Carried Forward
Sub-total Brought Forward
3.5 | Clean up all ungalvanized metal works (other than piping) i.e. stairs. Rails, cover screens, leaders By sand blast exposing clearly the metal and provide and apply oil paint as per Specifications, galvanized rails
3.5.1 | Inside Pumps Room Stairs | LM | 12
3.5.2 | Inside Pumps Room Opening Cover Screens | M2 | 10
3.6 | Clean up all galvanized metal works rails, leaders screens exposing clearly the metal, relacing damaged and missing parts by new rails of the same nature and quality of the existing as per Specifications, galvanized rails
3.6.1 | Rails Inside Pumps Room | L.M | 8
3.6.2 | Rails at Inlet Channel | L.M | 24
3.6.3 | Rails at Wet Well | L.M | 20
3.6.4 | Wet Well Screen Cover | M2 | 30
3.7 | Clean up all external stone wall by sand blast, clean and repair concrete damaged parts of the walls, roof parapet and sheds, provide and apply emulsion paint on the concrete parts as per Specifications. | M2 | 165
3.8 | Remove all layers of roofing exposing the concrete roof & repair any damages, then provide and apply roofing including concrete screed with minimum 5 cm thick inclined towards roof drain, as per Specification. | M2 | 115
Sub-total Carried Forward
Sub-total Brought Forward
3.9 | Concrete Blocks
Providing and cast in place concrete class30, including providing all required materials including steel reinforcement, forms, manpower, and machinery to complete the work as per Specifications and Drawings.
3.9.1 | cast blocks of 1x1x1 m dimensions with lifting hook | No | 18
B. | Mechanical Works:
3.1 | SPARE PART FOR Wastewater Pumps
supply, testing and commissioning wastewater pumps spare part and as per Drawings and the Technical Specifications and the price include:
a | mechanical shaft seals | No | 6
b | wear rings set | No | 6
c | set of bearings, bolts, nuts and washers | No | 6
d | O-rings and gaskets | No | 12
e | pump shaft | No | 3
f | pump impeller | No | 3
g | floats switches | No | 4
h | fuses set | No | 1
Sub-total Carried Forward
Sub-total Brought Forward
3.11 | Wastewater Submersible Dry pumps/Vertical
supply, install, testing and commissioning wastewater Submersible Dry pumps/Vertical and the pumps should be supplied with cooling jacket and control panel with electrical combatable pumps cable not less than 20m, pump base suitable to install on existing base and as per Drawings and the Technical Specifications and the price include:
a | wastewater pumps (Two duty and one stand by) with flow 124 l/s at 29.1 m head | No | 3
b | floats switches valves with wire cable and stainless steel chain | No | 4
c | pressure switch | No | 1
d | pressure gauges | No | 8
e | ductile iron pipes inside pumping station with supports | L.S | 1
f | ball check valves with 300mm diameter | No | 3
j | gate valves with 400mm diameter | No | 3
h | gate valves with 300mm diameter | No | 3
3.12 | Epoxy Coated Steel Manual Screen
| Supply and install Epoxy Coated Steel Manual Screen and the price include all bolts,nuts, civil works and all necessary work in accordance with the Drawings and the Technical Specifications. | No | 1
Sub-total Carried Forward
Sub-total Brought Forward
3.13 | Automatic Electrical wastewater Screen
supply, install, testing and commissioning Automatic wastewater screen and the price include drive unit, belt, control panel, electrical cable between control panel and screen, supports, civil works and all necessary work in accordance with the Drawings and the Technical Specifications.
a | Automatic wastewater screen | NO | 1
b | spare sets of screening elements and one spare motor | NO | 1
3.14 | Penstocks
supply, install, testing and commissioning wastewater stainless steel penstock with height as per Drawings and the price include control panel, float switch with wire, electrical connections, supports, rods and all civil works, electricalworks, mechanical works and as per Specifications and Drawings.
| Penstock for diameter pipe 600mm | No | 2
3.15 | Drain Pumps:
| Supply, install, testing and commissioning drain Pumps with flow 5 l/s at 10 m head and the price include control panel, electrical cables between control panel and pumps,HDPE pipes from pumps to wet well, float valves, valves, supports and all necessary work in accordance with the Drawings and the Technical Specifications. | NO | 2
Sub-total Carried Forward
Sub-total Brought Forward
3.16 | VITRIFIED CLAY pipe inside pumping station
Supply and Installation of VITRIFIED CLAY extra stengh Class (ES) according to DIN EN 295 Pipes suitable for sewage and the price Including supply, storage, transportation and handling of all pipes, connection to wet well and screen channel for inflow pipe, cutting and connect to existing lines to make a temporary bypass, fittings and accessories (including all types of bends, adaptors, collars, tees, flexible couplings, reducers, blind flanges, dismantling joints...etc.), jointing materials, and all other materials required; excavation at any depth in any kind of soil and rock , repair of any damage of any service at full satisfaction of relevant Service Authority, removal and transport at any distance of excess or unsuitable material, cleaning of sites; laying of pipes including all jointing any ancillary necessary for proper laying and jointing of pipes; supply from any distance placing and compaction of bedding, (sand fill) backfilling and surface reinstatement, including warning tape with ferrous strip and Concrete encasement of pipes in accordance with the Specification; testing and in accordance with the Drawings, the Technical Specifications and set out in the preamble to the BoQs
| 600 mm diameter gravity sewer pipe | LM | 32
Sub-total Carried Forward
Sub-total Brought Forward
3.17 | Air release valves
| Supply, install, testing and commissioning air release valve PN10 with 100mm diameter and the price include gate valve with diameter 100mm before air release valve, TEE, flanges, spool pieces, bends and all fittings and all necessary work in accordance with the Drawings and the Technical Specifications. | NO | 1
3.18 | Isolating valves
Supply, install, testing and commissioning gate valve PN10 and the price include surface box, ductile iron pipes inside chambers, flanges, spool pieces, bends, Tees and all fittings and all necessary work in accordance with the Drawings and the Technical Specifications.
a | isolating valve with 300mm diameter for drain pipe chamber | NO | 2
b | isolating valve with 500mm diameter for bypass chamber | NO | 1
3.19 | Crane
Supply, install, testing and commissioning automatic lifting crane with capacity 5 ton and the price include control panel, electrical connection, I beam, bridges, wheels, trolleys, supports and all necessary work in accordance with the Drawings and the Technical Specifications and as per the pre approval from Engineer
a | Automatic Lifting Crane | NO | 1
b | spare sets of fuses, trolley and electrical cable | NO | 1
Sub-total Carried Forward
Sub-total Brought Forward
3.2 | Centrifugal Roof Fan
Supply, install, testing and commissioning Centrifugal Roof Fan with flow 3000 m3/h at 25mmH2O pressure and the price include control panel, thermostat, electrical connection between control panel and fans, PVC air pipes from fan to pumps room, gravity shutter, supports and all necessary work in accordance with the Drawings and the Technical Specifications.
a | Centrifugal Roof Fan | NO | 1
b | spare sets of impellers, bolts, nuts, gaskets | NO | 1
3.21 | Axial Plate- Mounted Fans
Supply, install, testing and commissioning Axial Plate- Mounted Fans with flow 1000 m3/h at 10mmH2O pressure and the price include control panel, thermostat, electrical connection between control panel and fans, gravity shutter, supports and all necessary work in accordance with the Drawings and the Technical Specifications.
a | Axial Plate- Mounted Fans | NO | 2
b | spare sets of impellers, bolts, nuts, gaskets | NO | 1
Sub-total Carried Forward
Sub-total Brought Forward
C. | Electrical Works:
3.22 | Electrical Panels
3.22.1 | Supply, install, test and commission the following motor control Center (MCC) . The (MCC) shall include main incoming and outgoing circuit breakers, busbars, pumps running meters, 75kw three soft starters, Uninterruptible Power Supply (UPS) for 6 hours, (24 VDC) power supply and charger measuring and metering instruments, isolating transformer, indication lamps, motor monitoring and protection unit ( MMPU), with spare part 10% of protection equipment such as circuit breakers, fuses, relays... etc. . | No. | 1
3.22.2 | Supply, install, connect, test and commissioning exposed distribution boards (DB) 30way, 400V / 3-phase, 50Hz including fixings, enclosure, busbars, circuit breakers, on incoming and outgoing connection and accessories as per Drawings, Specifications and Supervision Engineer. Main MCCB 63A 25 KA 4 pole 400 V 50 Hz M.C.C.B adjustable type. One 200A RCD 30mA 4 pole 400 V 50 Hz -The Enclosure panel shall be weatherproof, corrosion-proof, dustproof with IP55 wall mounted type with enough space for cable termination and glanding. - All Busbar shall be Tinned copper type sized as per standed -The panel shall be provided with phase failer monitor, ampere meter, volt meter, current transformers, selector, control fuses and phase indication lamps. - The main panel shall be Equipped with a lightning protection device (SPD). -The live busbars shall be to be color coded and protected by fixing transparent plastic cover on the busbar. - the existing main cable then to be connected to the new main panel, include all accessories - The offer shall include accessories, cable gland, lugs, panel support,earthing cable and other materials, equipment, machinery, and associated works required for the successful installation | No. | 1
3.22.3 | Supply, install, test and commission automatic transfer switch (ATS) 630A. The price include all needed accessories as per Drawings, Specifications and Supervision Engineer | No. | 1
Sub-total Carried Forward
Sub-total Brought Forward
3.23 | Programmable Logic Controller (PLC)
a. | Supply, install, connect, test and commission all materials for programmable logic controller (PLC) comprising of all telemetry equipment I/O modules, interface modules, Ethernet switch suitable for fiber optic cable, fiber optic patch panel, serial port, interconnection of power and signal cables between the PLCs and the motor control centers, UPS unit, power supply and all necessary material according to Specifications and Engineer's instructions for handing over the works completely clear and in operation condition. Also prices shall include all related civil works needed for installation. must be installed in the PLC panel and all site signals and readings must be viewed *Communication Protocols: The controller shall support Hart protocol and at least one of the following industry standard protocols: - Modbus - Ethernet TCP/IP. - Profibus. - DNP3 * A Laptop shall be used for PLC programming and equipment configuration, all the required programs and software should be installed on the laptop and licensed, the laptop specs must be high. *PLC with Ethernet switch, fiber optic switch and fiber optic patch panel as specified. (including a latop). | No. | 1
Sub-total Carried Forward
Sub-total Brought Forward
b. | HMI (Human Machine Interface): Supply, install, connect, test and commission all materials for HMI (Human Machine Interface) including graphics for the station and control of pumps and valves, some of data which will be viewed on the HMI: • Communication status • Inlet Pressure reading • Outlet Pressure reading • Flow rate • Flow totalizer. • Full control for pumps and valves • Alarm Limits • Pumps trip, pumps status, soft starter signals and control & pumps speed • Over temperature trip for pumps and trips • General trip • Mains available • UPS battery low. | No. | 1
Sub-total Carried Forward
Sub-total Brought Forward
3.24 | Lighting
3.24.1 | Lighting works as a point, price include supply, install, connect, test and commissioning switches, exposed PVC conduits,wires, cables, laying wires & cables in conduits, connection boxes, connecting to distribution board and all needed accessories as per Drawings, Specifications and Supervision Engineer as follow:
a. | Internal lighting point with 3x2.5mm2 cable and PVC conduits. | No. | 23
b. | External lighting point with 3x4mm2 cable and PVC conduits. | No. | 6
3.24.2 | Supply, install, connect, test and commissioning lighting fixtures and all included accessories as per Drawings, Specifications and Supervision Engineer as follow:
a. | Ceiling mounted luminaire 38w LED, 4100 lumen, CRI>80, body extruded aluminum with polycarbonate diffuser, IP65. | No. | 8
b. | Same as above but with emergency kit, 3 hours duration battery. | No. | 2
c. | Wall mounted luminaire 38w LED, 3550 lumen, CRI>80, body extruded aluminum with polycarbonate diffuser, IP65. | No. | 8
Sub-total Carried Forward
Sub-total Brought Forward
d. | Same as above but with emergency kit, 3 hours duration battery. | No. | 2
e. | 8w LED exit sign, non-maintained with battery back up working 3 hours, surfaced mounted. IP65. | No. | 3
f | Wall mounted 150w LED lighting fixture ,21800 lumen, free glare with asymmetrical distribution, CRI≥70, color temperature 4000k, housing in die-cast aluminum with acrylate optic material, IP65. | No. | 6
3.25 | Power Sockets
3.25.1 | Supply, install, connect, test and commissioning sockets, price shall include sockets, wires, cables, exposed conduits, boxes, laying cables in conduits and all included accessories as per Drawings, Specifications and Supervision Engineer as follow:
a. | 13A, 230 volt single socket weather proof IP54. | No. | 4
b. | 13A, 230 volt single socket weather proof IP65. | No. | 3
c. | 16A,400 volt three phase socket weather proof IP54. | No. | 1
Sub-total Carried Forward
Sub-total Brought Forward
3.26 | Power Isolators
3.26.1 | Supply, install, connect, test and commissioning isolators, price shall include Isolators, cables, conduits, boxes, laying cables in conduits and all included accessories , as per Drawings, Specifications and Supervision Engineer as follow:
a. | 400 Amp Isolator, 400 Volt, 4 poles, IP65, housed in thermoplastic/polycarbonate or sheet steel enclosures, Straight Blade, Industrial Grade, Grounding, , Side Wired, Steel Strap. ( for waste water pumps, cable from MCC to pump will be supplied with pump as shown in mechanical BOQ & must be 20m) | No. | 3
b. | 40 Amp Isolator, 400 Volt, 4 poles, IP54, housed in thermoplastic/polycarbonate or sheet steel enclosures, Straight Blade, Industrial Grade, Grounding, , Side Wired, Steel Strap, ( for crane ) | No. | 1
c. | 20 Amp Isolator, 230 Volt, 2 poles, IP65, housed in thermoplastic/polycarbonate or sheet steel enclosures, Straight Blade, Industrial Grade, Grounding, , Side Wired, Steel Strap, ( for submersible pumps ) | No. | 1
d. | 20 Amp Isolator, 230 Volt, 2 poles, IP54, housed in thermoplastic/polycarbonate or sheet steel enclosures, Straight Blade, Industrial Grade, Grounding, , Side Wired, Steel Strap, ( for axial exhaust fans ) | No. | 1
Sub-total Carried Forward
Sub-total Brought Forward
e. | 20 Amp Isolator, 230 Volt, 2 poles, IP54, housed in thermoplastic/polycarbonate or sheet steel enclosures, Straight Blade, Industrial Grade, Grounding, , Side Wired, Steel Strap, ( for centrifugal curb mounted fan ) | No. | 1
f. | 20 Amp Isolator, 230 Volt, 2 poles, IP65, housed in thermoplastic/polycarbonate or sheet steel enclosures, Straight Blade, Industrial Grade, Grounding, , Side Wired, Steel Strap, with epoxy painted steel stand. ( for centrifugal curb mounted fan / to be installed at roof for safety ). | No. | 1
3.27 | Cable Tray & Ladder
3.27.1 | Supply and install heavy gauge hot dipped galvanized cable tray and cable ladder, 1.5mm thickness for cable tray,2mm thickness for cable ladder, complete with supports, fixing devices, separators, clamps, end caps, elbows, joints, branches, tees, reducers, offsets, flyovers, inspection boxes,...etc., with earth continuity connection to earthing system and all included accessories , as per Drawings, Specifications and Supervision Engineer as follow:
a. | 100x50mm perforated cable tray. | L.M | 12
b. | 600x100mm cable ladder | L.M | 1
c. | 400x100mm cable ladder | L.M | 30
3.28 | Fire Alarm Control Panel (FACP)
a. | Supply, install, test and commission an addressable analogue fire alarm control panel (FACP) inclusive of all equipment and accessories batteries, charger, internal conductors and/or cables, in the pump station, switches, accordance with the requirements of the Specifications and as shown on Drawings. | Set | 1
b. | Smoke-Heat Detector (multi sensors) addressable. | Pcs | 9
c. | Manual Call Break Glass Station (Analogue Addressable Type). | Pcs | 1
d. | Fire Alarm 6" Bell Outdoor Type | Pcs | 2
Subtotal of Bill No. 3 Carried to Summary

## Bill 4
Bill No. 4 : Facilities Building
Item No. | Description | Unit | Quantity | Unit Rate USD | Total Amount USD
important notes | A. The Contractor has to visit the site and examine the situation of all structures, both from inside and outside, and be fully aware of the works to be done in terms of nature, quantities, dimensions, and be aware of the existing facilities and equipment that may has affect on efforts to execute the works.
B. If in opinion of the Engineer/Client Drawings or method statement or both are needed for certain works, the Contractor shall prepare them and get the approval of the Engineer/Client before executing the works.
C. The items listed hereunder will be in lump sum and the Contractor is not entitled for any claim raise due to that in regard to quantities, nature, dimensions of works to be executed.
A. | Civil & Architectural Works:
Note: following works shall be executed after the works defined at items 3.1 & 3.2 of Bill No.3 are fully executed.
4.1 | Remove all existing plaster and ceramic works on floor, walls, ceiling, exposing the block work or concrete fix any damages and provide and apply new ceramic works, and new smooth cement plastering of 25 mm thick and emulsion paint as per Specifications and transport out of the site to approved by local authorities all wastes and rubbish come out of removing existing works. | L.S
Sub-total Carried Forward
Sub-total Brought Forward
4.1.1 | Ceramic Tiles 30x30x.9 cm on floor | L.S | 1
4.1.2 | Ceramic Tiles 20x20x.9 cm on walls full height | L.S | 1
4.1.3 | Plaster Works on the ceiling | L.S | 1
4.1.4 | Emulsion Paint on the ceiling | L.S | 1
4.2 | Remove all fixtures, dish washing basin, toilet chair, hand wash basin…etc. and transport all out of site to approved by local authorities location providing and fixing new ones will be covered by sanitary works at mechanical section of this BOQ. | L.S | 1
4.3 | Remove all doors, windows, louvers and replace them with new ones of the same sizes as per Drawings including repairing the concrete opening and make it neat to receive the metal work as per Specifications.
| SD02, Aluminum Door | No. | 3
| WD01, Aluminum Window | No. | 2
4.4 | Clean up all external wall, clean and repair concrete damaged parts of the walls and roof parapet and sheds, provide and apply emulsion paint on the concrete parts as per Specifications. | L.S | 1
Sub-total Carried Forward
Sub-total Brought Forward
4.5 | Remove all layers of roofing exposing the concrete roof repair any damages, then provide and apply roofing concrete screed with minimum 5 cm thick inclined towards roof drain, as per Specifications. | L.S | 1
B. | Mechanical Works:
4.6 | Supply, install, testing and commissioning mechanical works and the price include all plumping works from pipes, fittings, mixtures, valves, supports, floor drains, clean outs, wash basin, toilets, fans, sinks, water heater, water tanks on roof and all mechanical equipment as per Specifications and Engineer approvals | L.S | 1
C. | Electrical Works:
4.7 | works include supply, install, connect, test and commissioning lighting fixtures, lighting switches, power sockets, double pole switches, power isolators, exposed conduits, wires, cables, laying cables from distribution board (DB) through trench and manholes, | L.S | 1
Subtotal of Bill No. 4 Carried to Summary

## Bill 5
Bill No. 5 :Transformer Room
Item No. | Description | Unit | Quantity | Unit Rate USD | Total Amount USD
important notes | A. The Contractor has to visit the site and examine the situation of all structures, both from inside and outside, and be fully aware of the works to be done in terms of nature, quantities, dimensions, and be aware of the existing facilities and equipment that may has affect on efforts to execute the works.
B. If in opinion of the Engineer/Client Drawings or method statement or both are needed for certain works, the Contractor shall prepare them and get the approval of the Engineer/Client before executing the works.
C. The items listed hereunder will be in lump sum and the Contractor is not entitled for any claim raise due to that in regard to quantities, nature, dimensions of works to be executed.
A. | Civil & Architectural Works:
Note: following works shall be executed after the works defined at items 3.1 & 3.2 of Bill No.3 are fully executed.
5.1 | Remove all existing plaster works on walls and ceiling, exposing the block work or concrete fix any damages and provide and apply new smooth cement plastering of 25 mm thick and emulsion paint as per Specifications and transport out of the site to approved by local authorities all wastes and rubbish come out of removing existing works
Sub-total Carried Forward
Sub-total Brought Forward
5.1.1 | Plaster works on the walls | L.S | 1
5.1.2 | Emulsion paint on the walls | L.S | 1
5.1.3 | Emulsion paint on the ceiling | L.S | 1
5.2 | Remove existing flooring fixation and repair any damages and provide and apply epoxy paint as per Specification. | L.S | 1
5.3 | Remove all doors, windows, louvers and replace them with new ones of the same sizes, windows louvers and Doors will be of aluminum including repairing the concrete opening and make it neat to receive the metal work as per Specifications
| SD02 Aluminum Door | No. | 1
| SD04 Steel Door | No. | 1
| LW01 Aluminum Louver | No. | 1
5.4 | Clean up all external stone wall by sand blast, clean and repair concrete damaged parts of the walls and roof parapet and sheds, provide and apply emulsion paint on the concrete parts as per Specifications | L.S | 1
Sub-total Carried Forward
Sub-total Brought Forward
5.5 | Remove all layers of roofing exposing the concrete roof repair any damages, then provide and apply roofing concrete screed with minimum 5 cm thick inclined towards roof drain, as per Specifications | L.S | 1
B. | Electrical Works:
5.6 | works include supply, install, connect, test and commissioning lighting fixtures, lighting switches, power sockets, double pole switches, power isolators, exposed conduits, wires, cables, laying cables from distribution board (DB) through trench and manholes. | L.S | 1
Subtotal of Bill No. 5 Carried to Summary

## Bill 6
Bill No. 6 : Guard Room
Item No. | Description | Unit | Quantity | Unit Rate USD | Total Amount USD
important notes | A. The Contractor has to visit the site and examine the situation of all structures, both from inside and outside, and be fully aware of the works to be done in terms of nature, quantities, dimensions, and be aware of the existing facilities and equipment that may has affect on efforts to execute the works.
B. If in opinion of the Engineer/Client Drawings or method statement or both are needed for certain works, the Contractor shall prepare them and get the approval of the Engineer/Client before executing the works.
C. The items listed hereunder will be in lump sum and the Contractor is not entitled for any claim raise due to that in regard to quantities, nature, dimensions of works to be executed.
A. | Civil & Architectural Works:
Note: following works shall be executed after the works defined at items 3.1 & 3.2 of Bill No.3 are fully executed.
6.1 | a. Remove all existing plaster works on walls, exposing the block work fix any damages and provide and apply new smooth cement plastering of 25 mm thick and oil paint as per Specifications. b. Remove all metal sheets off the roof and provide and fix new Corrugated Metal Panels. c. Transport out of the site to approved by local authorities all wastes and rubbish come out of removing existing works.
Sub-total Carried Forward
Sub-total Brought Forward
6.1.1 | Plaster works on walls | L.S | 1
6.1.2 | oil paint on walls | L.S | 1
6.1.3 | Corrugated Metal Panels. | L.S | 1
6.2 | Remove all existing floor fixation and repair any damages, and provide and apply ceramic tiles 30x30x.9 as per specification
6.2.1 | Ceramic tiles 30X30X.9 | L.S | 1
6.3 | Remove all doors, windows, louvers and replace them with new ones of the same sizes and apply aluminum doors and windows instead the existing one including repairing the concrete opening and make it neat to receive the metal work as per Specifications.
| SD03 Aluminum Door | No. | 1
6.4 | Clean up all external wall , clean and repair concrete damaged parts of the walls and roof parapet and sheds, provide and apply emulsion paint on the concrete parts as per Specifications. | L.S | 1
Sub-total Carried Forward
Sub-total Brought Forward
B. | Mechanical Works:
6.5 | Supply, install, testing and commissioning mechanical works and the price include all HVAC works from air conditioning units, refrigerant pipes , fittings, thermostat, and all mechanical equipment as per Specifications and Engineer approvals | L.S | 1
C. | Electrical Works:
6.6 | Works include supply, install, connect, test and commissioning lighting fixtures, lighting switches, power sockets, double pole switches, power isolators, exposed conduits, wires, cables, laying cables from distribution board (DB) through trench and manholes. | L.S | 1
Subtotal of Bill No. 6 Carried to Summary

## Bill 7
Bill NO.7: Maintenance Area
Item No. | Description | Unit | Quantity | Unit Rate USD | Total Amount USD
important notes | A. The Contractor has to visit the site and examine the situation of all structures, both from inside and outside, and be fully aware of the works to be done in terms of nature, quantities, dimensions, and be aware of the existing facilities and equipment that may has affect on efforts to execute the works.
B. If in opinion of the Engineer/Client drawings or method statement or both are needed for certain works, the Contractor shall prepare them and get the approval of the Engineer/Client before executing the works.
C. The items listed hereunder will be in lump sum and the Contractor is not entitled for any claim raise due to that in regard to quantities, nature, dimensions of works to be executed.
A. | Civil & Architectural Works:
7.1 | a. Remove all existing plaster works on walls, exposing the block work fix any damages and provide and apply new smooth cement plastering of 25 mm thick and emulsion paint as per Specifications b. Remove all metal sheets off the roof and provide and fix new Corrugated Metal Panels. c. Transport out of the site to approved by local authorities all wastes and rubbish come out of removing existing works .
Sub-total Carried Forward
Sub-total Brought Forward
7.1.1 | Plaster works on walls | L.S | 1
7.1.2 | Emulsion paint on walls | L.S | 1
7.1.3 | Corrugated Metal Panels. | L.S | 1
7.2 | Clean existing floor and repair any damages, and provide and apply epoxy paint
7.2.1 | Epoxy Paint | L.S | 1
7.3 | a. Provide and Apply smooth cement plaster of 25mm on internal and external faces, b. Provide and Apply oil paint on internal and external faces, c. Provide and Fix door and windows all as per Drawings and Specifications.
a | Plaster | M2 | 350
b | Oil paint | M2 | 350
c | Steel Door SD06 | No | 1
d | Aluminum Louver LW02 | No | 2
Sub-total Carried Forward
Sub-total Brought Forward
B. | Electrical Works:
7.4 | Works include supply, install, connect, test and commissioning lighting fixtures, lighting switches, power sockets, double pole switches, power isolators, exposed conduits, wires, cables, laying cables from distribution board (DB) through trench and manholes, | L.S | 1
Subtotal of Bill No. 7 Carried to Summary

## Bill 8
Bill No. 8 : Store Room
Item No. | Description | Unit | Quantity | Unit Rate USD | Total Amount USD
important notes | A. The Contractor has to visit the site and examine the situation of all structures, both from inside and outside, and be fully aware of the works to be done in terms of nature, quantities, dimensions, and be aware of the existing facilities and equipment that may has affect on efforts to execute the works.
B. If in opinion of the Engineer/Client Drawings or method statement or both are needed for certain works, the Contractor shall prepare them and get the approval of the Engineer/Client before executing the works.
C. The items listed hereunder will be in lump sum and the Contractor is not entitled for any claim raise due to that in regard to quantities, nature, dimensions of works to be executed.
A. | Civil & Architectural Works:
Note: following works shall be executed after the works defined at items 3.1 & 3.2 of Bill No.3 are fully executed.
8.1 | a. Remove the existing door and provide and build block work as per specification closing the door opening. b. Make an opening on the opposite wall same size of the old door including proving concrete frame to receive the new door .
8.1.1 | Close the existing door opening by block work | L.S | 1
8.1.2 | Make new opening same size of the existing door | L.S | 1
Sub-total Carried Forward
Sub-total Brought Forward
8.2 | a. Remove all existing plaster works on walls, exposing the block work fix any damages and provide and apply new smooth cement plastering of 25 mm thick and emulsion paint as per Specifications b. Clean up ceiling concrete panels and provide and apply emulsion paint c. Transport out of the site to approved by local authorities all wastes and rubbish come out of removing existing works
8.2.1 | Plaster works on walls | L.S | 1
8.2.2 | Emulsion paint on walls | L.S | 1
8.2.3 | Emulsion paint on ceiling | L.S | 1
8.3 | Remove all existing floor fixation and repair any damages, and provide and apply epoxy paint as per Specification
8.3.1 | Epoxy paint | L.S | 1
8.4 | Remove all doors, windows, louvers and replace them with new ones of the same sizes and material except the windows and louvers will be of aluminum including repairing the concrete opening and make it neat to receive the metal work as per Specifications.
a | Steel Door SD06 | No | 1
Sub-total Carried Forward
Sub-total Brought Forward
8.5 | Clean up all external wall, clean and repair concrete damaged parts of the walls and roof parapet and sheds, provide and apply emulsion paint on the concrete parts as per Specifications | L.S | 1
8.6 | Remove all layers of roofing exposing the concrete roof repair any damages, then provide and apply roofing concrete screed with minimum 5 cm thick inclined towards roof drain, as per Specifications | L.S | 1
B. | Electrical Works:
8.7 | Works include supply, install, connect, test and commissioning lighting fixtures, lighting switches, power sockets, double pole switches, power isolators, exposed conduits, wires, cables, laying cables from distribution board (DB) through trench and manholes, | L.S | 1
Subtotal of Bill No. 8 Carried to Summary

## Bill 9
Bill No. 9 :Yard and Fence
Item No. | Description | Unit | Quantity | Unit Rate USD | Total Amount USD
important notes | A. The Contractor has to visit the site and examine the situation of all structures, both from inside and outside, and be fully aware of the works to be done in terms of nature, quantities, dimensions, and be aware of the existing facilities and equipment that may has affect on efforts to execute the works.
B. If in opinion of the Engineer/Client Drawings or method statement or both are needed for certain works, the Contractor shall prepare them and get the approval of the Engineer/Client before executing the works.
C. The items listed hereunder will be in lump sum and the Contractor is not entitled for any claim raise due to that in regard to quantities, nature, dimensions of works to be executed.
A. | Civil & Architectural Works:
Note: following works shall be executed after the works defined at items 3.1 & 3.2 of Bill No.3 are fully executed.
9.1 | a. clean up the whole yard area removing rubbish, wastes, dust, mud, oil and grease stains, syrup's. …etc. the concrete surface to be clearly exposed using sand blast if needed, cleaning the joints in its full depth. b. repair any damages in the concrete surface by removing lose parts exposing the steel and replace it with grout with fine aggregate and adhesive material . c. add polysuphade sealant in the joints with backing.
Sub-total Carried Forward
Sub-total Brought Forward
9.1.1 | Cleaning and repairing the yard | LS | 1
9.1.2 | cleaning the joints and applying sealant | LS | 1
9.2 | a. repair the fence, removing the damaged parts if any and rebuild it, and build new parts b. remove all existing plaster works and provide and apply new plaster works c. provide and apply emulsion paint on inner and outer faces of the fence
9.2.1 | repairing damaged parts and build new parts | LS | 1
9.2.2 | Plaster works on fence | LS | 1
9.2.3 | Emulsion paint on the fence | LS | 1
9.3 | Remove the Gates of the fence and provide and fix new Gates
9.3.1 | Steel gates | LS | 1
9.4 | Provide and apply 4 mm torch applied Damp proof membrane at the inlet channel base and wall up to 2 m above the base. | LS | 1
Sub-total Carried Forward
Sub-total Brought Forward
B. | Electrical Works:
9.5 | Cables and accessories
Supply, install, connect, test and commission 600/1000V power cables as per Drawings, Specifications and Supervision Engineer as follow:
a. | 4x120 mm² CU/XLPE/PVC ( MCC main cable). | L.M | 150
b. | 5x6mm² CU/XLPE/PVC (DB main cable). Price include 25mm PVC | L.M | 15
9.6 | Trench for electrical cable
Supply and install rigid UPVC conduits 4" complete with warning tapes, solid blocks, sand backfilling and concrete encasement as shown on Drawings. Price including civil works and rope traction as per Drawings, Specifications and Supervision Engineer as follow:
a. | Trench include 8x4" UPVC conduits. | L.M | 18
Sub-total Carried Forward
Sub-total Brought Forward
b. | Trench include 4x4" UPVC conduits. | L.M | 5
c. | Trench include 2x4" UPVC conduits. | L.M | 55
9.7 | Electrical Manhole
Excavate and install electrical manholes as shown on Drawings, including all civil works and sleevs as per Drawings, Specifications and Supervision Engineer as follow:
a. | 100x100x100 cm manhole | No. | 4
b. | 60x60x60 cm manhole | No. | 6
9.8 | Power Isolators
Supply, install, connect, test and commissioning isolators, price shall include Isolators, cables, conduits, boxes, epoxy painted steel stand and all included accessories , as per Drawings, Specifications and Supervision Engineer as follow:
a. | 20 Amp Isolator, 400 Volt, 4 poles, IP65, housed in thermoplastic/polycarbonate or sheet steel enclosures, Straight Blade, Industrial Grade, Grounding, , Side Wired, Steel Strap. ( for screen control panel ) | No. | 1
Sub-total Carried Forward
Sub-total Brought Forward
9.9 | Earthing
Supply and install earth system with resistance less than 2 ohm, price include rods, earth pits, earthing cable to MCC, testing points, UPVC conduits, concrete encasement, earthling conductoras per Drawings, Specifications and Supervision Engineer as follow:
a. | Earthing system for MCC. | L.S | 1
Subtotal of Bill No. 9 Carried to Summary

## Bill 10
Bill No.10 : Generator Room
Item No. | Description | Unit | Quantity | Unit Rate USD | Total Amount USD
Sub-total Brought Forward
important notes | A. The Contractor has to visit the site and examine the situation of all structures, both from inside and outside, and be fully aware of the works to be done in terms of nature, quantities, dimensions, and be aware of the existing facilities and equipment that may has affect on efforts to execute the works.
B. If in opinion of the Engineer/Client Drawings or method statement or both are needed for certain works, the Contractor shall prepare them and get the approval of the Engineer/Client before executing the works.
Note: following works shall be executed after the works defined at items 3.1 & 3.2 of Bill No.3 are fully executed.
A. | Civil & Architectural Works:
10.1 | a. Remove all existing plaster works on walls, exposing the block work fix any damages and provide and apply new smooth cement plastering of 25 mm thick and oil paint as per Specifications b. Clean up cieling concrete slab and provide and apply emulsion paint c. Transport out of the site to approved by local authorities all wastes and rabish come out of removing existing works
10.1.1 | Plaster works on walls | L.S | 1
10.1.2 | Oil paint on walls | L.S | 1
10.1.3 | Emulsion paint on ceiling | L.S | 1
Sub-total Carried Forward
Sub-total Brought Forward
10.2 | Remove all existing floor fixation and repair any damages, and provide and apply epoxy paint as per Specifications
10.2.1 | Epoxy paint | L.S | 1
10.3 | provide and fix steel and aluminum doors and windows, this to include providing materials, manpower, machinery to complete the work as per Drawings and Specifications.
10.3.1 | SD07 Steel Door | No | 1
10.3.2 | LD02 Aluminum Louver | No | 4
10.4 | Clean up all external wall, clean and repair concrete damaged parts of the walls and roof parapet and sheds, provide and apply emulsion paint on the concrete parts as per Specifications | L.S | 1
10.5 | Remove all layers of roofing exposing the concrete roof repair any damages, then provide and apply roofing concrete screed with minimum 5 cm thick inclined towards roof drain, as per Specifications | L.S | 1
10.6 | Doors and Windows
provide and fix steel and aluminum doors and windows, this to include providing materials, manpower, machinery to complete the work as per Drawings and Specifications.
10.6.1 | SD07 Steel Door | No | 1
10.6.2 | LD02 Aluminum Louver | No | 4
Sub-total Carried Forward
Sub-total Brought Forward
B. | Electrical Works:
10.7 | Standby Power Generator
| Supply, install, connect, test and commissioning 500 kva Standby generator run by diesel including sound proofing, 400v/50Hz, 3 phase, 1500 rpm complete with controllers, battery charger, preheating system, fire extinguisher 12 kg CO2, concrete base, exhust pipe, ducts with louver, earthing system, price include 630A 4 pole ACB breaker and all nesseccary material to complete the installation and the works as per Drawings,Specifications and Supervision Engineer. | No. | 1
10.8 | Electrical Works
| works include supply, install, connect, test and commissioning lighting fixtures, lighting switches, power sockets, double pole switches, power isolators, exposed conduits, wires, cables, laying cables from distribution board (DB) through trench and manholes, | L.S | 1
Subtotal of Bill No. 10 Carried to Summary

## DAYWORKS
DAYWORKS
Item No. | Description | Unit | Quantity | Unit Rate USD | Total Amount USD
DAYWORKS ( all provisional)
Labour
The rates entered here should include for all costs such as insurance, travelling time, overtime, accomodation, management, supervision, small trade tools, overheads and profit.
1 | unskilled labour | h | 70
2 | Skilled labour | h | 60
Plant (working)
These rates shall include for all operation and maintenance costs, fuel, oil, operations. Only the time employed will be paid for
3 | hydraulic backactor, 85HP capacity | h | 10
4 | wheel - mounted shovel loader, 1.0 - 1.3 m 3 capacity | h | 40
5 | compressor capacity 6 m3 / min, with two breakers | h | 10
6 | 5-ton, lorry- mounted crane | h | 10
7 | mobile crane 10 ton(tandem, 3 wheel steel roller dead weight 8 ton | h | 5
8 | dumper .75 m3 | h | 20
Sub-total Carried Forward
Sub-total Brought Forward
9 | Oxyactylene cutting and welding set including oxygen and acyleline | h | 10
10 | Electric welding set including elctrodes | h | 10
11 | 5-ton tipper lorry | h | 30
12 | Self propelled water tanker (including 5 m3 of water) | h | 30
13 | Self propelled exhausted truck 5 m3 capacity | h | 30
14 | Mechanical trench tamper, 1.2 ton capacity | h | 20
15 | Smooth wheel vibrating rolle, 1.2 ton capacity | h | 15
16 | Diesel / petrol driven sewage pump, 100 m3/hr, H = 10 m including suction hose and 50 m discharge hose | h | 25
Materials
17 | Aggregates for concrete | m3 | 30
18 | Sand for concrete | m3 | 30
19 | Portland cement | tons | 2
20 | Sulphate resisting cement | tons | 2
Sub-total Carried Forward
Sub-total Brought Forward
21 | Concrete B 15 | m3 | 5
22 | Concrete B 25 | m3 | 8
23 | Mild steel reinforced | tons | 1
24 | Concrete Blocks 20x20x40 | m2 | 2
25 | Shuttering / form work | m2 | 20
26 | Protective PE sheeting, including fasteners, etc. | m2 | 20
27 | Epoxy coating on surfaces exposed to sewage as spewcified in section 2.6.6 | m2 | 20
28 | Extra over for demolition, removal and disposal of concrete | m3 | 10
29 | Ditto but Bricks/ stone works | m3 | 10
30 | Filling of depressions or other places and compaction of fill material in layers including import of suitable material | m3 | 20
31 | Reinstatement of pavement layers to their original condition. | m2 | 20
Subtotal of DAYWORKS Carried to Summary

## Summary
Summary
Bill No. | Description | Cost(USD)
1
2 | Force Main Pipeline
3 | Crater Pump Station
4 | Facilities Building
5 | Transformer Room
6 | Guard Room
7 | Maintenance Area
8 | Store Room
9 | Yard and Fence
10 | Generator Room
Dayworks
Total Cost (USD)