Request for Quotation (RFQ) for Goods/Services

TECHNICAL QUESTIONNAIRE P-III-A Replacing force main sewer pipeline from Altawahi district to Mualla district and Rehabilitation of Altawahi pumping station (EHC-PR-WS-ADN-001)

Version: v2021

# Technical Quotation Form

RFQ reference no: RFQ/2023/46440

Name of Bidder: [insert name of Bidder]

Technical specifications for goods – Comparative Data Table:

| Item | Specifications required | Is quotation compliant? Bidder to complete | Bidder’s Offer specifications Bidder to complete |  |
| --- | --- | --- | --- | --- |
| First: HDPE Pipes and fittings |  |  |  |  |
|  | Date of manufacturing (pipes, fittings) | Bidder to insert |  | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
|  | Manufacturer Name (pipes, fittings) | Bidder to insert |  | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
|  | Country of origin (pipes, fittings) | Bidder to insert |  | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
|  | The bidder confirms that the Size range as per BoQ. | ☐ Yes ☐ No |  | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
|  | Pipe grades (PE. 100) with (SDR. 17) Minimum Required Strength (MRS) 10 Mpa. | ☐ Yes ☐ No |  | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
|  | Pressure Rating: PN 10 | ☐ Yes ☐ No |  | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
|  | The density (PE 100) should not be less 0.945 g/cm | ☐ Yes ☐ No |  | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
|  | Polyethylene (PE) Pipes and fittings Dimensions satisfies the requirements of DIN 8074, ISO 4427 or equivalent | ☐ Yes ☐ No |  | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
|  | HDPE pipe’s Length | Bidder to insert |  | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
|  | Joining type: butt fusion welding | ☐ Yes ☐ No |  | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
|  | Generally Marking the pipes have to be marked according to DIN 8074 No.8. intervals not exceeding 4 m the minimum marking should indicate: -Manufacturer’s name and/or trade mark. - Year of Manufacture - Dimension Nominal Size manufacture - Dimension Ratio (e.g., SDR 17) - Standard PE code designation (e.g PE100) - Applicable Standards | ☐ Yes ☐ No |  | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
|  | The bidder confirms that the manufacturer quality control test results and report will be provided. | ☐ Yes ☐ No |  | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
|  | The authorization of manufacturer (Form G) is attached to the offer. | ☐ Yes ☐ No |  | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
| Second: MECHANICAL WORKS. |  |  |  |  |
| - Sewage Submersible Pump, dry-vertical installed |  |  |  |  |
| - 1.1 | Brand/Manufacturer's Name | Bidder to insert |  | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
| - 1.2 | Country of origin | Bidder to insert |  | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
| - 1.3 | Year of Manufacture: | Bidder to insert |  | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
| - 1.4 | Model | Bidder to insert |  | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
| - 1.5 | Sewage Submersible Pump, dry- vertical installed | ☐ Yes ☐ No |  | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
| - 1.6 | suitable to handle Particle size: 10 cm | ☐ Yes ☐ No |  | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
| - 1.7 | -flow: 62 L/S - Head : 14.6 m | ☐ Yes ☐ No |  | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
| - 1.8 | Pump housing Materials: Cast Iron Impeller Materials: Cast Iron | ☐ Yes ☐ No |  | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
| - 1.9 | Power supply: 400 / 50/ 3 V/Hz/Ph | ☐ Yes ☐ No |  | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
| - 1.10 | Maximum Rated Power: 14.8 kw Maximum Power consumption: 13 kw | ☐ Yes ☐ No |  | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
|  | Operation method: by floats and pressure switch | ☐ Yes ☐ No |  | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
| - 1.11 | With cooling jacket | ☐ Yes ☐ No |  | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
| - VITRIFIED CLAY pipe inside pumping station |  |  |  |  |
| - 2.1 | Brand/Manufacturer's Name | Bidder to insert |  | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
| - 2.2 | Country of origin | Bidder to insert |  | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
| - 2.3 | Year of Manufacture | Bidder to insert |  | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
| - 2.4 | extra stengh Class (ES) according to DIN EN 295 | ☐ Yes ☐ No |  | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
| - 2.5 | PN10 | ☐ Yes ☐ No |  | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
| - Valves |  |  |  |  |
| - 3.1 | Brand/Manufacturer's Name | Bidder to insert |  | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
| - 3.2 | Country of origin | Bidder to insert |  | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
| - 3.3 | Year of Manufacture | Bidder to insert |  | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
|  | Model | Bidder to insert |  | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
| - 3.4 | Knife Gate Valve: - according to AWWA C 520 - DN: As per BoQ - PN10 - for wastewater | ☐ Yes ☐ No |  | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
| - 3.5 | ball check valves: - according to EN 12050-4 - DN: As per BoQ - PN10 - for wastewater - face to face according to DIN 3202 - F6. - Flange drilled acc. EN 1092-2. - Body and cover shall be of ductile iron GJS-400-15 (GGG-40). - Bolts and nuts of stainless steel A2 and cover gasket of NBR rubber - Epoxy coating to DIN 30677, internally and externally | ☐ Yes ☐ No |  | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
| - 3.6 | Air Release Valves: - according to AWWA C 512 - DN: As per BoQ - PN10 - for wastewater - The float, seat, and all moving parts shall be 1.4571 S.S. | ☐ Yes ☐ No |  | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
| - Penstocks |  |  |  |  |
| - 5.1 | Brand/Manufacturer's Name | Bidder to insert |  | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
| - 5.2 | Country of origin | Bidder to insert |  | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
|  | Year of Manufacture | Bidder to insert |  | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
| - 5.3 | Model | Bidder to insert |  | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
| - 5.4 | Penstocks: -Details: as drawing | ☐ Yes ☐ No |  | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
| - Automatic Electrical Wastewater Screen |  |  |  |  |
| - 6.1 | Brand/Manufacturer's Name | Bidder to insert |  | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
| - 6.2 | Country of origin | Bidder to insert |  | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
| - 6.3 | Year of Manufacture | Bidder to insert |  | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
| - 6.4 | Model | Bidder to insert |  | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
| - 6.6 | - Height: not less than 6.5 metres, width: 1.5 m. - Rated Power: 3 kw - Details dimension bars: as drawings | ☐ Yes ☐ No |  | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
| - Crane |  |  |  |  |
| - 7.1 | Brand/Manufacturer's Name | Bidder to insert |  | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
| - 7.2 | Country of origin | Bidder to insert |  | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
| - 7.3 | Year of Manufacture | Bidder to insert |  | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
| - 7.4 | Model | Bidder to insert |  | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
| - 7.5 | -automatic lifting crane with capacity 5 ton - Hoist Motor Power 9.5KW - Lifting Height 20m - Trolley Motor Power 2X0.25Kw | ☐ Yes ☐ No |  | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
| Third: ELECTRICAL WORKS |  |  |  |  |
| 1. Motor Control Centre (MCC) |  |  |  |  |
|  | Brand/Manufacturer's Name | Bidder to insert |  | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
|  | Country of origin | Bidder to insert |  | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
|  | Year of Manufacture | Bidder to insert |  | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
|  | Model | Bidder to insert |  | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
|  | - (MCC) shall include main incoming and outgoing circuit breakers, busbars, pumps running meters, 15kw three soft starters, Uninterruptible Power Supply (UPS) for 6 hours, (24 VDC) power supply and charger measuring and metering instruments, isolating transformer, indication lamps, motor monitoring and protection unit ( MMPU), with spare part 10% of protection equipment such as circuit breakers, fuses, relays... etc. . | ☐ Yes ☐ No |  | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
| 2. Programmable Logic Controller (PLC) |  |  |  |  |
|  | Brand/Manufacturer's Name | Bidder to insert |  | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
|  | Country of origin | Bidder to insert |  | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
|  | Year of Manufacture | Bidder to insert |  | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
|  | Model | Bidder to insert |  | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
|  | (PLC) comprising of all telemetry equipment I/O modules, interface modules, Ethernet switch suitable for fiber optic cable, fiber optic patch panel, serial port, interconnection of power and signal cables between the PLCs and MCC, UPS unit, power supply *Communication Protocols: The controller shall support Hart protocol and at least one of the following industry standard protocols: - Modbus - Ethernet TCP/IP. - Profibus. - DNP3 - A Laptop shall be included for PLC programming and equipment configuration - all the required programs and software should be installed on the laptop and licensed - PLC with Ethernet switch, fiber optic switch and fiber optic patch panel | ☐ Yes ☐ No |  | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
|  | Human Machine Interface (HMI): including graphics for the station and control of pumps and valves, some of data which will be viewed on the HMI: • Communication status • Inlet Pressure reading • Outlet Pressure reading • Flow rate • Flow totalizer. • Full control for pumps and valves • Alarm Limits • Pumps trip, pumps status, soft starter signals and control & pumps speed • Over temperature trip for pumps and trips • General trip • Mains available • UPS battery low. |  |  |  |
| 3. ATS |  |  |  |  |
|  | Brand/Manufacturer's Name | Bidder to insert |  | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
|  | Country of origin | Bidder to insert |  | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
|  | Year of Manufacture | Bidder to insert |  | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
|  | Model | Bidder to insert |  | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
|  | ATS: - CIRCIT BREAKER 3P 160A, - MECHANICAL INTERLOCK - UNDER VOLTAGE RELAY 400V, 3P, 50HZ - FREQUNCY MONITRING RELAY 230V | ☐ Yes ☐ No |  | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
| 4. Fire Alarm Control Panel (FACP) |  |  |  |  |
|  | Brand/Manufacturer's Name | Bidder to insert |  | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
|  | Country of origin | Bidder to insert |  | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
|  | Year of Manufacture | Bidder to insert |  | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
|  | Model | Bidder to insert |  | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
|  | -addressable analogue -inclusive of all equipment and accessories batteries, charger, internal conductors and/or cables, in the pump station, switches -Smoke-Heat Detector (multi sensors) addressable. -Manual Call Break Glass Station (Analogue Addressable Type). -Fire Alarm 6" Bell Outdoor Type | ☐ Yes ☐ No |  | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
| Fourth: Standby Power Generator 130 KVA |  |  |  |  |
| 1. GENERATOR SET |  |  |  |  |
|  | Brand/Manufacturer's Name | Bidder to insert |  | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
|  | Country of assembly | Bidder to insert |  | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
|  | Gen-set -Model.: | Bidder to insert |  | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
|  | Year of Production: 2022/2023 | Bidder to insert |  | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
|  | Skid-mounted Generator Set sound proof of KVA Net Rated Standby Power, including the diesel engine, alternator, MCCB, control panel, starting equipment, and fuel tank. | Bidder to insert |  | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
|  | Total Percentage(%) of de-rating in accordance to ISO 8528 or equivalent at site conditions: - Altitude:100 m A.S.L, - Temperature: 50°C Humidity: 70%. | % Bidder to insert |  | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
|  | Is it inserted The calculation and reference graph of de-rating for site conditions? | ☐ Yes ☐ No |  | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
|  | Total net rating Standby power at site condition after de-rating: 130 KVA. | ☐ Yes ☐ No |  | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
| 2. Diesel Engine |  |  |  |  |
|  | Brand/Manufacturer's Name | Bidder to insert |  | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
|  | Country of assembly | Bidder to insert |  | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
|  | Model. | Bidder to insert |  | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
|  | Year of Production: 2022/2023 | Bidder to insert |  | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
|  | Diesel, 4 stroke, direct injection, Water-cooled Engine | ☐ Yes ☐ No |  | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
|  | Aspiration: Turbo Charged | ☐ Yes ☐ No |  | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
|  | Gross engine power output… kWm | Bidder to insert |  | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
|  | Rated speed: 1500 rpm | ☐ Yes ☐ No |  | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
|  | Governor type: Electronic/Mechanic | ☐ Yes ☐ No |  | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
|  | Starting system: 12/24 Volt DC motor, maintenance-free lead acid batteries with charging system. | ☐ Yes ☐ No |  | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
|  | Set-mounted radiator cooling with proper size fan. | ☐ Yes ☐ No |  | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
|  | Specific Fuel consumption: max 28 Ltr/ hour at 100% load. | Bidder to insert |  | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
|  | Fuel tank of suitable construction with capacity sufficient to run the generator set continuously for 6 hours at the rated capacity. | Bidder to insert |  | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
|  | Exhaust system with silencers residential type. | ☐ Yes ☐ No |  | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
| 3. Alternator |  |  |  |  |
|  | Brand/Manufacturer's Name | Bidder to insert |  | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
|  | Country of assembly | Bidder to insert |  | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
|  | Model | Bidder to insert |  | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
|  | Year of Production: 2022/2023 | Bidder to insert |  | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
|  | Rated net Standby power at 0.8 power factor at site conditions not less than 104 KW | Bidder to insert |  | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
|  | Three phase, synchronous, drip proof, self-excited | ☐ Yes ☐ No |  | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
|  | Brushless Exciter | ☐ Yes ☐ No |  | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
|  | Voltage: 380-415 V Frequency: 50 Hz | ☐ Yes ☐ No |  | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
|  | Insulation class: H | ☐ Yes ☐ No |  | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
|  | (AVR) Model | Bidder to insert |  | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
|  | Tropical and moisture proof type (Anti-Condensation Heater) | ☐ Yes ☐ No |  | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
|  | Temperature rise Class: H (allowable temperature rise 125 oC over ambient temperature:40 oC) | ☐ Yes ☐ No |  | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
| 4. Control Panel and Instrumentation: |  |  |  |  |
|  | Brand/Manufacturer's Name | Bidder to insert |  | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
|  | Model | Bidder to insert |  | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
|  | Set-mounted Auto-start control panel Of IP 23 metal sheet enclosure with digital screen complete with all protection, metering and monitoring systems. | ☐ Yes ☐ No |  | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
|  | Provide complete autonomous generator set control and integration, precise frequency and voltage regulation, protection, fault detection, alarm notification, according to tech. specifications. | ☐ Yes ☐ No |  | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
|  | Four position selector switch with Off-Auto-Man-Test | ☐ Yes ☐ No |  | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
| 5. Others |  |  |  |  |
|  | The bidder confirms that the equipment and accessories is Brand-new current-model and never-used. | ☐ Yes ☐ No |  | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
|  | The bidder confirms that the catalogues and data sheet, performance curves are attached for the offered brands and models. | ☐ Yes ☐ No |  | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
|  | The bidder confirms to provide one-year (whichever occurs first) operation warranty of each supplied items. | ☐ Yes ☐ No |  | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
|  | The bidder confirms to provide Performance tests certificate from the manufacturer for the offered model and brand at the delivery stage. | ☐ Yes ☐ No |  | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
|  | The bidder confirms that A complete set of operation and maintenance manuals will be provided at delivery stage | ☐ Yes ☐ No |  | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
|  | The supplier confirms that the Manufacturer’s representative has Workshop and capable technical staff in Yemen, UNOPS has the right to do background check to confirm this requirement. | ☐ Yes ☐ No |  | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
|  | The bidder Confirms that the spare parts and after sale service is available in, Yemen | ☐ Yes ☐ No |  | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |