Section-13 Electrical Specifications

SECTION 01

GENERAL

1.   Scope

These Specifications cover the following systems that are intended to be used for the Project in accordance with the Drawings, Specifications and as directed and approved by the Engineer.

1.1  Electric Power

1.2  Lighting

1.3  Telephone System

1.4  Computer System

1.5  Bell System

1.6  Fire Alarm System

1.7  Grounding (earthing) System

1.8  Other Misc. Systems

2.   General Requirements

The Contractor shall supply all labour and material necessary and shall install, complete and ready for use, the above mentioned systems including the installation and wiring of miscellaneous equipment and devices, as indicated on the Drawings and as herein specified.

The Contractor shall carry out the whole of the Electrical Work in a workmanlike and substantial manner and in strict conformance with the codes listed in the following clauses, or approved equal.

All equipment and material supplied for this project shall be manufactured in strict compliance with the standards listed in the following clauses, or approved equal.

The Contractor’s attention is directed to the requirements of the GENERAL CONDITIONS OF CONTRACT,

If actual rating of equipment supplied under other sections are different than the values indicated on the Drawings, the Contractor shall bring the matter to the attention of the Engineer.  The Contractor shall implement all necessary modifications at no extra cost, to the approval of the Engineer.

3.   Interference and Erroneous Locations

The Contractor shall verify on Site all data and final locations of work done under other Sections of the Specifications, required for the installation of the Electrical Works.

In case of interference with other work or erroneous locations with respect to equipment or structures, the Contractor shall supply all labour and materials necessary to complete the Work in an approved manner.

4.   Climatic Conditions

Materials and equipment shall be suitable in all respects for operation on electrical systems under the following climatic conditions:

Max

- Temperature				35°C

- Relative Humidity 			45%

- Altitude				750 m

5.   Protection of Electrical Equipment

Electrical equipment shall be protected against mechanical damage and environmental conditions such as excess heat, water dripping or splashing upon it at all times during shipments, storage, and construction.  Equipment shall no be stored outdoors.  Where equipment is installed or stored in moist areas, such as unheated buildings, etc., it shall be provided with an acceptable means to prevent moisture damage.  This may be a uniformly distributed source of heat to prevent condensation.

Should any equipment or material  be subjected to possible damage by water, it shall be dried out thoroughly and put through a special dielectric test as directed, at the expense of the Contractor or shall be replaced by the Contractor without additional charge.

Should any equipment or material be subjected to possible mechanical damage, the Contractor shall repair or replace the damaged equipment as instructed by the Engineer.

6.   Codes and Standards

The Contractor shall carry out all electrical work in accordance with the latest issue of the “Regulations for the Electrical Installations published by the Institution of Electrical Engineers (IEE) referred to as IEE Wiring Regulations hereinafter, and where not in contradiction with the Local Electrical Authorities and Civil Defense Administration Instructions requirements.

If any redesign or modification of the Works in necessitated by the adoption of another approved code or due to local electrical authorities or safety instruction requirements, the extra cost incurred (if any) both for redesign and material shall be borne by the Contractor.

All equipment and materials supplied for this contract shall be manufactured in strict compliance with the latest relevant recommendations of the IEC if available.  Otherwise they shall comply with the latest relevant BS specifications

unless otherwise specified or approved.

7.   Acceptance Tests

Any work which is not in accordance with the Specifications or to the satistfaction of the engineer and/or local power authorities shall be removed and repaired at the Contractor’s expense.  All material must be factory finished and/or painted to the approval of the Engineer.

8.   Electrical Service

The electrical power system will operate on 400 volt, 3-phase,  50 Hz system.

The low current systems shall operated on the voltage specified or as recommended by the manufacturer to the approval of the Engineer.

9.   Equipment Supplied and installed by Others

Certain items of control and other equipment pertaining to plumbing, air conditioning, etc. indicated “by others” on the Electrical Drawings are shown for connection only.  Such items are not supplied as part of the Electrical Work, but all connections to such equipment shall be done under this Section.

10.  Equipment Not in Contract

Equipment so indicated or noted will not be in contract.  Connections to such equipment will not be carried out by the Contractor unless otherwise indicated or noted.

11.  Local Electrical Authorities Requirements

The Contractor shall attend on and afford all facilities to the Local Electrical Authorities and shall provide oil drainage pits, terminal cable pits, terminal boxes for cables, underground ducts, etc. to facilitate all main feeder work.  He shall be responsible for foreseeing any requirement as requested by the above mentioned authorities, and shall follow the Engineer’s instruction on Site.

The Contractor shall be responsible for preparing any shop drawings concerning transformer and electrical (meter) rooms, and feed in routings, and he shall consult the electrical authoritie in accordance with the Engineer’s instructions, to seek the approval of these authorities.  The Contractor shall also be responsible for follow up of the application for electrical connection.  The application form will be filled in by the Engineer unless otherwise requested from the contractor who shall carry out same at no extra charges.

12.  Abbreviations

The following abbreviations shall have the significance set forth opposite each:

NEC	:	National Electrical Code (Standard No. 70) (USA).

ANSI	:	American National Standards Institute (USA).

NEMA	:	National Electrical Manufacturers Associations (USA).

IEEE	:	The Institute of Electrical and Electronics Engineers (USA).

IEC	:	International Electrotechnical Commission.

BS		:	British Standards.

13.  Terminology

Terminology is used in the sense outlined in the Regulations and in BS 4727.

14.  Engineer’s Drawings

The Engineer’s Drawings issued with these Specifications are complementary to these Specifications.

These Drawings indicated the approximate location of all electrical devices and equipment.  The exact and final location shall be subject to the prior approval of the Engineer on Site.

The Contractor shall check Architectural, Structural, Air Conditioning, Plumbing andany other available Drawings to avert possible installation conflicts.  Should drastic changes from the original plans be necessary to resolve such conflicts, the Contractor shall secure the Engineer’s approval on necessary adjustments before any installation work is started.

All accessories and appertenances that the Engineer deems functionally necessary for a complete installation shall be supplied and installed whether or not explicitly indicated or described, at no extra charge.

Discrepancies shown on different Drawings or between Drawings and actual Site conditions, or between Drawings and Specifications shall be brought to the attention of the Engineer for a decision.

15.  Shop Drawings, Samples and Other Submittals

The Contractor shall submit shop drawings and samples Preliminary Items, Shop Drawings, and in the Conditions of Contract under Shop Drawings and Samples.

No equipment or system for which shop drawings and or samples are required shall be ordered or installed unless all such drawings and or samples are duly reviewed and approved by the Engineer.

The Contractor shall, upon the request of the Engineer provide plain paper copies of the standards extracts to which references are made in the specifications.

Two copies of the brochures submitted shall be originals as published the Manufacturer.  Other copies may be clear plain paper copies.

Submitted brochures shall include at least two copies of Manufacturer’s original publications, other copies may be clear plain paper copies.

The Contractor shall, upon the request of the Engineer, submit copies of extracts of standards to which references are made.

16.  “As-Built Drawings”

“As Built Drawings” shall be submitted Preliminary Items, “As-Built Drawings”.

17.   Instructions and Manuals

The Contractor shall provide the Employer with 3 complete sets of instructions or manuals covering operation, maintenance and ordering of spare parts of all of the electrical equipment, as applicable.

18.  Nameplates

Nameplates in Arabic and English shall be installed on all devices or pieces of equipment for which the use or identification may not be readily apparent, such as, but not limited to, starters, relays, contractors, controls, pushbuttons, indicating lights, switches.  Nameplates shall be mde of laminated sheet plastic, 2.5mm thick, or of anodized aluminium, approximately 1.5mm thick, engraved to provide white letters on a black background, and fastened in place with corrosion-resistant screws, or as specified by local authorities.  Nameplates shall also be provided on all manufactured assemblies to identify the assembly as well as feeders, circuits, compartments, switches, internal components, etc.

Nameplates shall be located in a position to be easily readable after completion of the installation of the equipment.

Nameplates for equipment weighing more than 15kg shall be marked giving the approximate weight to the nearest + or –5%.

19.   Modifications

if during the work, the Contractor wishes to make changes or modifications, then these modifications shall be submitted to the Engineer for approval.  If these changes result in extra expenses in design and/or material, these expenses shal be borne by the Contractor.

Should any equipment or material be subjected to possible mechanical damage, the Contractor shall repair or replace the damaged equipment as instructed by the Engineer.

END OF SECTION 1

# SECTION 02

## MOTORS & STARTERS

1.  General

The Contractor shall supply and install the motors and the starters under other sections when so mentioned, as shown on the Drawings and as herein specified.

Motor starting method and corresponding furnished starter shall be concordant.

2.  Rating of Motors

Motors shall be suitable for operation on 220 volt single phase or 380 volt 3-phase, 3-wire, 50 Hz system and shall be dripproof fan cooled to IEC 34-6 induction motor type unless otherwise indicated or specified.  All motors shall have a service factor of 1.15.

Motors of ratings smaller than 1 HP shall be single pahse and those of ratings 1HP and larger sahll be three pahse, unless otherwise indicated or approved.

Motors of rating 50 HP and larger shall be uato-transformer starting type, unless otherwise indicated.

Motors of rating larger than 5 HP shall be star-delta starting type, unless otherwise permitted or required by the Local Authorities.

Motors of rating five horse power and smaller shall be direct on line starting type.

Every motor shall be of sufficient capacity to operate the driven equipment under all load and operating conditions without exceeding its rated name-plate current or power or its specified temperature limit. The horsepower ratings for motors shown on the Drawings must be considered as an indication only.  For the use of motors other than that specified, the Contractor shall assume the cost of, and responsibility for satisfactorily accomplishing all changes (including engineering costs of redesign by the Engineer) in the work as indicated and specified.  All derating resulting from site conditions shall be allowed for in the design.

Motor performances shall comply with the requirements of IEC 34-1.

3.  Types of Motors

All motors shall be of a type approved for starting characteristics and ruggedness as may be required under the actual conditions of operation.

All motors shall have class F insulation as a minimum requirement.

The motors shall be designed so that the maximum temperature rise at continuous run under full load and operation conditions shall be in accordance with IEC Standards for Motors and Generators and based on the local ambient temperature.

4.  General Design of Motors

Motor windings shall be braced to withstand successfully the stresses resulting from the method of starting.  The windings shall be treated thoroughly with approved insulating compound suitable for protection against mousture and slightly acid or alkaline conditions.

Bearings shall be of the self-lubricating type, designed to ensure proper alignment of rotor and shaft, and to prevent leakage of lubricant.

Bearings for open motors shall be of the sleeve or ball type, as specified under respective items of mechanical equipment.

Indoor motors located in relatively clean surrounding, free from any abrasive or coducting dust or chemical fumes, shall be enclosed ventilated dripproof type.  Otherwise motors shall be totally enclosed fan cooled type.  Vertical motors if any shall be provided with thrust bearings adequate for all thrusts to which they can be subjected in operation.

Vertical motors of open type shall be provided with drip hoods of approved shape and construction.  When the drip hood is too heavy to be easily removed, provision shall be made for access for testing.

5.  Motor Terminal Boxes and Leads

Motors shall be furnished with oversize conduit terminal boxes to provide for making and housing the connections and with flexible leads of sufficient length to extend for a distance of not less than 10cm beyond the face of the box.  The size of cable terminals and conduit terminal box holes shall be as approved by the Engineer.  An approved type of solderless lug shall be supplied.  Totally enclosed motors shall have cast iron terminal boxes.

6.  Motor Shop Tests

Motor shop tests shall be made in accordance with IEC Test Code or approved equal.

Complete tests of each motor supplied shall be made and certified shop test data sheets shall be submitted, unless witness shop tests are reqired by the Detail Specifications pertaining to the equipment.  Each motor shall be tested for efficiency and power factor at 50, 75 and 100% of its rated horsepower, for temperature rise, torque, starting current and dielectric strength; and for compliance with all specified performance requirements.

7.  Motor Starters

Motor Starters shall be built and sized in accordance with IEC Standard 158-1, BS 775 and IEC 292-1&2, or approved equal.   Starters shall be non-reversing, magnetic type unless otherwise indicated or specified.

All starters shall be provided with thermal cutout devices in each phase calibrated for close protection of the motors against overloads.  These devices shall trip the starters in case of overload and shall bot allow it to be reset except manually.  The thermal overload relays shall be adjustable from 90 to 110% of nominal rating.  A signle calibration adjusts all three legs.  The overload relay shall be ambient compensated.

The starter shall be provided with auxiliary contacts for the connection of signaling, interlocking and other circuits as required for the controls.

Unless otherwise indicated, all starters shall be provided with START-STOP pushbuttons, and RED and GREEN pilot lights, all located on the starter front cover.  An overload reset button shall be provided inside the cover.  Pushbuttons shall be momentary contact or maintained type as applicable to the function of control.

Starters shall have horsepower ratings at least equal to ratings of motors they serve.

Voltage of control circuit shall not exceed 240 volts for starters in motor control centers or panels.  Individually mouted starters or combination starters may have their control voltage on 380-415 volts provided local regulations or local inspectors do not forbide the use of same.  The Contractor when utilizing such voltage for control shall provide a clear warning of existence of such voltage within the station.  If 240 volts are required by the local regulations or local inspectors, a neutral conductor shall be brought within the feeder of the starter of approved cross section, at no extra charge.

Starters shall be electrically held in, providing inherent undervoltage release.

Starters when no t part of a motor control center and are located indoors shall be encased in an IP 40 dust-proof enclosure, unless otherwise indicated.

“Star-delta” starters, if any, shall have additional “Star” and “Delta” contactors which shall be electrically and mechanically interlocked to close the motor in “Delta” connection with the supply after the “Star” contactor has opened.  A timing device shall be fitted to provide and adjust time in “Star” before changing over to the Delta connection.

“Star-Delta” Starters shall provide closed transition.

Schematic wiring diagram of all starters shall be provided on the interior of starter front cover.

Autotransformer starters if any shall have 2 coil construction with taps for 50m 65, and 80% starting voltage, shall be designed for medium duty, per NEMA standard ICS 2-214 or approved equal.  Closed transition shall be provided.  Three melting alloy overload relays shall be provided for overload protection except if used for fire pumps in which case provisions of approved regulations shall be applied.

8.  Motor Circuit Protective Devices

Motor circuit protective devices are rated in accordance with IEE Wiring Regulations.  Alternative proposals based on manufacturers recommendations shall be subject to the Engineer’s Approval.  The Contractor shall in any case be responsible to assure that the circuit protective devices shall carry the starting current with no tripping, and if reducing trip rating results in a reduction in frame size, the Contractor shall make sure that the new rating withstands the available short circuit current.

9.  Control Panel

Equipment indicated on plan of individual air handler units belonging to chilled water air conditioning system, shall consist of individually mounted combination starters and shall also include all additional control and instrumentation devices as described under corresponding clause in mechanical section.

### END OF SECTION 2

SECTION 03

AUTOMATIC TRANSFERE SWITCH

1.  General

The control cubicle shall be free standing or resiliently mounted on the main frame of the generating set.

The free standing control cubicle shall be of fabricated zinc coated sheet steel folded construction incorporating a lockable instrument and control panel mounted on the top front section and arranged to withdraw on runners for maintenance and inspection.  The rear, side and lower front panels shall be detachable for installation and maintenance purposes.  Control cubicles shall be finished in grey enamel paint to BSS 381 C-632.

The set mounted control cubicle shall be fabricated in zinc coated sheet steel with a full height hinged panel face allowing full access to all components.  The cubicle shall have lockable door handle.

Engine instruments shall be mounted on a separate engine sub-panel on the set.  The D.C. control circuit, battery charging fuses and charge regulator shall be incorporated in the plant wiring terminal box.

All plant wiring shall be in flexible PVC or PCP impervious to the action of water, fuel and lubricating oil, Interconnecting wiring through out the set shall be encased in flexible reinforced PVC or metallic conduit.

Coded Ferrules shall be fitted at the termination of each wire in the control cubicle.

The Control cubicle shall incorporate:

- 1 Voltmeter with six position selector switch.

- 1 Hand voltage trimmer.

- 1 Ammeter with four position selector switch.

- 3 Instrument current transformers.

- 1 Frequency meter.

TRANSFORMER SWITCH consisting of 2 triple pole mechanically and electrically interlocked contactors, with solid neutral.

- 1 Time delay controller (adjustable) for mains failure control.

- 1 Time delay controller (adjustable) for transfer of charge over switch control.

- 3 Adjustable magnetic overload unit switch dashpot time delays.

- 3 Current transformers for the overload units.

- 1 Overload indicator lamp.

- 1 Overload re-set push button.

- 1 Set HRC fuses for A.C. instrument and control circuits.

- 1 Set of relays arranged to sense a total failure or

- a drop to approximately 60% of the voltage in any phase.

The starting timer, monitoring unit and the relays shall be of the plug-in type.

- 1 Duty selector switch OFF/TEST/MANUAL/AUTO.

- 1 Mains operated trickle charger with mille-ammeter, switch and fuse.

- 1 Set of alternator, mains and load connections.  The D.C. control circuit and engine driven battery charging equipment and fuses, regulator, ammeter, etc., shall be incorporated in the plant wiring terminal box, and sub-panel.

Under normal mains available conditions, the load shall be fed via a three pole contactor.  When the mains fail i.e. remain below an adjustable level (setting 60%-90% from rated voltage) for an adjustable period of time (setting 0-60 seconds) this contactor shall be released and the plant started automatically.  An adjustable time delay control (setting 0-5 minutes) shall be provided controlling the changeover contactors after rated voltage frequency are available on the generator.  Changeover shall be possible both automatically and manually.  The load is then to be fed from the generator via a second contactor until the mains are restored when the contactors shall revert to the “mains available” condition and the plant shut down.  The transfer to normal mains shall be controlled via a time delay unit (0-30 minutes) adjustable.

### END OF SECTION 3

SECTION 04

UNDERGROUND DISTRIBUTION SYSTEM

- General

The Contractor shall supply, install and connect a complete underground distribution system as shown on the Drawings and as herein specified.

General routing of the underground distribution system shall be adhered to, except that any interference’s with other trades or with existing underground installation shall be brought to the attention of the Engineer.

Underground distribution shall be either directly buried or in concrete duct banks as specified or shown on the Drawings.  Roadway crossings shall in any case be in concrete duct banks.

Concrete used shall be class A.

Ducts shall be manufactured by Hepworth Industrial Plastics Ltd. (UK), or approved equal.

- Installation of Ductbanks

Ductbanks shall be installed as indicated on Drawings and as specified.  The Contractor shall provide all excavation and backfilling work.

Ducts shall be installed with a minimum slope of 0.5% and shall be sloped to manholes or handholes.  Ducts shall slope away from buildings where possible.

Spacers shall be installed at intervals of approximately 120cm and staggered between tiers of ducts to provide not less than 30cm of longitudinal separation.  Base spacers shall provide at least 7.5cm between the bottom of the trench and the underside of the bottom conduits.

The space shall be completely filled with concrete.  Conduits and spacers shall be firmly wired together before the concrete is placed.

Prior to the placing of the concrete, all and, dirt and any other debris shall be removed from the trench.  Conduits shall be held in place to prevent floating or accidental movement.

Joints in the conduits shall be staggered at 15cm minimum.  Couplings shall not rest on the bottom of the trench.  Steel reinforcement shall be provided for all Ductbanks under roadways.

Concrete encasement shall be installed so that a minimum clearance of 30cm is left between concrete and parallel pipes, structure, etc.  Crossing ducts shall be spaced 15cm as a minimum.

Top of the concrete shall not be less than 50cm below the finished grade or paving except for high tension cables in which case it shall not be less than 80cm.

Power driven vibrators shall not be used for spading of concrete around ducts.

The surface shall be restored to a condition at least equal to that in which it was before work was begun, or as otherwise indicated.

Ducts shall be clean of concrete, dirt and other substances.  A flexible mandrel 30cm long having a diameter approximately 0.5cm less than the conduit inside diameter shall be pulled through each duct.  A brush with stiff bristles shall be pulled afterwards to make certain that no particles of earth, sand, or gravel have remained.  All duct runs not allowing passage of the mandrel shall be replaced at no extra charges.

Ducts shall be sealed at  each end, with split teak wood plugs and bitumen or by other approved means to prevent the ingress of water and vermin.

20% spare ducts but not less than one shall be provided in each duct bank.

Cables leaving ducts shall be provided with duct seals.

Where duct banks are installed below the structural footing level of the building, it shall be the entire  responsibility of the Electrical subcontractor to coordinate with the Civil subcontractor for the laying of the concrete duct bank prior to the installation and erection of the structural footing.

All necessary diversions and warning signs and/or alternative diversion routs shall be provided in case existing roads or graded defined tracks are temporarily blocked for execution of the work.

- Directly Buried Cables

Directly buried cable shall be laid underground as shown on the Drawings and as herein specified.

Trenches shall be kept as straight as possible and shall be excavated to approved formations and dimensions.  Trenches shall have vertical sides and shall be close timbered and strutted where necessary to prevent subsidence.

All unsuitable excavated material shall be removed from site.

All cables laid in the same trench shall be placed in the same horizontal plane leaving a space of at least 7.5cm except  at otherwise  shown on the Drawings and specified hereinafter.

Cable trench depth shall be as shown on layout drawings, with minimum depth of 100cm for a single layer of HV cables.  Minimum depth from the top of cables to finished grade, unless otherwise, indicated on layout drawings, shall be 50cm for LV power feeders, and 45cm for street lighting cables.

High tension cables shall, where possible, be laid in separate trenches.  Otherwise a space of at least 50cm shall be left between these cables and any other cable.

Direct buried cables shall be laid in a clean soft sand bedding with nominal depth of 100mm below cables and at least 100mm above the top of cables.  Bedding shall be of clean small-grained sand or equivalent, free of stones and other material liable to damage the cables.

After the cables have been laid, the trenches shall be backfilled in 150mm thick layers which shall be well watered and rammed and consolidated.  Backfill containing large rock, paving materials, cinders, large/sharp angular material, or corrosive material shall not be placed in an excavation where materials may damage ducts, cables or other substructures, or prevent adequate compaction of fill or contribute to corrosion of ducts, cables or other substructures.

Trench filling shall be well-watered and compacted to obtain highest possible thermal conductivity and to avoid cavities in the trench-top covering following any settling of the soil.

The surface of refilled trenches shall be temporarily reinstated in a thoroughly safe condition until complete consolidation of the soil is achieved.

Direct buried cables shall be protected by suitable PVC cable covers, complete with marking indicating the presence of electrical cable Covers shall be standard interlocking type laid a nominal 100mm above the top layer of cables throughout their full length.  Covers shall extend to full width of cables laid, giving an overlap of at least 50mm, beyond outer cables.

A red  PVC strip marked “DANGER” and as specified in the design specification shall be installed 100mm above cable protection covers.

Adequate guarding and/or fencing shall be provided to all excavations for the protection and safety of the public, traffic and adjacent properties.

Where trench/joint pit excavations involve removal of pavement slabs/interlocked tiles, permission for taking them out shall be obtained form  the Ministry of Communications/Municipality.  All care and attention shall be excercised in their removal an later reinstatement to the entire satisfaction of the Ministry of Communication/Municipality.

Cables shall be laid direct from drums.

Sufficient number of rollers shall be provided to avid twisting of cable on its longitudinal axis during the pulling operation.

Rollers shall be placed as close as possible to avoid abrasion to the cable serving.

If power driven cable pulling in employed, it shall be by bond pulling method using steel carrier wire.

Cable laying operations shall be carried out with all care and attention, to ensure that no damage to the sheath, armor or its serving is caused during the process.

The ends of cross linked polyethylene cables shall be capped to prevent ingress of moisture into the filler or other hygroscopes elements of cable.  The caps shall remain intact during transport and laying operations.

All cable or armour shall have links to earth to enable testing of sheath.  Earth resistance shall not be greater than 10 ohms.

All schemes employing power cables having on extruded outer covering shall be installed as an insulated system.

Cable screens shall be solidly bonded to earth at each end of the route.  Bonding leads shall be of sufficient cross section to carry the maximum short circuit current.

- Manholes and Handholes

Manholes and handholes shall be constructed of class A concrete cast in place or of precast-concrete sections with leak proof joints.

Frames and covers shall be provided as indicated on the Drawings, and instructions of the concerned Authority, and be similar to existing in the site.

Manholes shall be provided with cable racks, hooks, pulling irons and other features as shown on the Drawings and as required.

A 15cm crushed-stone base shall be placed under each manhole and handhole.

Conduits entering manholes and handholes shall terminate in end bells.

Additional openings in manhole walls for future conduit entrance shall be provided where required or as indicated.  Such openings shall be sealed with necessary courses of brick.

The exterior surfaces of all manholes and handholes shall be given two heavy coats of bituminous water proofing material.

- Cable Identification

Cable Identification shall consist of:

Cable route and joint markers.

Identification markers of the cable itself.

Cable route and joint markers shall be placed at intervals of 50 metres and at points of route  alignment changes and at both ends of road for road or pipe crossings.  Cable trenches less than 100cm side shall be provided with single markers on the center line of the run.

Trenches wider than 100cm shall be indicated by markers mounted on each side of the trench at the intervals specified.

Markers shall be 60 x 40 x 10cm class B concrete block with 2.5 chamfer around edges.  The top of the markers shall be flush in paved areas, shall protrude 5cm in unpaved areas and 2cm in finished lawns.

The words “Electrical Ductbank” with directional arrows shall be impressed both in English and in Arabic on the markers used for Ductbanks.

The words “Electrical Cables” shall be impressed both in English and in Arabic on the markers used for direct burial Cables.

Similar materials suitably inscribed shall be used to indicate the position of underground joints.

All power and control cables shall be provided with identification markers at their termination, and at points along the route at intervals of not more than 2.5 metre apart.  Markers shall be made of permanent material of an approved type.

- Cable Records

Records of cables shall be carefully taken on site during the execution of the works.  The records shall show the routes, the exact location of each cable, the position of joints and terminations, the date of jointing, weather conditions prevailing, the date of testing, the name of jointer, the lengths between joints, the serial number of cable drums, the direction of lay of cable, that is A to Z ends, and where more than one cable is laid, sectional insert of cable trench.  Any other services that cross the route of the cable shall be recorded.

- Power Cables End Sealing

Power cables terminating in cable pits shall be left slack at least 2 meters.  Cable end sealing caps shall be used to terminate all cables in cable pits.

Sealing cap, shall be constructed of rubber with high density polyethylene ends, factory assembled onto removable collapsible cores supplied for site installation in a prestretched condition.

Sealing caps shall provide moisture, ozone, acid, alkali, ultraviolet and contamination resistance.  In addition they shall provide puncture resistance due to sharp conductor strands.

Sealing caps shall be similar to PST 8520, 1,2,3 as manufactured by 3M (USA).

- Power Cables Jointing

Power cables of long stretches that cannot be continuous may be jointed it an approved method of jointing suitable for directly burial.

Tape shall be of self-fusing EPR based material insulation, Corona and water resistant.  Physical and electrical properties shall be unaffected by the degree of stretch.

Tape shall be similar to Scotch 23 as manufactured by 3M (USA) or approved equal.

In-line mould assembly shall be used to encapsulate the joint.  Mould shall be similar to Scotchcast In-Line joints 91-A15,16,17 etc. as manufactured by 3M (USA) or approved equal, when using steel wire armoured cables.  Proper moulds shall otherwise be provided for other approved types of armoured cables.

Standard cable resin shall be used as recommended by the manufacturer.

- Low Current Cables Jointing

All low current cables splicing shall be done in handholes.  Splicing straight or butt shall be direct burial grade.  Splicing shall comprise a PVC transparent enclosure with end caps with required sizes and configurations to meet exact requirement.  End caps shall have 1, 2 or 3 stepped openings which shall accommodate at least 4 different cable sizes by trimming off the unwanted portion.  Stainless steel clamps shall hold the mold halves and end caps firmly in place.

Closures shall be filled with approved compound to completely encapsulate the splice for burial application.

Splicing shall be done under the following situations:

When standard cables lengths are not adequate for a long run.

When number of pairs entering a handhole is different than number of pairs outgoing.

Cables shall moreover be left 2 meters slack in the handhole.

Cable terminations shall be treated in a similar manner with end seal enclosures.  Future connection will be performed by removing this enclosure, doing the in-line jointing and encapsulating in a new enclosure.

Units shall be similar to 3M/K&B Better Buries Closure or approved equal.

- Site Tests

Power Cables

Conductor Resistance Test

When the installation of cables and associated jointing accessories has been completed, the D.C. resistance of each conductor shall be measured and recorded and shall not exceed the values given in IEC/BSS.

High Voltage Test

After the conductor resistance test, each cable shall be subjected to a d.c voltage of 2E (where E is the rated line voltage) applied for a period of 15 minutes between the conductor and the core screens which shall be connected to earth.  The test voltage shall be raised gradually to the specified value at which point the test period shall begin.  There shall be no breakdown of the electrical insulation.

For sections of cables already in service with new extensions, joints or terminations, test voltage shall be 70% of 2E.

Pilot/Control Cables

# Insulation Resistance Test

Insulation resistance test shall be carried out on all cables installed with an insulation resistance tester.

- Continuity Tests

Continuity tests shall be carried on each core of power and pilot cables, after the cables are installed and jointed.

12.  Inspection

Inspection by appropriate authority shall be carried out at the following stages of work:

  - Cable trench before laying of cables.

  - Cables laid in trench before back filling.

  - After protection tiles are laid.

  - After warning tape is placed.

Further work at each stage shall proceed only after inspection and approval.

## END OF SECTION 4

# SECTION 05

## DISTRIBUTION BOARDS

1.  General

The contractor shall supply and install the distribution boards as indicated on the DBs schematics and as shown on the drawings.

Distribution boards shall be provided with voltmeters, ammeters and instrument transformers.

Distribution boards shall be equipped with thermal magnetic moulded case circuit breakers of frame and trip ratings as shown on the drawings.

All  breakers and all devises in El. D. boards shall have current ratings as shown in the panelboards schematics.

Elect. Boards shall have 415 volt duty rating and shall have short circuit current interrupting capacity equal to or greater than the integrated equipment rating shown on the drawings.

Short circuit tests on the overcurrent devices and on the panelboard structure shall be made simultaneously.

Electrical DBs shall confirm to B.S. 5486 Part 2.

DBs circuit numbering shall be such that, starting at the top, odd numbers shall be used in sequence down the left-hand side and even numbers shall be used in sequence down the right-hand side.

All breakers and all protective devices shall be manufactured by Square D (U.K.), Moellar (Germany), and Merlin Gerin (France) or approved equal.

2.  Cabinets and Fronts

All DBs shall be enclosed in a steel cabinet.  Cabinet shall be of sufficient size to provide a minimum gutter space of 10 cm on all sides.  The thickness of the sheet steel shall be minimum 1.5 mm.

Fronts shall include doors and have flush, brushed stainless steel cylinder tumbler – type locks with catches and spring loaded door pulls.  The flush lock shall not protrude beyond the front of the adjustable indicating trim clamps which shall be completely concealed when the doors are closed.  Fronts shall have approved

directories with name of panel, number of phases, wires and voltage written on them.  Doors shall be mounted by completely concealed steel hinges.  Fronts shall not be removable with door in the locked position.  A circuit directory card shall provide a space of at least 0.5cm high x 7cm long or equivalent for each circuit.

The directory shall be typed to identify the load fed by each circuit.

Fronts shall be of code gauge, full finished steel with rust-inhibiting primer an baked enamel finish.  Color shall be gray to BS 381C or approved equal.

Joints shall be welded, galvanized and reinforced where necessary an galvanized after fabrication.

3.  Panelboard Bus Assembly

Bus for connections to the branch circuit breakers shall be the “Distributed Phase” or “Phase Sequence” Type.

Three-phase, four-wire bussing shall be such that any three adjacent single-pole breakers are individually connected to each of the three different phases in such a manner that two or three pole breakers can be installed at any location.  All current carrying parts of the bus assembly shall be plated.

Main and neutral buses shall be minimum 98% conductivity rectangular copper bars, provided with bolted-type lugs as necessary.

Buses shall be rigidly supported an insulated and be so designed that branch circuits can be removed without disturbing adjacent units or changed without additional machining, drilling or tapping.

Necessary bussing, drilling and blank plates shall be provided for installation of future circuits when so indicated in the Schedules on the Drawings.

All screws and bolts used for making copper connections shall be equipped with lock washers.  Riverted connections will not be acceptable.

Mains shall be equipped with solderless pressure indent type connectors and have means to prevent swiveling of connector.

Neutral busbars shall be full size and shall incorporate one neutral terminal for each single pole and neutral way.

Aluminium shall not be used for any interior panelboard parts.

Back pan or mounting on which buses and branches are mounted shall be rigid to properly support the component parts.

Reinforcing of back pan shall be by flanging or addition of angle iron.

Buses, connectors, and terminals shall be silver plated to a minimum thickness of 0.1mm.

4.  Earthing

An acceptable terminal bar for equipment earthing conductors shall be provided with minimum number of cable terminations equal to the single pole number of ways of the panelboard.

Cabinets shall be provided with an earth connector welded to it.

5.  Moulded Circuit Breakers

Moulded case circuit breakers shall have trip settings, and number of poles, as indicated on the Drawings.  All circuit breakers shall have their ampere trip rating clearly marked and visible.

Breakers shall have quick-make, quick-break, toggle mechanisms; and shall provide positive trip-free operation on abnormal overloads.  Stationary and movable contacts shall be adequately protected with effective and rapid are interruption.  Each pole of the breaker shall be equipped with an inverse time delay thermal overcurrent trip  element and magnetic instantaneous overcurrent trip elements for common tripping of all poles for multiple breakers.  Multiple pole breakers shall have a single handle mechanism.  Automatic tripping shall be indicated by the breaker handle assuming a clearly distinctive position from the manual ON and OFF position.

Circuit breakers shall have minimum RMS symmetrical interrupting capacities equal to the values indicated below for moulded case circuit breakers unless otherwise indicated, and shall in no case be less than the bus bar short circuit bracing of the panel board:

### Frame Size : Interrupting KA at 415 V

### [up to 63 A-(6KA)], [80-160A-(25KA)], [200-630A-(50KA)], [Above 630A-(100KA)]

Moulded case circuit breakers shall comply to BS 4752 Part 1.

6.  Panelboard Installation

Panelboard shall be aligned, leveled and securely fastened to the building.

Connecting conduits shall not be used to support the panelboard.

All unused openings in panelboard cabinets shall be properly closed.

Panelboard interiors shall not be installed in cabinets until all conduit connections to the cabinet have been completed.

Trim shall be installed plumb and square to finish painting.

Trim for flush mounted cabinets shall be installed in plaster frame, flush with finished wall.

Concealed surfaces of cabinets shall be given on site a heavy application of emulsified asphalt prior  to installation.

Free standing panelboards when installed in electrical closets, or rooms with depressed floors shall be provided with galvanized steel support structures to raise the level of the panel to 10cm above the original floor level.

## END OF SECTION 5

# SECTION 06

ELECTROMECHANICAL CONTROL PANEL

1.  General

The Contractor shall supply and install the pump control panel (indicated PCP, EPCP) as indicated in the Schedules, where shown on the Drawingsand as herein specified.  They shall include bus assembly, cabinet and front, molded case circuit breakers, motor starters, and all necessary parts to install complete unit.

Pump control panel shall be as manufactured by General Electric (USA), Duplex Motor Controller as Manufactured by Square D (USA), Allen Bradley (USA) or approved equal.

2.  Circuit breakers

Circuit breakers shall be molded case bolt-on type furnished only where indicated on the Drawings, and shall be as specified for under “DISTRIBUTION AND POWER PANEL BOARDS”.

3.  Current Limiting Circuit Breakers

Current limiting circuit breakers shall have a maximum interrupting rating of 100 KA rms symmetrical amperes.  All circuit breakers shall be UL listed and meet NEMA Standard No. AB1-1975, and Federal Specification W-C-375B/GEN where applicable.

Current limiting circuit breakers shall be supplied in unit molded case construction and shall consist of a common trip, thermal magnetic circuit breaker with an independantly operating limiter section in series with each pole.

The conventional breaker section shall have an over center, trip-free toggle-type mechanism with quick make, quick break action and positive handle indication.  A button shall be provided on the cover for mechanically trippin the circuit breaker.  The current limiting breaker shall have permanent trip units containing individual thermal and magnetic trip elements in each pole.  The thermal trip element shall be calibrated for 50 °C ambient temperature.

The limiter section shall consits of three current limiting elements electrically cordinated wit the conventional circuit breaker trip elements.  The contacts of the limiter section shall be electromagnetically and electrodynamically opened and held open until interruption is complete.  The unit shall not contain replaceable elements and the limiter shall automatically reset after circuit interruption.

On high level fault currents the limiter portion of the circuit breaker shall operate to limit the rise of fault current.  Integral resistance shall be introduced into faulted circuit to dissipate and limit let-through energy and to provide a voltage transient-free interruption at rear unity power factor.

The current limiting circuit breaker shall have fron removable lugs.  Lugs shall be U.L listed for copper conductors.

4.  Starters

Starters shall incorporate contactors made of a glass polyester case with silver cadmium oxide alloy contacts, molded coils, stainless steel kickout springs, U-type magnet and a shock absorber baseplate.  Overload relays shall be three-pole, inverse and ambient compensated type.

5.  Control and Miscellaneous Devices

Control relays shall be the heavy duty, industrial or machine tool type with at least two normally closed and two normally open spare contacts.  Relays shall be rated NEMA designation A600 or N600, as required.

Control Power transformer shall be provided as applicable to limit the control voltage to 240 volts, and to eliminate th need for phase-toneutral voltage.  It shall be 2- winding, dry type and of suitable VA rating but not less than 75 volt-amperes.

Automatic Alternator, if any, shall control the operation of two seperately enclosed motor starters so that they operate alternately at successive closing of a single pressure or float switch (to equilize equipment wear).  The second float or pressure switch is set to start the idle pump in case one pump will not handle the load.  Both pumps then working to handle the demand.

Pushbuttons shall be heavy duty, oiltight type with removable contact blocks.  Contact ratings shall be 10- ampere continuous current.  Pushbuttons shall be provided with chrome-plated metal or anodized aluminium mounting rings.

Selector switches shall be heavy-duty oiltight type with removable ocntact blocks and bat type lever operators.  Contact ratings shall be 10 ampere, continuous current.  Selectors shall be provided with chrome-plated metal or anodized aluminium mounting rings.

Indicating lights shall be heavy-duty, oiltight type with glass lenses.  Lights shall be equipped with reduced voltage transformers and 6-volt lamps.  Indicating lights shall be provided with chrome-plated metal or anodized aluminium mounting rings.

Extra secondary contacts for one or more remote controls terminal wiring bloks, etc.  shall be provided as required.

All devices shall be suitable for operating at 127 volts, 60 Hz when connected between phase and neutral, and at 220 volts, 60 Hz when connected between two phases.

6.  Labeling

Components of each module shall have individual printed label identifying size, voltage, ampere rating, etc.  Starter wiring diagram and overload thermal cutout device installation instruction shall be attached to each starter door.

7.  Intercabling

It shall be completely done in factory for all cabling within the Panel.

8.  Terminal Blocks

Terminal blocks shall be installed and interrnally connected by the manufacturer, for all interanl and exterrnal wire number.  Each terrminal point shall have a large marking area or to be equipped with two marking area.

In addition, with each group of terminals per unit, a minimum of 20% unconnected extra non-load terminals, but not less than one, shall be provided for the Contractor’s external connections.

9.  Operating Handle

It shall be interlocked with cover to prevent opening of cover while handle is in the “ON” position.  The handle must be moved to “OPEN COVER” position for door opening.

## END OF SECTION 6

# SECTION 07

## CONDUITS AND FITTING

1.  General

The Contractor shall supply and install a complete conduit system as shown on the Drawings and as herein specified.  The system shall include conduits, fittings (coupling, bends, boxes, cover plates, reducers, adapters, etc.)  and all necessary part to  install a complete conduit system.

Conduits and fittings shall be distinctively marked as manufactured for electrical purposes.

Conduit runs are shown diagrammatically to outline the general routing of the system.  The installation shall be made to avoid interfering with pipes, ducts, structural members, or other equipment.  Should structural or other interference’s prevent the installation of the conduits, or setting of boxes, cabinets, or other electrical equipment, as indicated on the Drawings, deviations must be approved by the Engineer, an after approval, shall be made without additional charges.  The number of conduits shall not be less than that indicated on the Drawings.

Conduits and conduit fittings shall be so designed and constructed that they ensure reliable mechanical protection to the cables contained therein, and shall withstand the stresses likely to occur during transport, storage and installation.  They shall be marked with the marker’s name or trade mark.  Marking shall be indelible and easily legible.

Conduits shall have a minimum ¾” (outer diameter) size and shall be adequate for proper and easy wire pulls, and in no case shall the wires occupy a cross-sectional area of more than 30% of the inner conduit cross-section.

The inside and outside surfaces of conduits shall be smooth and free from burrs, flash, and similar defects.  Thickness of wall shall be uniform.

The interior and ends of conduit fittings shall have no sharp edges; surface and corners over which the cables are likely to be drawn shall be smooth and well rounded.

Conduits and fittings shall have adequate mechanical strength.  Conduit when bent or compressed, or exposed to impact or extreme temperatures, either during or after installation, shall show no cracks and shall not be deformed to such an extent that introduction of the cables are likely to be damaged while being drawn in.

Conduit entries of fittings shall be so designed that a reliable joint can be made between the conduit and the fittings.

Conduits and fittings shall be BS tested or approved equal.

All accessories and fittings such as bends, straps, double straps, junction boxes, bushes, etc. shall be provided as required.

2.  Conduits – Metallic

Conduits shall be constructed from solid drawn mild steel, outside and inside galvanized.

The galvanized coat of zinc shall be of uniform thickness applied to outside and inside including the threads.

Each conduit shall be straight, free from blisters and other defects, cut square and taper reamed, furnished with coupling in standard lengths, threaded each end.

Couplings shall be applied at one end of each conduit and color coded plastic threaded protectors to the other end.  The interior threaded surface of each coupling shall be galvanized to ensure 100% galvanic protection on all surfaces.

The galvanized coating shall be of such quality and uniformity that a sample of the galvanized conduit will not show a fixed deposit of copper after four immersions of dips in a standard copper sulphate solution.

The galvanized coating on the conduit shall be sufficiently elastic to prevent cracking or flaking when a sample of finished conduit is bent 90º at a minimum temperature of 15ºC.

Conduits shall be manufacture by Simplex (UK) or approved equal.

3.  Conduits & Fittings – Non-Metallic

Non-metallic conduits shall be heavy gauge, high impact rigid PVC Type A (Metric) or Type AH (Imperial) unless otherwise indicated, having a maximum continuous service temperature of 70 C or more.  Conduits and fittings shall comply with BS 4607.

Conduits and fittings shall be manufactured by EGATUBE (UK), MARSHALLTUFFEX (UK) or approved equal.

4.  Conduits – Flexible

Flexible conduit shall be constructed by square locked galvanized steel with a PVC outer covering.

Conduits shall be manufactured by Kopex (England) or approved equal.

5.  Boxes – Metallic

Boxes shall be constructed of cast metal as specified hereinafter.

Boxes used for hanging fixtures shall be suitable for ceiling roses.  Boxes for installation in concrete shall be concrete tight.  Shallow boxes shall not be used unless building construction is such that it is impossible to use standard depth boxes.

Boxes shall be constructed of feraloy cad/zinc electroplated with aluminum cellulose lacquered.

Blank covers shall be constructed of sheet steel with gasket and stainless steel screws except for damp and wet locations.

In damp and wet locations blank covers shall be constructed from cast feraloy with gasket and stainless steel screws.

Floor boxes shall be water tight one piece cast iron color-coated inside and out for additional corrosion resistance.  Treaded steel cover shall be Electro-galvanized.  Boxes shall have adjusting screws.

Boxes shall be manufactured by Simplex (UK) or approved equal.

6.  Boxes – Non-Metallic

Boxes shall be standard PVC as specified under conduits and fittings.

Boxes shall be purpose made, to suit the wiring device to be used with.

Boxes shall be VDE tested, flame resistant.

Boxes shall be manufactured by Spelsberg (Germany), or approved equal.

7.  Installation of Conduits

Conduits embedded in ceiling slab, in walls and underfloor shall be non-metallic type.

Conduits exposed above false ceiling shall be non metallic type.

Exposed conduits other than above false ceiling shall be rigid steel type.

All conduit work and plastering shall be complete before wires are pulled in unless otherwise permitted by the Engineer.  Conduit shall be plugged with cork and boxes covered appropriately to avoid filling with plaster.

Conduit runs between outlets shall not contain more than three quarter bends or equivalent.  The maximum run between two outlets shall not exceed 25 meters for straight runs and 10 meters for runs with one or more bends.  Pull (draw in) boxes shall be provided otherwise whether so indicated on the Drawings or not.  Location of pull boxes shall be approved by the Engineer.

Conduits shall be installed without causing any damage to the structural members.

All bends shall be carefully made to prevent distortion of the circular cross-section.  Bends made on site in conduits shall have an inside radius of not less than nine diameters.

Where bends of less than nine diameters are necessary, standard factory elbows shall be used:  however the conduit size chosen shall be such as to permit a cable-bending radius within the factory elbow of at least eight times the cable diameter.

Conduits in slabs shall be installed as close to the middle of the concrete slabs as practicable without disturbing the reinforcement.  The outside diameter shall not exceed one third of the slab thickness, otherwise the Contractor shall use more than one conduit.  Conduits shall be place not closer than three diameters on centers.

Conduits in slabs shall be placed parallel to the main reinforcement steel in the slab.

Top of any conduit in slabs shall be at least 2cm below the finishes floor surface, unless otherwise indicated or authorized.

Conduits in slabs running parallel to beam axis shall not run above beams.

Exposed conduits shall be installed parallel or at right angles to walls and ceiling beams.  All changes in direction shall be made as far as possible with approved bends, elbows, and pull boxes.  The spacing between parallel runs shall be uniform throughout.  Unless otherwise indicated conduits shall be held securely in place by standard factory spacer bar saddles, spaced not more than 1.5, 2.0 and 2.4 meters for 2mm, 25mm and 32mm and larger conduit sizes respectively for metallic conduits and at 1 meter for non-metallic conduits.

Unless otherwise indicated, raceways exposed above false ceilings shall be supported from the slab above the ceiling in the same manner as exposed raceways.  Raceways shall not be supported from false ceiling supports.

Couplings, expansion couplings, strap saddles, spacer bard saddles, spring clip saddles, conduit clips, adapters, etc. shall all be standard factory conduit accessories.

Flexible metallic conduits shall be used only for connections to motors, or to other equipment subject to vibration or adjustment or to make connections to lighting fixtures in false ceilings.  Each connection shall contain at least one quarter bend so that no vibration can be transmitted behind the flexible connection.

In damp and wet locations all couplings, expansion coupling, strap saddles, spacer bar saddles, spring clip saddles, conduits clips, screws, adapters shall be corrosion proof, approved or use in damp and wet locations.

In damp and wet locations flexible conduits shall be liquidtight.

In damp and wet locations the entire conduiting system, including boxes, fittings, panelboards etc.. shall be mounted so that there is at least 7mm air space between it and the wall supporting surface.

All conduits shall be carefully cleaned before and after installation.  All ends shall be reamed free from burrs, and inside surfaces shall be free from all imperfections likely to injure the cable.

After installations of each complete new conduit run, the run shall be snaked with a band to which shall be attached and approved tube cleaner equipped with an approved cylindrical mandrel of a diameter not less than 85% of the nominal diameter of the conduit.  All conduits through which the mandrel will not pass shall be removed and replaced the Contractor at his own expense.

All field cuts in conduits shall be square, and cut ends shall be filed and shall have burrs removed.  An insulating bushing shall be installed on each end of conduit, unless the connector is designed to prevent contact with the cut end.  All connections shall be mechanically strong and tight, and made up properly with approved connectors.  No running threads shall be permitted.

Conduits for TV system shall have at least 10cm bending radius.  Two bends might be necessary for the transition from floor to wall.

8.  Installation of Boxes

Boxes of ample capacity shall be provided at every junction of conduit system and as required by the Specifications.

All boxes shall be securely fastened.

Blank plates shall be installed on outlet boxes in which no apparatus is installed, or the apparatus installed does not provide a suitable cover for box.

Device boxes shall be used for all wiring devices.

Non-metallic boxes shall be used only for concealed conduit work, and for conduit work above false ceiling.

Exposed boxes for switches, socket outlets and other devices shall be cast metal boxes.

Cast metal boxes shall be installed in such a manner that the conduit connections and the gasketed cover are dusttight.  All unused openings shall be closed with pipe plugs and compound.

Boxes for similar equipment shall be mounted at uniform height within the same or similar area.  Mounting shall be as shown on the Drawings.

Device box shapes and sizes shall be determined by the type and size of wiring devices for which they serve.

Boxes fixed inside false ceiling shall be provided with mounting brackets for rigid fixing to structure members or other means of support.

9.  Sleeves

Sleeves shall be provided for exposed conduit or cables passing through interior floor slabs and walls.  All openings shall be sealed with mastic compound.  The compound shall not cause any corrosion or harmful effects to the conduit.  Sleeves passing through floor slabs shall be flush with the bottom of the slab, extend approximately c above the surface of the floor and be watertight between sleeves and floor slab.

Sleeves passing through exterior walls and slabs shall be wall entrance seals of watertight construction.  They shall be watertight between slab and sleeve, and between sleeve and conduit and cable.

These wall entrance seals shall be of malleable iron with black paint finish and PVC sleeve, with a watertight sealing gland.

Sealing gland design shall be such that they may be tightened any time after installation.  Wall entrance seals have oversized sleeves of proper length to position the sealing-gland housing with the wall faces.

After the cable has been pulled through the duct, a seal shall be made round it, within the duct with a bituminous mastic compound, making the seal watertight.

10.  Adhesives and Joints

Conduits shall be jointed and terminated utilizing the appropriate components as supplied by the conduit manufacturer.

Permanent adhesives to produce a rigid watertight joint shall be used with standard couplers and accessories.

A flexible (non-hardening) adhesive shall be used where expansion facilities are required.

11.  Expansion Joints

Expansion coupling shall be provided at every 6 meter run of exposed conduit work, at expansion joints or as required to compensate for thermal expansion and contraction of both exposed and embedded conduits.

### END OF SECTION 7

# SECTION 08

CABLE TRUNKING

1.  General

The Contractor shall supply and install trunking for cabling as shown on the Drawings and as herein specified.  The system shall include but not limited to standard rectangular trunking sections, bends terminations, conversions, reducers, site made bends, offsets, risers, and all necessary parts to install a complete trunking system.

All parts shall have a minimum of 1.2 mm thickness.

Cable trunking shall be consturcted from heavy gauge PVC meeting BS 4678 Part 4 or approved equal, unless otherwise indicated on the Drawings.

The trunking system shall be manufactured by Davis (UJ), Egatube (UK), Walsall (UK) or approved equal.

2.  Trunking Sections

Sections shall be interconnedted with conneting sleeves.  Grounding continuity shall be ensured by means of grounding straps.

Cover plates shall be made from hot-dipped galvanized sheet steel, of standard sections.

Cover plates shall be secured by anchored turn buttons and locking bars.

Sections shall have ample space for the cabling they include.

3.  Terminations, Conversions, etc.

Terminations, conversions, bends, reducers, site make bends, offsets, risers, etc. shall all be provided as required.

Connections shall be made to other types of reaceway in an approved manner with fittings manufactured for the purpose.

4.  Installation

Trunking shall be securely fixed to walls, ceiling or multibeam trunk to the approval of the Engineer.  It shall be installed such that it shall not be obstructed by other trades.  Adjoining sections shall be securely fastened together to provide a rigid joint.

The sum of cross-sectional areas of all contianed conductors shall not exceed 20% of the interior cross-sectional area of the trunking.

Trunking shall inlcude all necessary cable retainers.  Runs of trunking shall be parallel or perpendicular to walls and partitions.

5.  Supports

Trunking when run horizontal shall be securely supported at intervals not exceeding 1.5m, unless specially approved for supports at greater intervals, but in no case shall the distance exceed 3 m.

Trunking when run vertically shall be securely supported at intervals not exceeding 4.5m and shall have not more than one joint between supports.

6. Skirting Trunking

The trunking shall have two compartments one for power cables and the other for telephone and low current wires, as detailed on the Drawings.

Trunking body shall be manufactured from 1.2mm nominal thickness zinc coated sheet steel in standard 2 meter lengths, with spot welded partition, each length supplied with one back connecting palte one earthing strap, with plated mushrooms head steel screws and shakeproof washers.  The cover fixings are secured by an itnernal fixing bridge and external fixing strap, both of which are mobile down the length of skirting to any given prosition, the covers shall be cut to suit on site.  Metal work shall be finished metallic silver enamel inside and outside to receive site painters finished coat.

Skirting trunking shall have engough space for standard receptacles and telephone outlets both being screened and totally enclosed by sheet metal.

Skirting trunking elbows shall be easil installed wherever necessary on site.  Similarly receptacle and telephone outlets shall be inserted at any place on the trunking with the same ease.

Skirting trunking shall be as manufactured by DAVIS (UK) or approved equal.

7.  Bench Trunking

Bench trunking shall be manufactured from a minimum of 1.6mm galvanized mild steel with 0001 mm zinc deposit.  Cover shall be of minimum 1.2 mm galvanized steel.  Fittings shall be manufactured from the same steel as body and covers.  Socket/switch socket plates shall be provided as one or two gangs and required.  Connector blocks with four pinching screws shall be provided as required.

Bench trunking shall be manufactured by Walsall (UK) or approved equal.

### END OF SECTION 8

# SECTION 09

WIRES & CABLES

1.  General

The Contractor shall supply and install all wires and cables necessary for the complete Electrical System, as indicated on the Drawings, as required, and as specified herein.

2.  Single Core Power Cables

Single core power cables running in concrete trenches such as those running from the transformer room to the electrical room equipment shall be single core, complying with the specifications indicated hereinafter.

Conductors shall be plain annealed copper complying with BS 6360.

Insulation shall consist of extruded PVC complying with BS 6746, with minimum 2.8 mm thickness for the 630mm2 conductor.

Sheath shall be of an extruded layer of black PVC of minimum 2.2 mm thickness for 630mm2 conductor.

3.  Wires & Cables – Lighting & Power

Conductors shall be of high conductivity annealed copper with concentric stranding for stranded conductors, to BS 6360, or approved equal.

Minimum conductor size used shall not be less than 2.5mm2.

All wires for lighting and power systems pulled inside conduits shall be single core, insulated with PVC compound, of grade not less than 450/750 volts, to BS 6004.

Wires in boiler rooms (if any) shall be MICC Cables to BS 6207.

Multicore cables shall be unarmored unless otherwise indicated, PVC sheathed.  Armoring if required shall consist of galvanized steel wire or double tape with overall PVC extruded sheath, of grade not less than 600/1000 volts to BS 6346.

Single core armored cable where used shall have a hard drawn aluminium wired armoring.

Conductors shall be solid-stranded.

Flexible cords for connection of fixtures to circuit-wiring shall have finely stranded copper Conductor with a PVC insulation, type NYFAF, 380 V grade.

Wires and cables shall be manufactured by BICC (UK), Pirelli (UK) or approved equal.

4.  Flexible cords

Cords used for water heater connections shall be of high conductivity tinned copper wires, (2.5mm2 unless otherwise indicated) insulated with ethylene propylene rubber, three cores twisted together, filled and sheathed with chlorosulponated polyethylene (EPR, CSP), 300/500 V rated, and shall withstand an operating temperature of 85 C, to BS 6500.

Cords used for pendant lighting points and between lighting outlet above false ceiling to lighting fixture shall be circular two core (1.5mm2) silicon rubber insulated, glass fiber braided 300/300 V rated, shall withstand an operating temperature of 150 C, to BS 6500.

Cords used for extract fans shall be of plain annealed copper conductor (1.5mm2), PVC insulated, circular twin cores twisted together, PVC overall sheated 300/500 V rated, shall withstand an operating temperature of 70 C, to BS 6500.

Cords shall be manufactured by BICC (England), AEI (England) Pirelli (England), or approved equal.

5.  Wires and Cables – Telephone

Indoor wires and cables shall comprise solid tinned copper conductor of 0.6mm conductor diameter, PVC insulated, polyester tape overall covered, PVC overall sheathed.  An additional ground wire of diameter not less than 0.7 mm shall also be provided.

Underground outdoor cables shall be directly buried type and shall comprise solid plain copper conductor of 0.6mm conductor diameter polythene insulated, polyester and PVC-tape covered, black polythene sheathed, two layers of galvanized steel tape armored, black overall polythene sheathed.  An additional ground wire shall also be provided.

6.  Cables – Fire Alarm

Cables of fire alarm system shall be of the mineral insulated, metal sheathed type.  Cable shall have a highly compressed refractory mineral insulation (magnesium oxide) enclosed in a seamless copper sheath, overall covered with PVC and shall be installed in strict accordance with manufacturer’s instruction.

7.  Flame Retardant Cable

Cable shall be supported at not more than 75 times the cable outside diameter intervals by means of approved staples, straps, hangers or other fittings to building structure or to specially designed brackets.

At termination points cable shall be provided with an approved seal immediately after stripping to prevent entrance of moisture into the mineral insulation.  When cable is connected to outlet boxes, panels or fire alarm equipment, fittings shall be of the threaded-gland type with seals filled with an insulating compound approved for the atmospheric and service conditions in which the cable is used.  Stripping of cable ends, installation of fittings, application of insulating compound, and terminations shall be made according to manufacturer’s instructions.  Cables shall be embedded plaster where other conduit work is concealed.

Cables shall be manufactured by Pyrotenax or approved equal.

8.  Control Cables

Control cables where used underground direct burial shall comprise stranded annealed copper conductor of minimum 2mm2 cross-section insulated with high dielectric polyvinyl chloride, nylon sheathed with a tape binder applied over the assembly, overall PVC jacketed.

Number of conductors shall be equal to the maximum number of functions plus 20% spare.

Cables shall be 300/500V insulation grade.

Junction boxes shall include all necessary terminal connector boards with proper labels.

Contractor shall make sure that the cross-sectional area of the conductors are sufficient to cater for the voltage drop due to the long runs involved.

Control cables where used in ducts underground or in conduits above ground shall comprise stranded annealed copper conductor of minimum 2mm2 cross-section for cables in ducts and 0.75mm2 for cables in conduits insulated with high dielectric polyvinyl chloride, and PVC sheathed.

9.  Installation of Wires & Cables

All wires shall be installed in accordance with the applicable provisions of the approved codes and as indicated on the Drawings.

The  number of wires and  sizes  of conduits  indicated on the Drawings are a guide only and are not necessarily  the correct number and sizes necessary for the actual equipment installed.  The Contractor shall install as many wires  and conduits as required and necessary for a complete electrical system, and shall provide adequately for the equipment actually to be installed.

Where more than one conductor is used per phase, each phase, neutral if any and ground wires shall be run in each metallic or non metallic conduit.

Conductors shall be continuous from outlet to outlet and nasplices shall be made except within outlet or junction boxes.

At every outlet and pull box, wires and cables passing through, shall be left slack by an amount equivalent to 15cm of cable length to allow inspection and connection to be made therein.

No cable bend shall have a radius of less than eight times its diameter.

The Contractor shall not change any circuit number, especially from a phase to a different phase.  If such a change is necessary due to modification on site, the Contractor shall bring this matter to the attention of the engineer.

All conductors to be contained within a single conduit shall be drawn in at the same time.

A wire pulling compound shall be applied to conductors being drawn through conduit.  Pulling compound shall be soap tone or other approved material.

Only cables forming part of a lift installation if any may be run in a lift shaft.

Wires and cables for feeders, sub-feeders, control, and branch circuit wiring shall be color coded as follows:

| Color | Phase |
| --- | --- |
| # Brown | R |
| Brwn-Red | S |
| Brown-Black | T |
| Blue | Neutral |
| Yellow | Equipment grounding |

Wire and cable size shall be as indicated on the Drawings; however in no case shall their size be smaller than required by the approved Code.

Unless otherwise indicated, no conductor for lighting smaller than 1.5mm2 and for power wires  smaller than 2.5 mm2.

All branch circuits for lighting and appliances shall be single conductor cables run inside conduits, unless otherwise indicated.

Feeders and sub-feeders shall be either single conductor wires pulled inside conduits or multi-conductor cables run exposed on walls or in trenches as shown on the Drawings.

Single cables shall be fixed directly to walls or ceilings.  Where 2 or more cables are run in parallel, they shall be fixed on galvanized steel perforated trays or on other approved special cable supporting and protecting arrangement.

Cables shall be fixed to supporting structures with approved galvanized cast steel clamps at distances not exceeding 20 diameters.

Armored cables used in vertical shafts shall be the steel wire armored and not the tape type.

No joints or splices shall be accepted on main feeders.

10.  Identification of Wires & Cables

Individual conductor or circuit identification shall be carried throughout, with circuit numbers or other identification clearly stamped on terminal boards and printed on directory cards in distribution cabinets and panelboards.

In junction boxes, cabinets, and terminal boxes where the total number of control, indicating, and metering wires is three or fewer and no terminal board is provided, each wire including all power wires, shall be properly identified by means of a plastic-coated, self-adhesive, wire marker.

Wires including motor leads and other power wires too large for connection to the terminal boards shall be identified by wire markers as specified above.

In manholes, handholes, pull boxes, junction boxes and at both terminals each wire and cable shall be properly identified by a laminated plastic tag located so as to be easily seen.  Wires and cables shall be identified by cable number indicated on the Drawings.

11.  Connectors and Terminal Blocks

For the wiring of circuits consisting of wire sizes 6 mm2 and smaller such as for lighting branch circuits, self-insulated pressure type connectors shall be utilized for all splices or joints.

For the wiring of circuits consisting of wire sizes 10 mm2 and larger shall be of the bolted pressure type, with a preinsulated sleeve.

Connectors shall be manufactured from high conductivity copper, Electro tin-plated.

Connector bodies shall be manufactured from Polyamide.

12.  Cable trays and Supports

Cable trays shall be manufactured from mild steel of a minimum thickness of 2mm.  They shall be light or heavy duty type as required with return flanges, and hot-dip galvanized finish.  Bends, corners, etc.. shall be specially manufactured for the purpose.

All supports and accessories like hangers, channels, bolts, nuts, cable ties, conduit clamps, shall be furnished as to function, to the manufacturers standard.  Metallic elements shall be hot dip galvanized.

The contractor shall provide technical catalogues and shop drawings to illustrate the sufficiency of the supports and tray sections thicknesses.

The installation shall have a design assuming double the actual load in addition to the safety factor recommended by the tray manufacturer.

Cable trays, supports, and accessories shall be manufactured by BICC (England) or approved equal.

13.  Cable Ladders

Cable ladders shall be manufactured from 14 SW Mild steel, with hot-dip galvanized finish.

All parts like flat elbows, offset reducers, straight reducers, cross pieces, tee pieces, drop outs, etc.. as well as accessories shall be furnished as to function, and to the manufacturers standards.

Cable ladders, part and accessories shall be manufactured by BICC (England) or approved equal.

14.  Cable Glands

Cable glands shall be provided at the termination of armored cables at the enclosure of a distribution board or any other equipment.

Cable glands shall be indoor or outdoor type, ordinary or weatherproof according to the location of the termination, to the approval of the Engineer.

### END OF SECTION 9

SECTION 10

LIGHTING FIXTURES

1.  General

The Contractor shall supply and install lighting fixtures including but not limited to lamps, ballasts, accessories, fixing hardware necessary for installations, as shown on the Drawings, as required, and as herein specified.

Fixture, Housing, frame or canopy, shall provide a suitable cover for fixture outlet box or fixture opening.

Fixtures shall not cause a temperature exceeding 90° centigrade on any outside surface.

Fixtures shall comply with all applicable requirements as herein outlined unless otherwise specified or shown on the Drawings.

Manufacturer’s name and catalogue reference of lighting fixtures are given for general reference only.  It shall be understood that the actual fixtures supplied shall meet all the requirements of the Specifications, and, if necessary, the standard fixture indicated for reference, shall be modified accordingly.  Material of other manufacturers complying with the Specifications will be considered on equal basis.

Fixtures shall bear manufacturer’s name and the factory inspection label.

Fixtures shall be completely wired and constructed to comply with IEC Publication 162, unless otherwise specified.

Relamping the fixture shall be possible without having to remove the fixture from its place.

Certain fixtures may be shown in provisional position.  They shall be exactly located as soon as the final layout of equipment is known.

Fixtures that are used under canopy or directly exposed to weather shall be considered as being outdoor type.

2.  Construction - General

Indoor fixtures shall be constructed of 0.7 mm thick steel minimum.  If other metals are used they shall be of the required thickness to have at least the same mechanical strength.

Cast portions of fixtures shall be not less than 1.5 mm thick.

Metal parts of the fixtures shall be completely free from burrs and tool marks.  Solder shall not be used as a mechanical fastening device on any part of the fixture.

Fixtures with visible frame shall have concealed hinges and catches.

Recessed fixture shall be constructed so as to fit into ceiling without distorting either the fixture or the ceiling.  Plaster rings shall be provided for plaster ceilings.  The Contractor shall coordinate the dimensions with the false ceiling tile or panel dimensions.

Outdoor fixtures (under canopy or directly exposed to the weather) shall be constructed of an appropriate weather resistant material including gasketing preventing entrance of water into wiring and shall be marked by the manufacturer “Suitable for Outdoor Use”.

Fixtures with hinged diffuser doors shall be provided with spring clips or other retaining devices to prevent the diffuser from moving.

Bathroom fixtures shall marked as being suitable for damp locations.  Lamp holders of  such fixtures shall be provided with a protective shield to prevent contact with the lamp cap.

Fixtures with exposed metal parts shall be provided with a means for connecting an equipment grounding conductor for such fixtures.

Incandescent fixtures shall be equipped with porcelain medium base with nickel-plated shells.  Sockets shall be bayonet type for lamps up to and including 150 watts and right hand screw type for lamps 200 watts and above.

Pendent fixtures and lamp holders shall be provided with ball type aligners.

3.  Construction – Fluorescent Fixtures

Fixtures shall be provided with white click-in type lamp holders.

Pendent individually mounted fixtures 60cm and longer shall be provided with twin stem hangers.  Stems shall have ball aligners and provision for a minimum of 2.5cm vertical adjustment.

Diffusers shall be manufactured from one piece non-glued methacrylate.

Mirror system light controlled fixtures shall comprise a metal encased aluminium mirror system with plastified aluminium mirror stips forming a parabolic reflector.  Lamps shall be screened in the longitudinal direction by means of matt-white louver partitions.

Clear smooth diffusers shall be smooth from outside, finely grained from inside.

Corrosion resistant fixtures shall comprise polyester resin fiber-glass reinforced body, dust and splash-proof.

Damp-resistant fixtures shall comprise polyester resin fiberglass reinforced body, dust and jet-proof.

Explosion proof fixtures if any shall be suitable for hazardous location specially for paint spray booths, and locations having deposits of readily combustible paint residue.  All exposed hardware shall be stainless steel.  All exterior material shall be non-sparking.

4.  Finish

All hardware shall be bonderized, cadmium-plated, given a corrosion-resistant phosphate treatment or other approved rust inhibiting prime coat, to provide a rustproof base before application of finish.

Finish shall be baked enamel.

Non-reflecting surfaces such as fixture frames and trims, shall be finished with baked enamel paint, unless otherwise specified.  The color of the paint shall be as indicated on the Drawings or as directed later by the Engineer on Site.

Light reflecting surfaces shall be finished with baked white enamel paint having a reflection factor of not less than 85%.

All parts of the reflector shall be completely covered by the finish and free from irregularities.

Unpainted surfaces shall be finished with a clear lacquer except for anodized or “Azac” surfaces.

After finish has been applied and cured, it shall be capable of withstanding a 1cm radius bend without showing signs of cracking, peeling or loosening from the base metal.

Finish shall be capable of with standing 72 hours exposure to an ultra-violet RS sum lamp placed 10cm from the surface without discoloration, hardening, or warping and shall retain the same reflection characteristics after exposure.

5.  Wiring

Wiring within fixture and for connection to the branch circuit wiring up to the outlet box of lighting point shall not be less than 1.5 mm2.  insulation shall be silicone rubber, finish shall be glass braid.  Suitable for 150 °C normal service temperature, 300/300 volts.  Cable entry to fixture shall be dust sealed.

6.  Installation

Fixtures shall be installed at mounting heights as detailed on the Drawings or as instructed on Site by the Engineer.

Fixtures and/or fixture outlet boxes shall be provided with hangers to adequately support the complete weight of the fixture.  Design of hangers and method of fastening, other than shown on the Drawings or, herein specified, shall be submitted to the Engineer for approval.

Pendent fixtures within the same room or area, shall be installed plumb and at a uniform height from the finished floor.  Adjustment of height shall be made during installation.

Flush mounted recessed fixtures, shall be installed so as to completely eliminate leakage of light within fixture and between the fixture and adjacent finished surface.

Fixtures mounted on outlet boxes shall be rigidly secured to outlet box.  Hickeys or extension pieces shall be installed where required to facilitate proper installation.

Surface mounted fixtures longer than 60cm shall have one additional point of support besides the outlet box fixture stud when installed individually.

Fixtures located on the exterior of the building shall be installed with non-ferrous metal screws finished to match the fixtures.

Where Edison screw lamp holders are used, the outer contact must be connected to the neutral conductor.

Fixtures installed in false ceiling shall be connected to the relevant lighting outlet through a flexible cord & ceiling rose, unless otherwise specified under (CONDUITS”.  Each fixture shall have its corresponding lighting outlet.

7.  Lamps – General

Lamps shall be supplied and installed in all lighting fixtures listed in the Schedule of Lighting Fixtures on the Drawings.

Lamps used for temporary lighting services shall not be used in the final lamping of fixture units.

Lamps shall be of wattage and type as shown in the Schedule of Lighting Fixtures.

Lamps for permanent installation shall not be placed in the fixtures, until so directed by the Engineer, and this shall be accomplished directly before the building areas are ready for occupancy by the Employer.

8.  Lamps - Fluorescent

Lamps shall be of the normal start energy saving type, unless otherwise indicated.

Lamps shall be krypton filled, in place of the traditional argon fill.

Lamps shall have bi-pin bases and a minimum approximate rated life of 8,000 hours.

Lamps with WHITE color rendering shall have the color rendering features similar to ‘TL’D color 84 lamps, and lamps with WHITE DELUXE color rendering shall have the color rendering features of ‘TL’D color 83 lamps as manufactured by Philips (Holland).  Lamps shall have 96 lm/ watt output minimum based on 36 watt lamps.

Lamps watt as discripted in BOQ

Lamps shall have WHITE color rendering unless otherwise indicated.

9.  Lamps - Incandescent

Incandescent lamps shall be inside frosted type, unless otherwise indicated.

Lamps shall have a minimum approximate rated life of 750 hours.  Lamps shall have medium base bayonet type for lamps up to 150 watts and right hand screw type for lamps 200 watts and above unless otherwise indicated or approved.

Lamps shall be manufactured by Philips (Holland) or approved equal.

10.  Lamps – Mercury Vapour, and Metal Halide

Mercury lamps shall b high-pressure mercury-vapour fluorescent lamps, with a quartz discharge tube enclosed in an internally coated avoid outer bulb.

The quartz discharge tube shall contain a small quantity of mercury and a starting gas.

The average luminous flux after 100 burning house shall for a 50 W lamp, be 1850 lumens horizontal and 2000 lumens vertical.  The number of minutes after which the lamp has reached 80% of its final luminous flux shall not exceed 5 minutes for 50 W lamps and 4 minutes for higher wattage lamps.

Lamps below 125 W shall be fitted with normal glass and lamps 125 W and above shall be fitted with hard glass.

Lamps shall be similar to Philips HPL-N type or approved equal.

Metal Halide lamps shall be similar to mercury vapour lamps except that the discharge tube shall contain metal halide compounds and the average luminous output after 100 burning hours for a 375V lamp shall not be less than 30000 lm.

11.  Lamp – High Pressure Sodium

High pressure sodium vapour lamp shall be suitable for outdoor use.  It shall include a sintered aluminium oxide discharge tube enclosed in a clear, tubular hard-glass outer bulb.

The average luminous flux after 100 burning hours shall be the following:-

For 150 watts: 14000 lumens.

For 250 watts: 27000 lumens.

For 400 watts: 47000 lumens.

For 1000 watts: 125000 lumens.

The number of minutes after which the lamp reaches 90% of its final luminous flux shall be the following:-

For 150, 250 and 400 watts, 5 minutes.

For 1000 watts, 6 minutes.

The re-ignition time shall not exceed 3 minutes.

The lamp shall be suitable for universal burning position.

The lamp shall be able to operate in both high (+50 °C) and low (-50 °C) ambient temperatures.

The lamp shall have a stable operation with supply voltage as low as 200 Volts.

12.  Ballasts - Fluorescent

Only single and/or two-lamp ballast shall be used in any one fixture.

Ballasts shall be high power factor type, with a minimum power factor of 0.85.  Voltage  rating shall be equal to the nominal voltage or be the next higher standard.

Ballasts sound performance shall be suitable for the lowest sound level likely to be encountered in the subjected space with sound ratings as shown on the Lighting Fixtures Schedules of the Drawings.

Ballasts shall have manufacturer’s lowest sound level and case temperature rise rating.

Ballasts shall be special cool operated type.

Ballasts shall be normal start type unless otherwise indicated.

13.  Starters - Fluorescent

Starters shall produce a sufficiently high peak voltage for proper ignition of the lamp.  Ample pre-heating of the lamp electrodes prior to ignition shall be provided to have a favorable effect on the life of the lamp with a minimum of end blackening.

The glow-switch and a radio-interference suppression capacitor shall be safely housed in a high quality white polycarbonate canister ensuring excellent insulation.

Starters shall comply with IEC 155/155 A or approved equal.

14.  Starters – Fluorescent (Electronic)

Starters shall be electronic type, enclosed in a polycarbonate box mounted inside the luminaries with the ballast.

Starter shall provide immediate ignition (0.5 seconds) of standard fluorescent lamps.

Starters shall have negligible watt loss, and shall be noiseless.

It shall be similar to the universal vivatronic catalog ref.  G69577 as manufactured by Thorn EMI Lighting, ES 08 as manufactured by Philips or approved equal.

15.  Ballasts – Fluorescent (Electronic)

Ballast shall be solid state electronic controlled type with no noise nuisance, high operating frequency, 0.95 power factor, instant non-flickering start, automatic switch-off if lamp is defective, no stroboscopic effect and no electrode flickering.  All components shall be mounted on a common wiring board, with a sheet metal housing mechanical protection.  Is shall require no starter.

The unit shall be similar to electronic control gear as manufactured by Philips, Siemens or approved equal.

16.  Ballasts – Mercury Vapor

Ballasts shall be suitable for use in the area to be installed.

Ballasts for 400 W lamp shall consist of two parts = gear housing and cover.

The housing and the cover are made of polyamide, which is heat, impact and stress resistant, with very good insulating properties.

The ballast box shall be protected to IP 54.

All ballasts boxes shall include the integral ballast, the igniter, the capacitors for power factor correction to min 0.85, a terminal block, and two properly rated fuses.

17.  Ballast and Ignition device Sodium

All Sodium lamps shall be equipped with individual control gears comprising a ballast and an ignition device.

The igniter housing shall be able to withstand a + 85 °C temperature.  All control gears shall be equipped with capacitors so as to raise the power factor to 0.85.  Ballasts shall have low losses which shall not exceed the following values:-

For 150 watts lamps, 20 watts losses.

For 250 watts lamps, 30 watts losses.

For 400 watts lamps, 36 watts losses.

For 1000 watts lamps, 60 watts losses.

Ballasts shall operated with a voltage range of 210 to 230 V, with 50 Hz frequency.

18.  Auxiliary Lights

Auxiliary light units shall operate on 12-volts DC.  Units shall be self contained, flexible cord connected for use on 220 volt, 50 Hz supply.  Unit shall have sealed lead-acid calcium battery with a 36 ampere-hour capacity at the 8 hour rate.  Unit shall incorporate an automatic high-low solid state charger with an indicting light for high rate charge, ready light, battery voltmeter and test switch; enclosed in a suitable steel contained with two 25 watt, seal beam lamp assembly.  A sheet-metal bracket shall be provided for mounting each unit.

In areas with high pressure sodium or mercury vapor lighting, unit shall be provided with an adjustable time delay device.

19.  Emergency Exit Light

Emergency exit light shall be constructed of extruded aluminium section, thermolaquered white, riveted askew with beads.

Front side shall be made from acrylic glass XT, 3mm thick dyed black throughout with white inscription “EMERGENCY EXIT”.

2 x 8W  lamps or led lamps shall be provided, and 3 hour duration emergency kit

Emergency exit lights with directional sign shall have an arrow sign on the front side in addition to the inscription.

### END OF SECTION 10