Section-14 Mechanical Specifications

table of contents

Preamble	4

General	5

1	ENERAL CONDITIONS / REQUIREMENTS	7

1.1	Introduction	7

1.2	Equipment Ratings	7

1.3	Coordination	7

1.4	Equipment	7

1.5	Shop Drawings	7

1.6	Record Drawings And Manuals	7

1.7	Services For Testing	7

1.8	Spare Parts And Tools	8

2	STANDARDS	9

2.1	Introduction	9

2.2	Standards For Installations	9

2.3	Safety And Fire Precautions	9

2.4	Contractor's Plant And Tools	9

2.5	Pipe work Connections	10

2.6	Materials	10

2.7	Standards	10

2.8	Trade Customs And Practice	10

2.9	Dimensions	10

2.10	Setting Out	10

2.11	Nameplates	10

2.12	Interruption of Services	11

2.13	Misuse Of Materials	11

2.14	Vouchers	11

2.15	Obstructions	11

2.16	Inspection, Testing And Rejection	11

2.17	Inspection Before Concealment	12

2.18	Valve Labels	12

2.19	Painting, General	12

2.20	Cleaning	12

2.21	Installation of Pipes Services	12

2.22	Pressure Gauges	14

2.23	Testing and Commissioning -General	15

3	COLD WATER AND HOT WATER SERVICES	17

3.1	General Requirements	17

3.2	Pipe work	17

3.3	Underground Pipe work	17

3.4	Domestic Cold & Hot Water Pipe work	17

3.5	Valves	18

3.6	Strainers	18

3.7	Float Valves	18

3.8	Water Tanks	19

3.9	Electric Water Heaters	20

3.10	Water Meter	20

3.10.1	Water Meter Cabinet	21

3.11	Testing	21

4	FIRE FIGHTING SERVICES	22

4.1	General	22

4.2	Pipework	22

4.3	Fire Hose Cabinet	22

4.4	Landing Valve	22

4.5	Inlet Breaching Valve Connections	22

4.6	Fire Fighting Pump set	23

4.7	Pre-commissioning Cleaning	23

4.8	Testing	24

4.9	Painting	24

4.10	Portable Fire Extinguishers	24

4.11	Labels And Identification	24

5	SANITARY FIXTURES	34

5.1	General	34

5.2	Wash Basin	35

5.3	Water Closet	35

5.4	Hand Spray (Hose Bib)	36

5.5	Kitchen Sink	36

5.6	Accessories	36

6	ABOVE GROUND DRAINAGE INSTALLATIONS	37

6.1	General Description	37

6.2	Pipe work	37

6.3	Joints And Connectors	37

6.4	Supports	37

6.5	Water Proofing	38

6.6	Floor Drain	38

6.7	Traps	38

6.8	Testing	38

7	BELOW GROUND DRAINAGE INSTALLATIONS	39

7.1	General Description	39

7.2	Pipe work	39

7.2.1	Pipework -Installations	39

7.2.2	Gully Trap	40

7.2.3	Floor Cleanout	40

7.2.4	Excavation For Pipe Lines	40

7.2.5	Bedding And Surrounding Of Pipes Beneath Building	40

7.2.6	Bedding And Surround Of Pipes -Generally	41

7.2.7	Testing Of Drains	41

8.	Ventilation & air conditioning installation	42

8.1     General	42

8.2	British  Standard  and  Codes of  Practice	43

8.3       Outdoor Unit	43

8.4  Unit construction	43

8.5 Compressor	43

8.6  Condensing Unit	44

8.7   Condenser Fan	45

8.8   Cooling circuit	45

8.9   Control & safety devices	45

8.10 Functions	45

8.11Backup function	46

8.12   Indoor Unit	46

8.13   Pipes Connection	48

8.14   Control	48

8.15   Refrigerant Pipes	48

8.16	extract Fans	49

8.17	Centrifugal fans	50

8.18	Air  Outlets	51

8.19	Manual  Volume Control Damper	53

8.20	ROOM THERMOSTAT	54

8.21Drawings	55

8.22  DELIVERYY STORAGE, AND HANDLING	55

8.23    PIPING INSULATION MATERIALS	55

8.24    DUCTWORK INSULATION MATERIALS	55

8.25      INSPECTION	55

8.26     DEMOSTIC HOT WATER PIPING SYSTEM INSULATION	56

HVAC PIPING SYSTEM INSULATION   8.27	56

8.28   DUCTWORK SYSTEM INSULATION	56

9 INSTALLATION SYSTEM	57

9.1     INSTALLATION OF PIPING INSULATION	57

9.2    INSTALLATION OF DUCTWORK INSULATION	57

9.3    INSTALLATION OF EQUIPMENT INSULATION	57

9.4     INSULATION EXPOSED TO WEATHER	58

10 - SPECIALIST SERVICES MEDICAL GASES INSTALLATION	58

10.01	Scope of Works	58

10.02	Medical Gases, Air and Vacuum	59

10.03	Central Storage Cylinder System	59

10.04 Liquid Oxygen Supply System (VIE)	63

10.05	MEDICAL SURGICAL AIR SUPPLY SYSTEM	65

10.06	Medical Vacuum Plant	74

10. 07	Distribution Park System	80

10.08 	 Rigid Pendants for Operating Theaters	92

10.09	Identification of Pipelines	94

10.10	Warning and Alarm System	94

10.11	Waste Anesthetic Gas Systems	98

10.12	Commission and Testing	99

# PREAMBLE

The Bills of quantities are classified under headings and sections with the same reference numbers and titles as the specifications.

Each section referred to in the Bills of quantities shall be read in conjunction with the respective section and with all other sections of specifications.

The Bills of Quantities, Specifications, and Drawings and all other Contract documents are complementary to each other.

It is the responsibility of the Contractor to check the locations and quantities of the materials and equipment to be executed in accordance with the contract drawings.

The unit rate of the materials and equipment shall be based on the Specification, all components as required and specified under each item concerned in the Specifications, Technical Data and Notes on the Schedules of Equipment Sheet, Contract Drawings, and all other Contract documents.

In addition to the above mentioned requirements, the Unit Rate shall include the following:

(The following requirements are complementary to the mentioned items in the B.O.Q.),

General

1.	Supply of materials and equipment.

2.	Off loading and handling from trucks on site to place of installation.

3.	Installation of materials and equipment.

4.	All civil work required and connected with the mechanical installations, such as:  supports, cutting through walls and slabs for passage of pipes and conduits and ducts, pipe sleeves, repatching, fixing of pipe and duct hangers and supports to structure, wooden frames for air outlets and louvers excavation and backfillings, riggings, hoisting, water proofing, cleaning, protection and painting. In addition, all electrical works required for installation and commissioning of mechanical equipments should be executed and coordinated with electrical works. The related electrical works include, but not limited to, cables, power sockets, circuit breakers, connection, testing, commissioning and all other works needed to commission the mechanical equipments in an efficient and proper way according to materials specifications and approval of engineer.

5.	All testing, balancing, adjusting, commissioning and handling to client complete operational systems.

6.	Allowance for cleaning and for proper protection of all equipment plants, electrical installations and structures during insulation  and paintings.

7.	Disinfection, flushing and water treatment.

8.	All labour, materials, tools, instruments, electric power supply and water required for installation, testing, balancing, adjusting, disinfection, flushing, operation and commissioning.

9.	Thermal insulation for all equipment, valves, trimming and accessories.

10.	System identifications, tags, labels, nameplates, and charts.

11.	Shop-drawings and record drawings.

12.	Spare parts and components for ideal running of all services and equipment.

13.	Spare parts information and tools.

14.	Operation and maintenance manuals.

15.	Training

16.	Samples as required by the Engineer.

17.	Inspection, testing , rejection , adjusting, balancing, commissioning, and handling to client of all materials, equipment and workmanship.

18.	Maintenance of all items supplied by contractor as per Contract Conditions

19.	Install and assist in testing and commissioning of all automatic control field devices which are supplied by others for all equipment and systems as shown on drawings and called for in the specifications

# GENERAL CONDITIONS / REQUIREMENTS

## Introduction

The General Specifications included as part of this Specification indicates the minimum standard of work, workmanship and materials that will be accepted in the provision of a normal installation. It is not intended to cover the requirements of installations of a specialist nature. The General Specifications shall be read and considered in conjunction with, Particularly Mechanical and Electrical Specifications and Drawings that are issued for and appertain solely to the particular installation concerned; in the event G of conflict the more stringent condition shall apply and the Engineer or his Representative  IS decision shall be final.

The Contractor shall include for the complete installation, testing and commissioning of the mechanical, associated electrical and plumbing systems outlined on the drawings and described in this specification.

## Equipment Ratings

All equipment selected for use on this Contract shall be suitable for continuous and reliable operation under the external design conditions stated. In addition, items of equipment installed in enclosed spaces may be subject to temperatures in excess of those prevailing externally and this shall be taken into account. Where ratings are given in this Specification and/or shown on the Drawings, they are the actual ratings to be achieved after the application of all de-rating factors.

All equipment and enclosures that may be subject to internal condensation shall be fitted with suitably rated electrically operated thermostatically controlled anti-condensation heaters.

## Coordination

The Contractor shall be responsible for all aspects of project coordination as set out in the General Conditions.

## Equipment

All equipment to be installed under this contract shall comply with the requirements of the General Conditions.

## Shop Drawings

The Contractor shall prepare shop drawings for the installation as per the requirement of the General Conditions.

## Record Drawings And Manuals

The Contractor shall prepare record drawings and manuals as per the requirement of the General Conditions.

## Services For Testing

All fuel, oil, gas, water and electricity for the purposes of testing and commissioning shall be provided by the Contractor up to the date of the issue of the Certificate of Temporary Acceptance. This shall include the initial charging of all systems and equipment with water, oil and gas, etc.

## Spare Parts And Tools

After completion of the Works and during the specified maintenance period the Contractor shall be responsible for the supply and installation at the fixed time recommended by the manufacturers of all spare parts and components, required for the ideal running of all engineering services installation.

The contractor will be responsible to provide the list of recommended spare parts for all equipments used in the project and to provide such spare parts for two years after the maintenance period.

# STANDARDS

## Introduction

This General Specification indicates the minimum standard of work, workmanship and materials necessary for the execution of the Contract to the approval of the Engineer or his Representative  and the true intent of this Specification and associated Drawings.

## Standards For Installations

The installation shall conform to:

- The general and specific requirements of the local water authority, public health officer, local drainage inspectorate and other local statutory authorities.

- Local authority by laws and other regulations.

- General and specific requirements of the local fire officer.

- Health and Safety at Work Act., U.K.

- Central supply of liquefied petroleum Gases to Buildings.

- Factory Act Requirements and Regulations, U .K.

- Relevant codes of practice of the British Standards Institution.

- The requirements of the insurance companies concerned.

- The regulations for the electrical equipment of buildings, (current edition) published by the Institution of Electrical Engineers, London.

- The recommendations of the manufacturers of all materials, plant and equipment.

- CIBSE Regulations for water supply and drainage services.

## Safety And Fire Precautions

The Contractor shall ensure that safe methods of working are followed when using any equipment of materials which may involve a danger to life or to property and he is to take all necessary precautions to safeguard against damage by fire or explosion where the execution of the works may involve the presence of flame or sparks.

## Contractor's Plant And Tools

The Contractor, unless otherwise specified, shall provide all materials, tackles, slings, scaffolding, ladders, haulage, labour and apparatus necessary for the supply, delivery and erection of the plant on site.

The Contractor shall be responsible for providing at his own expense, all the requirements such as hand tools, hand lamps, and transformers, where necessary, to carry out the works including all cabling and intermediate connections from supply point to location of work.

All wiring, cabling, etc., serving temporary installations are to be designed, installed and operated, as to be safe and in full accordance with the appropriate regulations.

As soon as any part of the Contractor's Site establishment or plant is no longer required for carrying out the Works, the Contractor shall disconnect and remove the same to the satisfaction of the Engineer or his Representative .

## Pipe work Connections

The Contractor shall include for all pipe work and connections to all sanitary fittings, and specialist equipment as detailed in the specifications and shown on the Drawings.

## Materials

All materials, plant and equipment shall comply fully with any relevant British Standard Specification or Code of Practice current at the time of tendering.

The Engineer or his Representative  reserves the right to inspect materials, plant and equipment on Site at reasonable times and to reject any of the same not complying with the Specifications.

The cost of dismantling and re-erection of the installation occasioned by the removal of rejected materials, plant or equipment shall be borne by the Contractor.

## Standards

Corresponding parts of all apparatus shall be interchangeable and where mechanical or electrical details are used or which any part of parts are covered by a British Standard Specification, all such parts are to be made in accordance with such specification as shall be issued at the date at which the parts have been ordered.

Except where otherwise specified, all bolts, nuts and stud screws thread shall be metric and all pipe threads to be to B.S. pipe threads standards.

## Trade Customs And Practice

The Contractor shall be entirely responsible for arranging and ensuring that the various classes of work comply with local trade customs and practice and shall provide accordingly in his Works.

## Dimensions

The Contractor shall take his own dimensions on Site for all plant and material to be supplied by him and shall be entirely responsible for the accuracy of his measurements.

## Setting Out

The Contractor shall set out the Works in accordance with his installation working drawings.

## Nameplates

All plant and apparatus supplied under this Contract shall be provided with brass nameplates, bearing the maker's name shop or reference number, size, type, test and working pressure, speed and other relevant particulars engraved thereon.

## Interruption of Services

The Contractor shall not, without permission of the Engineer or his Representative  interrupt or interfere with the operation of existing services such as water, electric lighting and power, buried cables, sewers, drains, etc., nor, in the case ofworks of statutory authorities or private owners, without the permission of these authorities or owners.

In the event of any such damage, the Contractor shall be responsible for the making good of same to the satisfaction of the Engineer or his Representative , authorities or owners, as the case may be.

## Misuse Of Materials

No materials brought on to Site for incorporation in the Works shall be used for scaffolding or any other temporary purpose.

## Vouchers

The Contractor, at the request of the Engineer or his Representative , must produce invoices, paid or unpaid, or accounts if required as proof that the goods are in all respect as herein specified.

## Obstructions

No extra charge shall be made for moving or circumventing any obstruction or other Contractor's equipment that may be laid on the Site and the Contractor must, therefore, allow in his tender for these and any other contingencies likely to arise.

## Inspection, Testing And Rejection

The Engineer or his Representative shall be entitled during manufacture to inspect, examine and test the materials and workmanship for all plant to be supplied under the Contract, whether at the Contractor's or manufacturer's premises or on the Site. Such inspection, examination or testing shall not release the Contractor from any obligation under the Contract. The whole of the installation shall be tested on completion (in the presence of and to the satisfaction of the Engineer or his Representative or his representative) in the relevant Sections of this Specification as applied to the particular installation concerned.

The Contractor must furnish certificates of test, in duplicate, to the Engineer or his Representative, for all plant or materials specified to be tested at maker's works.

The tests on Site specified hereinafter are to be carried out in the presence of the Engineer or his Representative or his Representative. The accuracy of all tests is to be to the satisfaction of the Engineer or his Representative, whose decision shall be final.

The Contractor shall provide free of charge on the Site at his own expense and/or the manufacturer's works, such labour, materials, apparatus and instruments as the Engineer or his Representative may consider requisite from time to time and as may reasonably be demanded to efficiently test the plant, materials or works as far as completed, until the plant is accepted as a whole by the Engineer or his Representative. The Contractor shall at all times give facilities to the Engineer or his Representative or his authorized representative to accomplish such testing.

The Contractor shall demonstrate, if required, the accuracy of any instrument used for testing. At least seven days' notice must be given by the Contractor of any test carried out on the Site to enable the Engineer or his Representative  or his authorized representative to be present if they so desire.

Testing of pipes and other apparatus as specified under the various Sections of Specifications may be required to be carried out in parts against testing as a whole and the Contractor must provide accordingly in his tender.

Should the Works on testing not conform to the Specifications, the Contractors must make them so conform at his own expense and, if he fails to do so within a reasonable period, not exceeding fourteen days, the Engineer or his Representative shall be at liberty to call upon him to remove the defective part and reinstate without cost to the Employer.

## Inspection Before Concealment

Whenever work subsequently to be concealed, requires inspection or testing due notice of at least seven days shall be given to the Engineer or his Representative so that inspection may be made or tests witnessed before concealment.

Failure to give due notice may necessitate the Contractor uncover the work and re install it at his own expense.

## Valve Labels

The Contractor shall supply and fix on all valves and stop cocks throughout the system, white ivorine labels with black engraved lettering to provide a clear indication of the precise function of the valve. Each label shall be numbered to agree with the Schedule of Valves and the' As Built' drawings.

## Painting, General

All fire fighting pipes, exposed drainage pipes, exposed water supply pipes and all other related mechanical works to be finished or coated as per the consultant instructions.

## Cleaning

Due allowance shall be made for the full and proper protection of all items of plant and equipment, electrical installation and building structure during the whole of the application of the insulation and painting works.

Any damaged insulation/paintwork shall be replaced at no additional cost to the Employer.

## Installation of Pipes Services

Installation of all pipe work shall follow the detail set out in the accompanying drawings and be in accordance with the best-accepted practice.

Details set out in the following clauses of this Section are generally appropriate to all services except where specifically stated elsewhere in the Specifications and Drawings.

All exposed pipe runs shall be arranged to present a neat appearance and, where practical be parallel both with one another and with the building structure, taking due regard however to the grading, venting and draining requirements. All vertical pipes shall be plumb.

All exposed pipe runs shall be arranged so that the longest length of tube practicable is used between bends, tees and flanges or unions. Short lengths of tube joined together by sockets shall not be permitted.

No joints shall be formed within the thickness of walls, floors or ceilings.

Unions or flanges shall be provided generally at a maximum spacing of one per 18 meters in position agreed by the Engineer or his Representative.

Where pipes are held in vices, as when screwing or cutting, care shall be taken to ensure that the pipe surface is not damaged. Any pipework so damaged shall not be fitted. Any pipework surface damaged by scoring whilst being installed shall not be accepted.

The Contractor shall ensure that all pipes, fittings, valves, etc. are free from corrosion and internal obstruction. Pipes and fittings showing signs of corrosion shall not be fitted.

The Contractor shall protect the open ends of all pipework. Suitable caps, plugs or plastic covers only shall be used to cover open ends. Wood, rag or paper plugs shall not be used.

The Contractor shall not use a valve fitted to the open ends of a disconnected pipe to prevent the entry of dirt.

Failure to comply with the above instructions shall mean that the Engineer or his Representative  shall have the right to order the pipework to be dismantled for as far as considered necessary and the pipework to be thoroughly cleaned internally.

The Contractor shall carry out this work free of cost to the Employer and shall bear all costs incurred by removing, cleaning and replacing the sections of pipework .

### Pipework Supports

All pipework shall be adequately supported on galvanized steel hangers or on brackets with rollers in order to permit free movement due to expansion and contraction.

Pipework support shall be arranged as near as possible to joints and changes in direction.

The Contractor shall include for the supply of all necessary supports and brackets complete with all bolts, screws and inserts or plug fastenings.

Vertical pipework shall be adequately supported at the base of the rise and at all intermediate levels. Branch circuit pipes shall not be used as a means of support for the riser main.

Brackets and support shall be set out so that they do not obstruct the access to valve flanges or fittings requiring maintenance.

Pipes shall be spaced in relation to one another and to the building structure so as not to interfere with any other service and to allow for the required thickness of thermal insulation as specified later.

Pipes shall not be supported from each other, but, where there is no alternative, the Engineer or his Representative’s written approval must be obtained. The brackets so installed shall not prevent the removal of any individual pipe where necessary and provision shall be made for any unequal expansion.

Pipes shall not be supported from any item of equipment.

All hangers and supports, except at necessary fixed points, must be allowed to swing freely to make up expansion and contraction.

All brackets, hangers and supports, are to be hot dip galvanized after manufacture to B.S.729.

In addition to the centers given, support shall be provided adjacent all valves, flanged joints and other special components to prevent undue strain on the adjoining pipework and so that the equipment or sections of pipework may be removed, leaving the adjoining pipework adequately supported at the ends.

Main walls and partition walls etc. where pipes pass through sleeves, shall not be considered as pipe supports.

### Pipe Supports Spacing

Supports Spacing for Steel/Metal Pipe

| Pipe Size Normal dia. mm Spacing | Horizontal Support Spacing | Vertical support Spacing |
| --- | --- | --- |
| 15 | 1.5 | 1.6 |
| 20 | 1.8 | 1.9 |
| 25 | 2.0 | 2.3 |
| 32 | 2.4 | 3.0 |
| 40 | 2.7 | 3.3 |
| 50 | 3.0 | 3.6 |

Supports Spacing for Plastic Pipes

| Pipe Size Horizontal Support Spacing Normal dia. mm Spacing |  |
| --- | --- |
| 15 | 1.4 |
| 20 | 1.4 |
| 25 | 1.5 |
| 40 | 1.7 |
| 50 | 1.8 |
| 75 | 2.1 |
| 100 | 2.3 |

### Pipe Sleeves

In all cases where pipes pass through walls, floors, ceilings and footings, the Contractor shall provide sleeves which shall be built in and shall be responsible for ensuring that this is performed correctly. Sleeves shall in no case be used as pipe supports, a free annular space always being provided. Puddle flanges shall be provided on pipework passing through walls and trenches intended to be covered by earth, etc., or where passing through bund walls.

Sleeves shall be of pipe cuttings properly reamed, cleaned and trimmed at 90□to bore.

Sleeves in non-load bearing walls, floors ceiling and partitions shall be copper or mild steel to suit the particular pipe materials.

Sleeves shall be provided with an inside diameter of not less than 15 mm. larger than the insulated outside diameter of the pipes.

## Pressure Gauges

Pressure gauge's shall be Bourdon tube type with 100mm diameter dial with needle pointer, normal operating pointer, brass casing, bronze syphon and bronze gauge cock, all suitable for the working pressure of the system. Each gauge shall be calibrated in kPa from Zero to 1.5 times the working pressure at the point selected, all to the Engineer or his Representative’s approval. All pressure gauges shall be fully tropicalised and fitted with a red indicating needle set to show the normal operating position.

## Testing and Commissioning -General

- At least three (3) working days written notification of all site tests shall be given to the Engineer or his Representative.

- Fuel, water and electricity necessary for the operation of systems in preliminary runs and for adjustments and tests will be provided free of cost by the Contractor.

- The Contractor shall supply all labour, apparatus and instruments necessary for the prescribed tests. The accuracy of the Contractor's instruments shall be demonstrated if required.

- Any defects of workmanship, materials, performance, design of equipment,

maladjustments or other irregularities, which become apparent during the tests, shall be rectified by the Contractor and the tests repeated at the Contractor's expense, to the satisfaction of the Engineer or his Representative  .

### Pre-Commissioning Cleaning

Tubes and all items of equipment shall be delivered stored and maintained in storage with their open ends effectively plugged, capped or sealed. All fittings, valves and sundry items shall be stored in clean bins or bagged and stowed in suitable racks. All such stored items shall be maintained under weatherproof cover to be supplied by the Contractor until they are ready for incorporation in the works. Particular care shall be taken to ensure the electrical equipment components are kept clean and dry.

Before installations are handed over or subjected to the inspection and tests required the entire installation shall be thoroughly cleaned, both internally and externally.

All water installations shall be flushed out with clean water. This shall be preceded by chemical cleaning. During the flushing out process provision shall be made to exclude filters, pumps and any other items of plant, which could be damaged by the cleaning operation. The entire operation shall be carried out to the satisfaction of the Engineer or his Representative.

Cold water services shall, after pre-commissioning cleaning and hydraulic testing, be sterilized by the application of chlorine as detailed in BS 6700.

### Site Tests

The Contractor shall be responsible for site tests on static systems in order to ensure safe operating conditions consistent with design performance. Such tests shall include inspection and testing of welds and pressure testing for soundness of hydraulic systems.

### Commissioning

All aspects of the commissioning procedure shall follow the recommendations in the relevant CIBSE Commissioning Codes. Commissioning shall include:

- Preliminary checks to ensure that all systems and system components are in satisfactory and safe condition before start up.

- Preliminary adjustments and setting of all plant and equipment consistent with eventual design performance.

- Energizing and setting to work all plant.

- Final regulation and demonstration that the installation delivers the correct rate of flow of fluids at the conditions specified in the Contract Documents.

The entire commissioning procedure shall be performed to the satisfaction of the Engineer or his Representative. The results of the commissioning shall be recorded by the Contractor and shall be endorsed by the Engineer or his Representative. The items on the certificate shall be read in conjunction with the appropriate Clauses of this Specification and the design requirements of the drawings and the certified results and statements pertaining to the commissioning procedure shall be interpreted accordingly.

# COLD WATER AND HOT WATER SERVICES

## General Requirements

The cold and hot water system, as well as the required flushing water system, shall be executed as shown on the drawings, complete with all water distribution piping, water tanks, pumps, solar heat. etc.

The Contractor shall be responsible for providing the main cold water supply pipe and accessories from the municipal water network including obtaining the necessary permits, performing all legal matters and making the tie-in to the water source in accordance with local codes, regulations and requirements of the water authorities having jurisdiction and including the provision of the water meter or orifice installation as might be required and as instructed by the authorities or the Engineer or his Representative , all on his own account, if it dose not exist in the site.

All works shall be carried out to comply with BS6700, current local water and public health regulations and other byelaws and shall be to the entire satisfaction of the Engineer or his Representative.

## Pipe work

Galvanized steel pipes shall be used for the external cold and hot water supply for domestic use. All connections of Galvanized steel pipes to threaded fittings shall be via adapters. Cut threads shall not be allowed.

## Underground Pipe work

All underground potable water pipes shall be galvanized steel pipe (schedule 40). Underground water pipes shall not be run in the same trench as sewer pipes. Adequate precautions shall be taken for protecting underground water pipes from contamination from any source.

All underground pipe work unless otherwise indicated shall be laid at a depth of a 900 mm below finished level.

Underground pipe work shall be bedded on sand with a compaction ratio of less than 0.15, or small gravel. Initial backfill to a cover of 300mm shall be hand consolidated. Backfill material shall be no greater than capable of passing through a 20mrn diameter B.S. 1377 sieve. Mechanical ramming of subsequent backfill shall not commence until at least 300mm cover has been hand compacted.

## Domestic Cold & Hot Water Pipe work

### Galvanized Steel Pipes

Where specified, pipes for water supply shall be seamless galvanized screwed and socketed mild steel tubes and fittings in compliance with BS 1387 -1967 standard for class B galvanized steel.

For pipe diameters 3" and above, flanges shall be used. For pipe diameters below 2", unions shall be used.

Unions and flanges are required at each side of equipment.

### Distribution System

Distribution system shall include hot and cold-water distribution and connection to sanitary fixtures.

All hot and cold water pipe shall be distributed through under tiles to each sanitary fixture through wall (concealed) to connect their respective fixtures. All hot and cold water pipe distribution (horizontal) under the tiles shall be PEX pipe within conduits. The outside diameter of PEX pipe shall be l6-mm and its wall thickness shall be 2.2 mm. The pipe shall be flexible and shall run in conduits (sleeves) to each individual outlet. The conduits shall be flexible corrugated polyethylene pipe of 25-mm outside diameter and 20-mm inside diameter.

Isolating valves shall be installed on cold & hot water supply lines. The valve size shall be of the same bore as the pipe work connection and shall be connected to Cold-water services and hot water services feeders by copper fittings.

The connections of PEX pipes to the taps, mixers etc., shall be made using brass elbow/adapter housed in PVC box (Termination Box) built inside the wall. The boxes shall have provision for incoming flexible conduit.

The termination box shall have compression connection for PEX pipe on one side and female thread for the tap, mixer connection on other.

The complete assembly shall be such that the PEX pipe can be withdrawn and replaced without damaging the wall finish.

The connection of elbow to the tap, mixer etc. shall be made using chrome plated angle valve complete with flexible connection as per the Specifications.

## Valves

All valves shall be of 16 bar working pressure rating.

Gate valves shall be bronze body and trim, solid wedge disc, non-rising stem screwed in bonnet with hand wheel. Gate valves up to and including 50 mm diameter shall be threaded to BS 21. Gate valves above 50 mm diameter shall be flanged to BS 4504.

Check valves installed on the discharge side of pumps shall be of the silent, non-slam, and spring-loaded type to prevent water hammer when the pump stops. Silent check valves shall be threaded with bronze body, bronze seated disk and stainless steel spring. The valve body shall be of 20 bar working pressure rating.

Gate valves and check valves shall be to BS 5154.

Ball valves shall be chrome plated brass body and cover. The ball plug and valve stem shall be coated with chrome. The ball valves shall be equipped with level handle covered with epoxy plastic. The ball valves shall be threaded to BS 21.

## Strainers

All strainers shall be of 16 bar working pressure rating. Strainers shall be y -type, bronze body with 26-mesh stainless steel screen with 0.8 mm diameter perforations. Strainers shall be threaded to BS 21.

## Float Valves

Float valves shall be of all bronze construction including levers and anus, with plastic float and shall be suitable for a cold water working pressure of 10 bars.

Float valves shall be of the full bore, equilibrium ball type, designed to close tight against maximum valve disk and balancing piston bucket. Float valves shall conform to BS 1212.

## Water Tanks

GRP roof Tanks must be obtained from a manufacturer who is approved and listed in the Water Bylaws Advisory Service, UK, National Water Council, UK, Public Utilities Board, Singapore, Office of the Water Authority, Hong Kong and other international Organizations. GRP roof tanks shall be amber in colour and cylindrical in shape. Tanks shall be designed to current British Standards.

### Materials

Materials for the construction of the tank walls shall be pre accelerated thixotropic polyester resin to conform to an appropriate standard with J.I.S.K6919 or B.S.3532: 1962, and the glass fiber used shall be non-alkali type emulsion bonded conforming to J .I.S.R34l1 to 3417 or an appropriate B.S.3396 and B.S.3749 (minimum density 450 gms/m2). Materials used in the construction of the tank shall not support bacterial growth of algae & fungi Panels and covers shall be designed and manufactured to prevent light transmission so as to avoid algae growth in tank. (Value of light transmission shall not be exceeding 0.00%).

### Bolts and Nuts

- Bolts, nuts and washers shall be stainless steel grade A4-316 and not A2-304.

- Rubber Capped bolt sets shall be used for fixing the flanges for pipe catchments-

- .Diameter of tank fixing bolts shall not be less than 12mm & at a rate of 8 bolt sets per meter.

### Sealing Materials

Materials used for joints sealing shall be chemically stable. For locations whereby the respective sealant is in contact with water, such sealant must be non-toxic and must be tested for such non-toxicity in accordance to the SISR 245-1981.

Material for the roof sealant shall be made of EPDM and the main solid sealant shall be made of S.E.B.S. (Stylene Ethylene Butyrene Styrene) i.e. Solid synthetic Rubber.

The main sealant shall be ribbed in not less than 4 locations. These ribs shall be continuous along the length of the sealant without any breaking. Such main sealant shall remain flexible and resistant to ultra-violet rays.

The main sealant shall be subject to testing in accordance to SS245 for the following:

- Effect on taste, odour, colour and turbidity.

- Toxic metals.

- Cytotoxicity.

Such test shall be performed and witnessed by an approved neutral party.

No Resin putty, Fibreglass material, silicon, or non-approved rubbers against non-toxicity, shall be used to seal the joints between the panels.

### Supports For Tank

Water tanks shall be provided with transverse stiffened integral support beams or legs capable of spreading the load onto a flat bearing plinth. The number of legs and spacing should be determined by the tank manufacturer to ensure the structural adequacy of the tank and bearing plinth.

Any Internal A4-316 and A2-304.

### Tank Cover

- The water tank shall be mosquitos' proof and completely covered.

- Access manhole panel shall have a 610rnrn diameter opening and complete with Stainless Steel locking device and Hinges-

- The manhole cover shall be designed to facilitate the manhole to be opened fully and/or detachable.

### Air Vent

The air ventilator shall be 50mm or 100mm diameter made of UPVC suitably covered with net of mesh No.22 to prevent access of mosquitoes and insects.

### Cat ladder

- External ladder shall be fitted to all water tanks of height more than 1 meter.

- The external ladder shall be made of the hot dipped galvanized steel conforming to  J.I.8. G3l0l 88400 and H864l.

### Electric Water Heaters

Electric water heaters are required to supply hot water to sanitary fixtures and shall be designed and rated in accordance with current British Standards.

Electric heater units shall be of the immersed type; heating elements made of nickler-plated copper about 8 wattlcm2 density, with thermostat hot water trap and cold water inlet baffle.

The units shall be made of heavy gauge steel lined with improved glass or copper, with magnesium alloy or nickel chrome alloy anode and stainless steel dip tube.

The units shall be provided with 50mm fibreglass insulation and enamelled steel jacket, temperature and pressure relief valves, non return valve and drain valve.

Each electric water heater shall be fitted with 2 No Y2 " diameter valve for inlet and outlet water.

Water heaters will be of the wall-mounted type with wall-hanging brackets, which permit the water heaters of different makes without need for making holes in walls.

The top and bottom covers should be made of synthetic material and shape in order to permit easy cleaning of the appliance and has an up-to-date design.

The particular construction should permit rust proof installation in project location.

The outlet hot water temperature should be of90DC in winter.

## Water Meter

Water meter shall be provided by the Contractor and procured from the local water authority or approved suppliers. The Contractor shall be responsible for liaison with local Water Authority to ensure that the meters are available at the programmed time. The Contractor shall include for water meters, their handling, storage, installation, labeling etc.

### Water Meter Cabinet

The Contractor shall supply and install water meter cabinets in accordance with the Specifications and local regulations. Cabinets shall be manufactured from galvanized steel sheet of minimum 3 mm thickness. The steel sheet shall be Electro-galvanized, powder coated and oven backed at 180 deg.C.

Cabinets shall be sized to house the required number of water meters and shall be provided with a concealed architrave trim, doors, door handle and locks, etc. "

## Testing

The Contractor shall ensure that all pipe work is completely clear of obstructions, debris, or superfluous matter before any tests are applied. Pipe work shall be slowly filled with water, so as to exclude all air. The pipe work shall be tested at 10 bars or 1.5 times the maximum pressure in the system (whichever is greater) for a period of two hours without loss.

The Contractor shall give the Engineer or his Representative two working days notice of his intention to test a section of pipe work. The Contractor must ensure that each test is witnessed by the Engineer or his Representative and shall maintain signed test reports for the complete installation.

All items of plant and pipe work, which are individually pressure tested, may be isolated from the system (using blanking plates) for the duration of the test. However, the complete system shall then be pressure tested for working pressure after successful pressure testing as described above.

# FIRE FIGHTING SERVICES

## General

The fire fighting services shall be executed as shown on the drawings. All fire fighting components shall be approved by the Local Civil Defence Department.

## Pipework

All pipe work shall be galvanized seamless steel to BS 1387 heavy grade. Pipework with screw fittings shall be supplied with screw and socket ends. Pipework for gas and arc welding, where permitted by the Engineer or his Representative, shall be supplied with plain ends, bevelled for butt welding. All pipework and fittings shall be to NFP A 14.

For pipe work installation, hangers, welding, etc., details refer to Section 14-22 of these Specifications.

Under tiles, steel pipe work shall be protected against corrosion by two layers of hessian and tar to the Engineer or his Representative IS approval.

Valves, strainers, etc. shall be as specified in Section 3.11 of this Specification.

## Fire Hose Cabinet

Fire hose cabinets shall be installed where shown on the drawings. The fire hose cabinet shall be automatic swinging recessed type of dimensions 800x800x250 mm. Hose reels shall be in accordance with BS 5274.

Where specified, the rubber fire hose shall be 1" x 25m smooth seamless reinforced with double synthetic textile yams layer capable of withstanding a working pressure of 20 bar and a bursting pressure above 50 bar. It shall be complete with 1" nozzle.

Where specified the hose connected to the landing valve shall be 2" x 30m long circular woven synthetic fibre and root proof yam capable of withstanding a working pressure of 16 bar and a bursting pressure of 50 bar. It shall be provided with suitable male and female instantaneous coupling so that it can easily be fixed to the landing valve at one end and to a jet/spray nozzle at the other end.

The hose reel shall be equipped with shut-off valve for connecting with pipe work.

The hose nozzle shall be chrome-plated brass, JET/SPRAY/SHUTOFF nozzle.

The cabinet shall be heavy steel construction finished with red colour paint labelled "FIRE HOSE REEL II in English and Arabic.

## Landing Valve

Landing valve shall be 50mm size screwed inlet gunmetal construction, fitted with 50mm instantaneous coupling with removable blank cap and retaining chain.

The valve shall be hydraulically tested at 20 bar before connected to the riser, and shall be compatible with the local fire authority regulations.

Valve hand wheel shall be 150mm minimum diameter and marked with "OPEN" and "SHUT" direction plate. It shall be normally secured shut with strap padlock.

## Inlet Breaching Valve Connections

Inlet breaching valve connections shall have bronze body with 6Smm (2Y2 inch) nom. dia. threaded bottom outlet and two (2) nos. threaded front inlets with individual, internal drop flaps, extension nipples, chrome plated brass, rectangular escutcheon with lettering "Stand pipe -Fire Department Connection", 2 nos. 50mm (2 inch) nominal diameter, instantaneous male inlets with chain and cap etc. complete.

## Fire Fighting Pump set

The fire fighting pump set shall consist of two pump, pressure vessel, and control panel.

The capacity of each pump shall be as shown on Drawings and Bill of Quantity.

The pump set shall be provided with motors, starters, controls, pressure gauges, accessories and all other components for the proper operation.

The pressure vessel shall be of capacity 50 litre, and suitable for working pressure of 10 bar.

The pump set shall be mounted on concrete foundation extended 300mm above finished floor level.

The fire pump set components, controls and operation shall be as detailed for cold water booster pump set in Section 15 of these specifications with the exception of the following: -

- Impeller shall be of bronze construction.

- The pumpset shall operate under the control of pressure switches.

- Standby pump shall be diesel engine direct driven-

- The engine may be of the air-cooled type and shall automatically start on demand if the duty pump fails to maintain system pressure.

- The standby pump shall be manually switched off. The engine exhaust pipe shall be insulated and arranged to discharge outside. Multi attempt relay shall be included in control panel to allow at least 3 attempts for the engine to start.

- The control panel shall include an earth leakage sensor with hooter, mute push button and indication lamp.

The fire pump set shall be constructed to Local Civil Defense requirements and a certificate stating this shall be provided with the pumps.

## Pre-commissioning Cleaning

Tubes and all items of equipment shall be delivered, stored and maintained in storage with their open ends effectively plugged, capped or sealed. All fittings, valves and sundry items shall be stored in clean bins or bagged and stored in suitable racks. All such stored items shall be maintained under weatherproofed cover to be supplied by the Contractor until they are ready for incorporation in the works. Particular care shall be taken to ensure that electrical equipment and components are kept clean and dry.

Before installations are handed over or subjected to the inspection and tests, the entire installation shall be thoroughly cleaned, both internally and externally.

All fire protection installations shall be flushed out with clean water. During the flushing out provision shall be made to exclude any items of plant, which could be damaged by the cleaning operation. The entire operation shall be carried out to the satisfaction of the Engineer or his Representative.

## Testing

All pipe work shall be pressure tested at PN 16 and to the satisfaction of the Engineer or his Representative  and local Civil Defence Authority.

## Painting

All pipe work for fire protection services shall be given one coat of rich primer and two coats of 'Post Office Red' paint after installation and pressure testing.

## Portable Fire Extinguishers

The Contractor shall supply and install portable fire extinguishers in the positions shown on the drawings.

All fire extinguishers located outside hose reels cabinets shall be complete with wall mounting brackets, and placed inside recessed type, red colour cabinets clearly marked (Fir Extinguisher).

CO2 gas fire extinguisher of 6Kg capacity with a rugged all brass operating valve, large size operating lever, full vision pressure gauge, discharge hose and heavy duty drawn steel cylinder with hard, scratch resistant finish.

## Labels And Identification

All items of Fire protection system shall be labelled and identified according to the requirements of local Civil Defence Authority .

  - FM-200 - Clean Agent Fire Extinguishing System

This Section covers an FM-200 clean agent fire extinguishing chemical and includes all components required for a complete system. This Section includes performance and descriptive type specifications. Edit to avoid conflicting requirements.

4.12.1 This section includes the following:

A. FM-200 clean agent suppression systems.

B. Fire alarm and detection system.

    - References

(List reference standards that are included within the text of this Section. Edit the following as required for

project conditions.)

A. ANSI/ASME B16.3 - Malleable Iron Threaded Fittings Class 300.

B. ANSI/ASME B16.9 - Factory Made Wrought Steel Buttwelding Fittings.

C. ANSI/ASME B31.1 - Power Piping.

D. ANSI/ASME SEC 9 - Welded and Brazing Qualifications.

E. ANSI/AWS D1.1 - Structural Welding Code.

F. ANSI/NFPA 2001 - Clean Agent Fire Extinguishing Systems.

G. ANSI/NFPA 70 - National Electric Code.

H. ANSI/NFPA 72A - Local Protective Signaling Systems.

I. ANSI/NFPA 72E - Automatic Fire Detectors.

J. ANS/NFPA 75 - Electronic Computer Systems.

K. ASTM A53 - Pipe, Steel, Black and Hot-Dipped Zinc coated, Welded and Seamless.

L. ASTM A106 - Seamless Carbon Steel Pipe for High-Temperature Service.

M. ASTM A197 - Cupola Malleable Iron.

N. ASTM 394 - Ductile Iron.

O. ASTM A234 - Pipe Fittings of Wrought Carbon Steel and Alloy Steel for Moderate and Elevated Temperatures.

P. FM - Factory Mutual Approval Guide.

Q. NEMA - Enclosures for Industrial Controls and Systems.

R. UL - Fire Protection Equipment Directory.

S. Department of Transportation (DOT) Title 49 Code of Federal Regulations parts 100 to 199,

transportation of hazardous materials.

T. Federal Communication Commission (FCC)

4.12.3	 System Description and Design Requirements

SECTION INCLUDES:

A. This Section covers a fire protection system of the Total Flooding type utilizing an FM-200 clean agent fire extinguishing system. System is a fixed installation where equipment is

designed and installed to provide fire extinguishing capability for hazards  described.

(A complete description of the areas/equipment to be protected must be given along  with references to appropriate drawings.)

(If hazards are inter-exposing or in close proximity to one another, provision for            simultaneous discharge shall be specified.)

B. Design, fabrication, and installation of system and its components shall be in              compliance with

requirements and recommendations of ANSI/NFPA 2001.

C. Interface system with (building fire alarm) (Plant annunciation system) ( ).

4.12.4   PERFORMANCE REQUIREMENTS

(Give concentration required and holding time for total flood.)

4.12.5   SUBMITTALS

(Do not request submittals if drawings sufficiently describe the products of this Section or if proprietary specifying techniques are used. The review of submittals increases the possibility of unintended variations to drawings, thereby increasing the Specifier's liability.)

A. Submit shop drawings .

B. Submit shop drawings indicating detailed layout of system, locating each                component. Include control diagrams, wiring diagrams, and written sequence of                    operation.)

C. Submit product data .

D. Submit product data for each piece of equipment comprising the system                       including storage cylinders, control valves and pilot controls, control panels,                                  nozzles, discharge stations, detectors, alarm bells or horns, switches, and                      annunciators.

E. For total flood hazards, submit design calculations derived from computer                   program written specifically for FM-200 Analysis shall include calculations to verify system terminal pressures, nozzle flow rates, orifice code number, piping pressure losses, component flow data, and pipe sizes considering actual and equivalent lengths of pipe and elevation changes.

F. Submit (piping drawings) (product data) (electrical schematics) (and calculations)  to (authority having jurisdiction) (Fire Marshal) (Owner's fire insurance underwriter) for approval. Submit one set of approved submittals..

G. Submit test reports indicating successful completion of tests.

H. Submit manufacturer's installation and operator's manual under provisions.

4.12.6 OPERATION AND MAINTENANCE DATA

A. Submit operation and maintenance manuals.

B. Include electrical schematic of circuits, written description of system design, drawings illustrating control logic and equipment location, and technical bulletins describing equipment.

C. Provide list of recommended spare parts.

(No special tools need be specified)

4.12.7 QUALIFICATIONS

A. Equipment and Agent Manufacturer: Company specializing in manufacturing the        products specified in this Section with minimum (five) ( ) years (documented)  experience.

B. Installer: The installer shall be trained and certified by the manufacturer to design, install, test and maintain an FM-200 clean agent fire suppression systems and   maintain required licensing for the state of ( ) and/or City of ( ).]

4.12.8 REGULATORY REQUIREMENTS

A. Conform to (applicable) building code requirements as specified.

B. All equipment and devices used shall be listed in the UL Fire Protection                       Equipment.

4.12.9 WARRANTY

(This Article can extend the warranty period beyond one year. Extended warranties add to the construction

cost and may present difficulties to the Owner in enforcing them. Specify with caution.)

Provide (one) year warranty under provisions of Section ( ). (Avoid contingent liability requirements.)

4.12.10 MAINTENANCE SERVICE (Included as part of initial installation)

A. Inspect system 6 months and 12 months after substantial completion of Project.

B. At each inspection, determine agent contents and pressure, and that system is in           proper working order. Include complete checkout of control, detection, and alarm        systems.

C. Submit documents, certifying satisfactory system conditions. Include                            manufacturer's certificate of acceptance of qualifications of Inspector.

SECTION A - GENERAL

The following specifications set forth the MINIMUM standards for installation. If the requirements of local codes or the authority having jurisdiction are MORE stringent, these more stringent requirements shall govern the given installation.

- Black or galvanized steel pipe shall be either ASTM A53 seamless or electric             welded, Grade A or B, or ASTM A-106, Grade A, B, or C, ANSI B36.10. Ordinary     cast-iron pipe, steel pipe conforming to ASTM A-120, or non-metallic pipe SHALL    NOT be used. Stainless steel shall be TP304 or TP316 for threaded connections or      TP304, TP316, TP304L, or TP316L for welded connections.

Piping materials such as stainless steel or other piping or tubing may be used with approval of the authority having jurisdiction, providing an internal pressure of 300 psi will not cause material stress greater than the materials yield point when calculated according to ANSI B-31.1, Power Piping code.

- TYPE OF FITTINGS: Shall have a minimum working pressure of 620 psi, cast iron and Class 150 pound fitting shall not be used.

- Installation shall be performed in a workmanlike manner according to the highest standards of modern practice.

- All pipe and fittings shall be new and of recent manufacture.

- All pipe shall be reamed after cutting so that all burrs and sharp edges are removed.

- All pipe must be thoroughly cleaned before installation. A wire flue brush should be pulled through the length several times, followed by clean cloth rags treated with a noncombustible metal cleaner designed for the purpose. All foreign matter and oil must be removed by this process.

- All pipe and fittings installed out of doors or in corrosive areas must be galvanized or treated with a proper protective coating.

- THREAD PREPARATION - All screwed pipe shall be coated with Teflon tape or an appropriate pipe joint compound. When tape or pipe joint compound is used, coating of the threads must start at least two threads back from the pipe end. On small piping, care must be taken so as not to allow sealant to enter valves or controls.

- WELDING

a. All welding must be performed by an experienced welder.

b. All welded pipe 3/4" and smaller shall be welded using gas welding or other      approved method. Unshielded electric arc welding may be used on pipe            larger than 3/4".

c. All welds shall be pounded to loosen scale and weld beads and then cleaned of the same.

- PIPE REDUCTIONS - Reductions in welded pipe shall be by one of the following devices:

a. Butt weld concentric reducers.

b. Swaged nipples.

c. Weld-o-lets (TM).

d. Where socket weld fittings are permitted (see below), a socket weld reducing coupling can be used only for a one size reduction. All other reductions in socket weld pipe shall be made using the above permitted methods.

When methods (b), (c), or (d) are used, it is imperative that these fittings be installed in strict accordance with the manufacturer's installation instructions. In each case, they must be installed so as to permit full flow. All entrance holes from the main pipe run to the fitting must be of proper size and free of sharp edges, ridges or burrs.

11. REDUCTIONS - SCREWED PIPE

All reductions in screwed pipe shall be by means of screwed concentric reducing fittings or swaged nipples.

SECTION B - PILOT NETWORK

1. All pilot piping shall be either (A) 1/4" threaded pipe or (B) 1/4" steel or stainless        steel tubing.

2. When Method A is used, the following applies:

a. The pipe shall be minimum of Schedule 40 and where it is installed outdoors or                      in other corrosive environments, galvanized pipe shall be used.

b. All threaded pilot pipe connections shall be treated with a suitable pipe sealant            (i.e. SWAK by Cajun Part No. MS PTS-50; Rector Seal or equivalent are                     acceptable). THE USE OF TEFLON TAPE ON PILOT PIPING IS NOT                           ALLOWED.

c. All pipe fittings shall be 300 pound malleable or ductile iron. A 300 pound brass           to steel union shall be installed near the terminations of all pilot piping. 150                 POUND FITTINGS ARE NOT ALLOWED.

3. Whenever Method B is used, the following applies:

a. All steel tubing shall be 1/4" x ( ) wall and shall be painted to provide corrosion            protection. All tubing installed outdoors or in corrosive atmosphere shall be                 stainless steel 1/4" x ( ). All tubing must be reamed after cutting.

b. All tubing fittings shall be of the same material as the tubing and shall be of the

compression type. All tubing to pipe fitting shall be treated with a pipe sealant as             described in 2.b above.

c. All tubing shall be properly supported.

SECTION C - VALVE AND EQUIPMENT CONNECTIONS

Threaded valves such as selector valves, check valves, and solenoid valves shall be installed with a union immediately downstream. Valves having more than two connection points such as shuttle valves and pilot valves shall be installed with a union adjacent to the valve in each connection line. Pipe connections to equipment items such as discharge delay devices, pressure switches, etc., shall have a union adjacent to the equipment.

SECTION D - PRESSURE RELEASE PIPING AND FITTINGS

Piping to pressure releases shall be as specified above for discharge piping. All take-offs for pressure release piping shall be from the top of the discharge piping.

SECTION E - PIPE SLEEVES

All piping through building walls, partitions, floor slabs, roof slabs and the like shall be sleeved.

1. Sleeves shall be Schedule 40 pipe at least two sizes larger than the pipe being              sleeved. One inch pipe is the minimum size to be used as a sleeve.

2. Sleeves shall be packed with an approved sealing material so as to be dust tight.

3. Sleeves through floor slabs must extend at least 2" above the floor. A greater               extension may be used if required by local building codes.

4. Sleeves extending through roof slabs must extend above the roof and be flashed in        accordance with local building codes.

SECTION F - PAINTING

(Specify owner's painting requirements)

SECTION G - PIPE HANGERS AND SUPPORTS

All pipe hangers and supports shall conform to the provisions outlined in ANSI B31.1, latest edition, except as modified and supplemented by this specification. All pipe must be solidly anchored to structural members where longitudinal or lateral movement is possible.

1. Rigid hangers are required wherever a change in direction or change in elevation in the piping system occurs. On long straight runs, at least every other hanger shall be  rigid.

2. Most installations lend themselves to the use of support systems such as Unistrut.

3. All hangers shall be fabricated of steel and installed in a workmanlike manner.

4. All piping shall be attached to rigid hangers by means of U-bolts locked with double nuts, one on each side of hanger. The pipe shall be free to move  longitudinally within the U-bolt except where the piping design requires it to be   anchored.

5. Hangers and pipe shall be designed to prevent stresses from being induced into the               piping during the temperature change caused by the carbon dioxide system  discharge.

6. All piping supports shall be fabricated and installed so that they will not be                 disengaged by the movement of supported pipe.

7. Pipe shall not be hung using one pipeline as a support for another.

8. Piping supports shall be arranged so that no excessive bending stresses are induced into the piping from concentrated loads between supports.

9. THE MAXIMUM SPACING BETWEEN PIPE SUPPORTS IS GIVEN BELOW:

TABLE #1

MAXIMUM SPACING BETWEEN SUPPORTS

FOR SCREWED OR WELDED PIPE

NOMINAL PIPE MAXIMUM SPAN

SIZE (INCHES) (FEET)

1/4 . . . . . . . . . . . . . . . . . . . . . . 5

1/2 . . . . . . . . . . . . . . . . . . . . . . 5

3/4 . . . . . . . . . . . . . . . . . . . . . . 6

1 . . . . . . . . . . . . . . . . . . . . . . 7

1-1/4 . . . . . . . . . . . . . . . . . . . . . . 8

1-1/2 . . . . . . . . . . . . . . . . . . . . . . 9

2 . . . . . . . . . . . . . . . . . . . . . 10

2-1/2 . . . . . . . . . . . . . . . . . . . . . 11

3 . . . . . . . . . . . . . . . . . . . . . 12

4 . . . . . . . . . . . . . . . . . . . . . 14

TABLE #2

MAXIMUM SPACING BETWEEN SUPPORTS

FOR PIPE WITH GROOVED JOINTS

NOMINAL PIPE MAXIMUM SPAN

SIZE (INCHES) (FEET)

3/4 . . . . . . . . . . . . . . . . . . . . . . 7

1 . . . . . . . . . . . . . . . . . . . . . . 7

1-1/4 . . . . . . . . . . . . . . . . . . . . . . 7

2 . . . . . . . . . . . . . . . . . . . . . . 7

3 . . . . . . . . . . . . . . . . . . . . . 10

4 . . . . . . . . . . . . . . . . . . . . . 10

2.03 FM-200 CLEAN AGENT SYSTEM COMPONENT REQUIREMENTS

The components of the FM-200 system(s) shall be provided in accordance with the following requirements:

- CYLINDERS

Cylinder assemblies shall be Chemetron Fire Systems ( ) pound capacity and shall conform to the regulations of the Department of Transportation. Cylinders shall be fitted with a resilient pressure seat type forged brass valve and shall have a threaded steel anti-recoil protective cap for handling and shipment. The cylinders shall be mounted in free standing steel racks or on solid walls. The cylinders and racks shall be arranged to allow a service aisle for cylinder removal and cylinder weighing.

(When a beam scale for cylinder weighing is used add: The rack uprights shall be provided with a weigh bar spanning the rack for support of a portable weighing device.)

(A portable direct reading beam scale shall be provided for weighing cylinders in place by loosening cylinder clamps and disconnecting the discharge heads. It shall not be necessary to disconnect any control components.)

(A Cali 2000 unit may be used in lieu of weighing)

- EXTINGUISHING AGENT

Extinguishing agent must be FM-200® (HFC-227ea) as manufactured by Great Lakes Chemical Corp. in West Lafayette, Indiana.

1. The fire suppression agent shall be FM-200 gas; clean, dry, non-corrosive, non-                                   damaging, non-deteriorating, and meeting the requirements of NFPA 2001.

2. System shall only displace approximately 7.5 to 10.5% of the air in the protected   hazard upon actuation.

3. The agent shall be suitable for use in normally occupied spaces.

4. The agent shall be stored in a container super pressurized with nitrogen to a  maximum working pressure of 360 psia. Higher pressure agents shall be  unacceptable.

5. The agent shall have the following characteristics:

• Ozone Depletion Potential of Zero (0).

• Atmospheric Lifetime less than 50 years.

• LC >800,000 ppm 50

• Boiling point of 3°F @ 14.7 psia

• Electrically nonconductive and noncorrosive

6. Agent shall be listed as "Acceptable" on the EPA's SNAP list.

- DISCHARGE VALVES

Each cylinder shall be fitted with a pressure operated discharge valve. Each valve shall include an integral safety relief device which serves to protect cylinder against excessive internal pressure.

The cylinder valve shall have a forged brass body with external connections for actuation devices. Each valve shall be provided with a removable pressure gauge or solenoid valve with gauge for pressure reading.

When more than one cylinder is connected to a common manifold, a check valve shall be provided with each cylinder. Check valves that utilize "O" ring seats shall not be used as they can be dislodged during discharge.

D. SYSTEM ACTUATION

Only solenoid type devices shall be used to electrically actuate the system. Under no

circumstances will explosive devices such as squibs be an acceptable means of actuation.

E. CONTROLS AND ACCESSORIES

Automatic operation (For thermostat/heat detector operation). (The system shall be released automatically by actuation of rate compensated detector(s) located in the hazard in accordance with the detector rating and applicable detection system standards. Closing of the normally open switch element of the detector operating through the control panel, shall actuate a normally de-energized, normally closed solenoid valve on the cylinder valve.) Before this operation, the control panel shall sound appropriate alarms to evacuate the hazard area.

(For smoke detector operation substitute the following for the first two sentences of the above paragraph.) (The system shall be released automatically by (optical) (ionization) type smoke detectors located in the hazard in accordance with detector ratings, good practice and applicable detection system standards. Operation of smoke detector will signal the control panel for automatic release and/or alarm as specified under the detector portion of this specification. An electric signal shall actuate a normally de-energized, normally closed solenoid valve on the pilot head.)

(Control Panel) (See Chemetron Fire Systems Control Panel Specifications)

(For systems with a reserve supply) (A manually operated transfer switch shall be provided to transfer the pilot cylinder electric solenoid actuation from the main bank pilot cylinders to those on the reserve bank.)

(Electric Release) (Discharge stations located, as shown on the drawings, are to be provided for manual release.)

(For reserve supply) (A second release shall be provided for the reserve bank. Main and reserve bank releases shall perform similarly and shall be independent of any automatic release.)

(For Systems with Selector Valves) (Operation of the pneumatic remote manual release shall also open the proper selector valve.)

(Note to Specifier: The features of the electrical manual release and pneumatic manual release should be studied before specifying which type is best.

F. DETECTION

(The desired detection system as to type and configuration should be specified at this point. To be considered is whether heat, smoke or flame detection is to be used alone or in conjunction with another type. Also, whether detection should be one zone or cross-zoned. If an abort system is to be used it should be specified here.)

G. DISTRIBUTION SYSTEM

The piping shall be laid out to give maximum flow and to avoid possible mechanical, chemical or other damage. Installation shall follow drawings as closely as possible. System designer must be consulted for anything other than minor deviations in pipe routing.

H. SELECTOR VALVE SYSTEMS

The protection for hazards ( ) and ( ) shall be from the same bank of cylinders. Selector valves shall be used. (NOTE: Two or more hazards can be served by selector valves.)

Those selector valves shall be pressure operated and self restoring. They shall be released by

pilot operators which can be operated directly, by remote pressure source and/or by electric solenoid.

NOTE to Specifier: When using selector valves you must ensure that there is little likelihood that hazards protected from a common bank of cylinders will need to discharge simultaneously. (For small systems it is economical to specify individual systems rather than systems using selector valves.))

I. NOZZLES

1. Nozzles shall be supplied in quantities sufficient to properly cover the area(s) being

protected in accordance with NFPA 2001.

2. Nozzles shall be of corrosion resistant construction and shall be designed                     specifically for FM-200 application.

3. Nozzles shall be permanently marked as to type and orifice.

J. ALARM DEVICES

1. Electrically actuated fire alarm horns (and strobe lights) shall be furnished and  installed. Each fire alarm horn (strobe) shall be actuated and receive operating power from the control panel. Terminals for this purpose shall be provided in the   system control cabinet. Each device shall be approved or listed.

2. Alarms shall be adequate to alert plant personnel located in the protected areas.

(Additionally, one horn/strobe shall be provided outside each entrance to the  protected area. The sound output for the horns shall be adequate for the conditions                                                        encountered.)

3. The control panel shall be programmable such that an adequate pre-discharge alarm                period can be set at the time of system test to ensure personnel safety.

K. ACCESSORIES

1. Pressure Switches: The system shall include ( ) normally open and ( ) normally                       closed contacts on a pressure switch actuated by the agent discharge to shut down                      equipment and sound alarm.

Switches shall be heavy duty, double pole, single throw, two to a unit. Each switch shall be provided with a manual operator for test and reset.

2. Pressure Operated Releases: The system shall include ( ) releases to release self closing (doors, dampers, windows, louvers, lids or valves) upon FM-200 discharge.

(NOTE to Specifier: All devices to be closed must be self closing and capable of being held open by a cable or chain hooked to the release.)

2.04 TESTING AND ACCEPTANCE

System shall be listed and tested by either Factory Mutual Research Corporation (FMRC) or Underwriters Laboratories (UL) for Class A, B, & C rated fires.

Upon completion of installation, the system shall be thoroughly tested for correct operation and function. Tests shall include functional operation of all mechanical and electrical equipment and careful inspection of all piping and nozzles.

The door fan method of room pressurization shall be used in each hazard to determine leakage. Instruments recording shall be made as directed by the approving authority.

The contractor shall provide a test report, including a copy of the recording. After testing the system shall be in full operation condition.

4.12.11 FINAL INSPECTION

At the final inspection a factory trained representative of the manufacturer of the major equipment shall demonstrate that the systems function properly in every respect.

4.12.12 INSTRUCTION

Provide instruction as required to the building personnel. "Hands-on" demonstrations of the operation of all system components and the entire system shall be provided.

4.12.13 MAINTENANCE

Contractor shall make available an inspection service contract to ensure that services are always available to keep the protection system in full operation.

# SANITARY FIXTURES

## General

The Contractor shall furnish and install all the sanitary fixtures as shown on the drawings and as specified below, complete with all their trim and accessories as specified. Prefix numbers identify and locate the fixtures on the Drawings relative to the fixtures described herein.

Sanitary fixtures shall be of vitreous china of white colour. Fixtures shall have smooth glazed surface free from warp, cracks, flaws discolouration or other imperfections.

Imperfect fixtures will not be accepted.

Sanitary fixtures shall be supplied complete with all required metal trim and accessories, as specified, including but not necessarily limited to faucets, wastes, traps, supplies, stop valves, wall flanges, hangers, plates, brackets, anchors, supports, soap holders, toilet paper holders etc.

All exposed piping and metal trim for the sanitary fixtures shall be chrome-plated brass to BS 5750 Part (I) with polished finish.

All vitreous china accessories shall match the sanitary fixtures and shall be of the same manufacture and colour .

All sanitary fixtures, trim and accessories shall be the product-approved manufacture and as far as practicable shall be procured from one manufacturer unless specified otherwise.

Sanitary fixtures and their trim and accessories shall be installed in a neat, finished and uniform manner as directed by the Engineer or his Representative. They shall be set straight, true, and securely attached to the supporting surfaces. Roughing shall be accurately laid out to conform to finished walls and doors.

Sanitary fixtures shall be connected to the drain and water supply pipes in an approved gastight and watertight manner and as detailed on the Drawings.

Strap or padded wrenches shall be used on chrome-plated pipe, fittings, valves and other trim.

Sanitary fixtures, metal trim and accessories shall be thoroughly cleaned of labels, plaster, paint dropping and all foreign matter and shall be well polished and tested for perfect working condition before turning them over to the Employer.

Concealed brackets, hangers and pales shall be painted as directed by the Engineer or his Representative.

The Contractor shall submit to the Engineer or his Representative a list of all fixtures, trim and accessories that he proposes to use indicating manufacturer, type and model number, with descriptive catalogues clearly marked as to the item proposed.

The Contractor shall submit samples of all fixtures, trim and accessories when asked to do so by the Engineer or his Representative. The Contractor shall not charge the Employer with the cost of such samples nor shall he use any item different from the approved sample.

## Wash Basin

Shall be white vitreous china, pedestal type as approved by the Engineer or his Representative, complete with one tap hole, waste and over flow. Basin shall be securely fixed to wall with fixing brackets or on pedestal.

Taps shall be 15-mm (1/2in) chrome plated (CP) single level monobloc mixer with ceramic disc cartridge combing on-off water flow and hot-cold water mix in one lever control.

Wash basins shall be complete with pop-up waste mechanism.

Pedestal screwed to the floor, if required, 32-mm dia. chrome plated bottle trap with 75-mm seal, CP waste tail to wall and CP flange l5-mm dia. C.P. angle valves with rigid CP tail connections and CP wall flanges.

## Water Closet

Each water closet shall be white vitreous china mono-block and shall be complete

with the followings:

  - white vitreous china flush tank.

  - White heavy-duty solid plastic open front seat with stainless steel check

hinge.

  - Chrome plated wall fixing screws and gaskets.

  - Paper holder.

  - All necessary fixing and accessories required for its drainage and its satisfactory operation.

## Hand Spray (Hose Bib)

Hand Spray shall be complete with CP angle valve, I-meter metal, flexible tube, hand spray, wall hook etc. The metal flexible tube shall be provided with transparent plastic cover. Hand spray to be provided to the right side of each WC for washing purposes.

## Kitchen Sink

- Fire glazed kitchen sink shall be single bowl and drainer as specified or shown on the Drawings. The sink shall be provided with three tap holes for pillar mixer, chain stay hole and overflow and with back splash end.

- The sink shall be complete with the following trim and accessories: -

- 40-mm dia. chrome plated waste with stainless steel grating and chain stay and plug.

- 40-mm plastic bottle trap with extension tube-

- Flexible plastic tube for overflow connection.

- l5-mm dia. chrome plated angle valves with flexible copper tube and wall flange.

- 15-mm dia. chrome plated pillar mixer with swivel spouts projection 210-mm.

## Accessories

The sanitary fixtures accessories shall be as shown and detailed on the architectural drawings and shall be from approved suppliers to the Engineer or his Representative’s approval.

# ABOVE GROUND DRAINAGE INSTALLATIONS

## General Description

The work under this section of the specifications shall include all above ground drainage pipe work waste, soil, vent and rain water, complete with all drains, traps, gullies, cleanouts, vents and all accessories, as shown on the drawings and as specified hereafter.

The above ground drainage pipes shall mean all building pipework not buried underground and located as follows: -

-Above floor slab

-Suspended under floor slab

-Under tiles

-In walls

-All vertical pipes (risers)

## Pipe work

The pipes and fittings used for above ground drainage installations shall be unplasticised polyvinyl chloride UPVC and shall conform to BS 3505, BS 4514 and BS 5255, and shall be push-fit type with rubber ring seal.

All change in direction in drainage pipes shall be gradual and not abrupt.

Long sweep fittings and 45-degree fittings, of solvent weld sockets type shall be used.

All pipes shall be plain-ended for seal ring connection to all fittings.

All pipe jointing and supporting shall be made as recommended by the pipe manufacturer.

All pipes and fittings including adapters, couplings and connectors shall be marked with the manufacturer name, BS. number and diameter.

All exposed pipes shall be provided with suitable paint for protection against U .V. rays.

## Joints And Connectors

All joints for above ground drainage pipe work shall be airtight and water tight and- care shall be taken to insure that no jointing materials projects inside the bore of the pipe.

Seal ring coupling (expansion joint) fitted with black rubber seal ring shall be provided for each vertical pipe (not embedded) located between every two floors, and for horizontal pipes (not embedded) at 4.0 m. intervals.

The connection of UPVC pipes to all water closets shall be made by WC-connector with solvent weld socket and pan seal socket.

Special UPVC connectors and adapters shall be used for connecting the pipes with dissimilar material of other pipes or fittings such as bottle traps, P-traps of plumbing fixtures.

The connection between vertical pipes and under-ground pipes shall be made by long radius sockets bend fitted with rubber seal rings.

## Supports

Vertical pipes shall be supported at a minimum of 1.8 m intervals, and at least two pipe support brackets at the floor height.

All buried pipes shall be supported along their entire length on clean and well compacted layers of fine sand that should not contain any stones.

All hangers and supports shall be of approved types, as recommended by the pipe

Manufacturer.

## Water Proofing

Where UPVC pipes pass 'through roofs, they shall be provided with paddle flange to make watertight seal around the pipes at roof level.

The method of waterproofing shall be made as per the drawings and the manufacturer's instructions.

## Floor Drain

Floor drains shall be UPVC trapped floor gully with 110mm diameter top socket, three side inlet sockets, and one 75-mm diameter outlet socket equipped with screwed plug for rodding.

Each side inlet socket shall be 50 mm diameter blanked off and must be cut out of inlet used.

The top socket shall be fitted with 110 mm. diameter raising piece with a 150 mm. square top to suit standard floor tiles complete with a nickel bronze screw down grating.

## Traps

All traps in washbasins, sinks and floor drain, etc. shall have 75 mm water seal. All traps shall have the same bore throughout the trap, connection to the buildings fixed drain shall be via an "0" ring fittings.

## Testing

The work shall be inspected and tested during installation. Testing shall be carried out by applying a 3m water head above the highest section of the pipe under test for a period of 2 hours.

All work, which will be concealed, shall be tested before it is finally enclosed.

A final test shall be made upon completion of the work for soundness and performance in accordance with BS 5572: 1978 Code of Practice for Sanitary Pipe work.

# BELOW GROUND DRAINAGE INSTALLATIONS

## General Description

The work under this section of the specifications shall include all building underground pipe work complete with gullies, traps, cleanouts, manholes, and all accessories, as shown on the drawings.

The following types of pipes will be used in the work and to be covered by this specification:

- Unplasticised Polyvinyl Chloride UPVC.

- Stainless Steel Pipes.

## Pipe work

The pipes and fittings shall be unplasticised polyvinyl chloride UPVC, push-fit type with rubber ring seal. Pipe size 110 mm and 160 mm shall conform to BS 4660. Pipes shall operate under working pressure of8 bar.

The stainless steel pipes used for sewer drainage between facilities shall be connected together by welding. Flanges will be provided as needed/required during installations and to the main connection with Ductile Iron pipes. All pipes shall operate under working pressure of 16 bar.

All change in direction in drainage pipes shall be gradual and not abrupt.

Long sweep fittings and 45-degree fittings shall be used.

All pipes and fittings including adapters, couplings and connectors shall be marked with the manufacturer name, BS number and diameter.

### Pipework -Installations

The installation of pipe work shall be carried out in accordance with the requirements and recommendations of BS 5955 Part (6)-1980.

Connections to manholes and main sewers shall be made in a completely watertight and approved manner.

Any connections to existing systems shall be made with minimum disturbance to the existing lines.

Any existing pipelines or structures, which are damaged while making connections, shall be replaced or reconstructed to the satisfaction of the Engineer or his Representative and without any cost to the Employer.

Pipes shall be kept clean until final acceptance of the work. Exposed ends of all uncompleted lines shall be closed with wooden plugs and adequately secured at all times when pipe laying is not actually in progress.

Pipes shall be installed on a good foundation and adequate means taken to prevent settlement. Pipes laid in trenches shall be provided with a solid uniform bearing throughout the entire length.

Pipes shall not be buried at less than 600 mm. below finished grade for protection against mechanical damage. Pipes shall not be run closer than 1 m. to building bearing walls and footings for protection against building settlement.

All pipes shall be laid to a uniform slope as shown on the drawings. The free vertical drop of a sewer pipe into a new or an-existing-manhole shall be limited to 450 mm. between the invert level of the pipe opening and the bottom of the manhole.

Where conditions necessitate that the drop would exceed 450 mm. a drop manhole shall be used, of detail as shown on the drawings.

Trenches shall be kept free of water by pumping, use of well points, under drains or other approved means during pipe laying operations so that all pipe joins are made in the dry.

Precautions shall be taken to protect uncompleted work from floating due to storms or from any other cause. All pipe lines or structures not stable against uplift during construction shall be well braced or otherwise protected.

All joints shall be inspected and an inspection of the lines as a whole shall show all pipes to be true to line and grade with full circle visible at the manholes.

If on inspection the completed sewer or any part thereof shows any structures, pipes or joints which are defective, the defective work shall be replaced or repaired as directed.

### Gully Trap

The gully trap shall be UPVC provided with 110 mm diameter, P-trap and gully piece as detailed on the drawings

The gully trap shall be provided with 300 x 300 mm clear opening cast iron cover and frame Grade (B).

### Floor Cleanout

The floor cleanout (FCO) shall be UPVC rodding eye with 110 mm dia. spigot outlet and supplied with 150 x 150 mm. nickel bronze cover screw down. Floor cleanout shall be provided at each change in pipe direction.

### Excavation For Pipe Lines

- Trenches for pipes shall be excavated to a sufficient depth to allow a l00 mm minimum bed below the underside of the pipe.

- Trench width shall not be less than the outer diameter of the pipe plus 300 mm and not wider than necessary.

- The sides of trenches, manholes and other excavations shall be adequately supported at all times.

- Any material excavated in forming pipe drains shall, if found unsuitable, be run to spoil and replaced with suitable approved material. All suitable excavated material shall be used as backfill except in trench drains-

- Where drain trenches are to be excavated beneath foundations or below the level of adjacent foundations, the sides of the excavation shall be supported by such substantial planking and strutting as steel trench sheeting driven plumb in advance of the excavation proceeding. The trench sheeting shall be carefully withdrawn after compaction of the backfill material so as to cause the minimum disturbance to the backfill and adjacent ground.

### Bedding And Surrounding Of Pipes Beneath Building

- All pipes shall be bedded on Class C20 concrete and shall be supported at the concrete cradles placed behind the sockets or on each side of the joint by methods approved by the Engineer or his Representative. The supports shall be provided with soft contact padding such as roofing felt or other approved material.

The annular gaps inflexible joints shall be sealed with approved means to prevent the intrusion of concrete. The pipes to be in contact with concrete shall be washed clean of any mud or clay.

- Concrete shall be gently and evenly placed over the entire width of the trench of bedding as shown on the drawings, and to within 25 mm. of the bottom of the pipe. Then, without stopping, it shall be placed gently on the side of the pipe only and carefully worked under the pipe, ensuring that no voids are left below the pipe.

- Concrete shall be brought up equally on each side of the pipe to the required finished height, care being taken not to force the pipes off their supports.

- No fill material shall be placed over the concrete until the concrete has reached a crushing strength of 14 N/mm2. The concrete and the pipes shall be kept damp and protected from sun or frost until the concrete has reached the required strength for filling to take place.

### Bedding And Surround Of Pipes -Generally

After jointing the pipes, the bedding shall be brought up equally on both sides of the pipe, first to the level of the centre of the pipeline and then up to a height of 300 mm. above the top of the pipe barrel. This material shall be placed in layers not exceeding 150 mm. in thickness and shall be carefully compacted with wooden rammers.

### Testing Of Drains

- The Contractor shall provide the necessary labour and equipment and include in his Tender for testing and work to the requirements and satisfaction of the Engineer or his Representative and all relevant public authorities.

- Drains shall be tested by either water or air as directed by the Engineer or his Representative and the results of the test must be approved by the Engineer or his Representative before concerting. A further test shall be carried out after backfilling of excavations. The test shall be carried out in the manner described in the following paragraph.

- To facilitate the general building programme, tests shall be made of sections as the work proceeds; such testing however will not absolve the Contractor from his liability for any subsequent or final testing.

- Any defects that become apparent during these tests of any part or parts of the installation shall be rectified at the Contractor's expense and the part, or parts, retested to the satisfaction of the Engineer or his Representative and the relevant public authorities.

- For a water test, the drain lines shall be subjected to test pressure of at least 3m head of water above the highest point of the section under test. Allowance should be made for added water until absorption has ceased, after which the test proper should be commenced and the water level be maintained for a minimum of 30 minutes without the addition of further water.

- For an air test, a gauge in the form of a glass 'U1 tube shall be provided and connected to the drain plug of the length of drain under test. Air shall be pumped into the length of drain until a pressure equivalent to 100 mm. head of water is indicated on the gauge. Without further pumping, pressure should not fall below 75 mm. during the period of five minutes.

- The whole of the installation shall be left clean and free from debris

- The Contractor shall keep a record of the tests carried out on the drainage installation throughout the Contract, recording date of test, by whom tested and the result, one copy of the records shall be sent to the Engineer or his Representative on completion of the Contract.

- Ventilation & air conditioning installation

8.1     General

This Section of the Specifications covers Air Conditioning and Mechanical Ventilation Systems, comprising Variable Refrigerant Flow (VRF) units, air conditioning split units, ventilation fans, work duct,  air outlets, dampers, etc. all as shown on the Drawings and as specified hereafter to form a complete installation.

The spaces shall be air-conditioned all the year round by means of VRF units.

A various air distribution system shall be installed in accordance with the environmental conditions required in the served area.

8.2	British  Standard  and  Codes of  Practice

Unless otherwise stated, the provisions of the latest revised editions of British Standards and Codes of Practice relevant to the particular installation or part thereof shall be held to be incorporated in the Specifications of materials and workmanship to do with that part of the works as specified herein. Other Standards, national or otherwise and Codes of Practice which are equivalent to the relevant British Standards and Code of Practice may be adopted subject to the approval of the Engineer.

8.3 Outdoor Unit:

- Modular design enables the units to be joint together in rows. Light weight and vibration free so no additional reinforcement is needed for the location of the unit slab. High-capacity condenser/ evaporator.

- Optimized for 410A refrigerant. Less refrigerant charge through compact construction with HI-X Cu piping in counter-flow design.

- Specially profiled aluminum vanes, achromatized and plastic coated for surface Protection against corrosive air, acid rain and saline air.

- Each module should  contain an inverter compressor in order to modulate capacity according to the demand of the indoor  units.

- Each module can be operated independently of the total combination in case of a failure of  a module or compressor.

- Ability to place the outdoor unit inside mechanical  room.

8.4  Unit construction:

Rugged, integral unit module with base frame and sturdy feet. Weather proof,

galvanized steel plate, primed and powder coated for outdoor or indoor

installation. Easy access from the front, for operation and servicing. The

modules are combined using the connection piping provided. All units are the

same height and depth, they can be installed neatly in rows.

  - Compressor:

- Scroll type compressor with only one moving component (scroll); optimized for R410A refrigerant in a hermetically sealed.

- pressurized gas cooled.

- Sound insulated casing with integrated drive motor.

- Modules include an inverter compressor with DC motor (digitally

commutated brushless DC motor), which is frequency controlled.

- The inverter compressor is operated in conjunction with a

fixed-speed compressor.

- All compressors are fitted within the unit on anti-noise mountings. To prevent a lack of oil occurring, a dynamic oil balancing system is fitted to the inlet side and a large surface area oil separator is installed on the outlet side. In addition, an automatic oil return cycle for the whole of the system network is periodically activated by the MICRO-PROCESSOR system controller. The installation of oil lifters in the system is thus no longer necessary. The compressor, the electrical and thermal motor protection and the oil sump heating are all controlled by the MICRO-PROCESSOR system controller.

8.6  Condensing Unit

- Units of weather proofed anti corrosion type enclosure complete with compressors, fans, motors and condenser coil, as follows:

Refrigeration System:

1.	Hermetically (at least 2 compressors), one scroll type inverter

Compressor & the other scroll compressors are constant speed .

2.	Condenser coil and propeller direct drive fan.

3.	Accumulator.

4.	Capillary restrictor and electronic expansion valve.

- Condensate Drain: Drain pan to direct condensate to condenser coil for re-evaporation.

- Condenser Fan: Propeller type with permanent split capacitor motor, with high external static pressure.

- Unit shall be designed to work with several fan coil units tied on refrigerant pipe network.

- Automatic control system shall be handle the conditions of operation for any number down to one, the frequency of the inverter control to be determined electronically by sensing ambient temperatures, operational pressures and monitoring the exact requirements of all the connected indoor units.

- The refrigerant control enabled a full 165 m of refrigerant pipes to be laid in a single system. Also the vertical distance between the outdoor and indoor unit is not less than 60 m. (when the outdoor unit is located in a higher position), and the level difference between the indoor units is 15 m.

- Ambient operation range to -5 0C to 43 oC in cooling/ -20  to 15 0C heating modes.

- Outdoor units shall be equipped with a propeller fan developing low vibration and fan shroud. This fan and fan shroud maximize air flow volume and minimize air turbulence (sound pressure level

- The safety devices should include:

      - Thermal protection for compressor and fan motors.

      - Low and high pressure switches

      - Crank case heater

      - Inverter over current protection

      - Anti recycling timer

      - Circuit control fuses

- Heat exchanger: seamless copper tube mechanically bonded to aluminum fins.

8.7   Condenser Fan:

Propeller. Quiet operation, slow running, propeller fans with characteristic

curve optimized for partial load for large volume of air at low noise level.

Aero Fitting Grill, swirl optimized, protective grill, for vertical air discharge.

DC fan motors (digitally commutated brushless DC motor). Optimum pressure flow in the heat exchanger through quasi-permanent fan speed control by the micro-processor system.

External Static pressure > 70 Pa

8.8   Cooling circuit:

Optimized for the use of R 410 A refrigerant. Cooling circuit comprising refrigerant collector, filter and oil separator. Four-way changeover valve for switching between cooling/heating and dynamic defrost circuit by reversing the circulation flow. Optimum level of fill for the evaporator and overheating control for the heating mode by way of an electronic injection valve (EEXV) with 2000 servo steps, controlled by the Micro-processor system controller.

8.9   Control & safety devices:

Control sensors are provided for low pressure, high pressure, refrigerant suction temperature, oil temperature, heat exchanger temperature and outside temperature.

Safety pressure switches are provided for low and high pressure (manual reset on the remote control). The unit is equipped with shut-off valves for suction and liquid pipes and service connections with Schrader valves. The refrigerant circulation is dried, evacuated and charged with the required refrigerant.

- The control of indoor unit fan air flow and heat exchanger capacity by means of the independent PI control system enables air conditioning operations to be carried out at outdoor air temperatures between 0 0C and 43 0C.

- Control Module: Remote mounted adjustable individual thermostat with heat anticipator, off- heat-auto-cool switch, programmed time, diagnostics feed back, high-low fan switch connected with main control panel at central condensing unit to comply with any conditions of operation.

  - Functions

Low-Noise Operation: Noise-reduced Operation, night time operation.

- Sequence start: automatic run-time compensation between compressors

- Self-diagnosis function: for outdoor and indoor units over the data bus

with operator access via the local manual operating level and/or via the diagnosis

tool: Computer - presentation and storage of all process parameters for

effective system maintenance. Including a maintenance protocol print out.

  - Backup function:

If a compressor failure occurs in single module systems  the

remaining compressor ensures a 50% system capacity. This function is activated at the outdoor unit. If a compressor fails in a module in a two or three module

systems , this module can be de-activated. The remaining

module or modules then keep uphold the basic supply. The operator can use the

remote control to activate this function.

Auto Restart:

Built in auto restart capability to ensure automatic system start after power failure.

Auto initialization:

Automatic detection and addressing of the indoor units on the system.

Automatic charge up :

Refrigerant charging is done automatically via the outdoor unit. Charging refrigerant stops automatic when the appropriate volume of refrigerant has been transferred.

Leak check function:

Refrigerant containment detection.

Operation Range:

Heating

15.5 CWB to -20 CWB

Cooling

43 CDB to -5 CDB

Expansion Valve:

Electronic injection valve with 2000 servo steps, controlled by the Micro-

processor system controller.

Defrost:

Short, direct defrost function by reversing the circulation flow.

Connection ratio :

From 50% up to 130%

8.12   Indoor Unit:

A.	Air Cooled Condensing Unit

- System Description

Outdoor - Mounted, air cooled split system outdoor section shall be suitable for on the ground/roof top installation. Unit shall consist of a hermetic compressor, an air cooled coil, propeller type blow-thru condenser fan, accumulator, holding refrigerant charge, and control box.

Units shall be used in a refrigeration Circuit matched to a duct-free fan coil unit.

- Quality Assurance:

a.	System shall be rated and certified in accordance with an international standard.

b.	Unit shall be constructed in accordance with an international standards.

- Products

a.	Factory assembled, single piece, air cooled outdoor unit, contained with in the unit enclosure shall be all factory wiring, piping, controls, compressor, holding charge of R-410, Refrigerant, and special features required prior to field start up.

b.	Unit cabinet shall be constructed of galvanized steel, compressor compartment shall be isolated to assure quiet operation.

c.	Condenser fans shall be direct drive Propeller type, and motors shall be totally enclosed.

d.	Compressor shall be fully hermetic reciprocating or Scroll type.

- Condenser coil shall be constructed of aluminum fins mechanically bonded to internally enhance seamless copper tubes.

- The condensing units (outdoor unite) of heat pump type: shall be provided with anti-freeze thermostat to prevent freezing  during heating operation in winter season.

- Split units; where required: shall be provided with low ambient control kit to provide cooling all year round (summer and winter).

The unit shall also be provided with automatic switch to operate

automatically with   emergency generator in case of power failure

at the same operational conditions.

- Controls and Safeties

Operating controls and safeties shall be factory selected, assembled, and tested.

B- Fan coil unit (indoor unit)

- Indoor, direct-expansion, ceiling fan coil. Unit shall be complete with coil,

supplementary electric heater, fan, motor, piping connectors, electrical controls, integral         temperature sensing, and a holding charge of R-22 refrigerant.

- Unit shall be furnished with integral mounting bracket.

- Cabinet discharge and inlet grilles shall be attractively styled, high impact polystyrene.

- Fan shall be tangential blower type with air intake at the upper front face of the unit and discharge at the bottom front.

- Coil shall be copper tube with aluminium fins and galvanized steel tube sheets. A drip pan under the coil shall have a drain connection for hose attachment to remove condensate. Motors shall be multi speed, permanently lubricated with inherent overload protection.

- Controls shall consist of a microprocessor - based control system which shall control space temperature, determine optimum fan speed, and run self diagnostics.

- Unit shall have filter track with factory supplied cleanable filter.

Control wiring:

A simple 2-wire non-shielded multiplex transmission system links each outdoor unit to multiple indoor units using one 2-wire, non-polar to simplify the wiring operation.

8.13   Pipes Connection:

Possibility of use either joints or headers. Pipes and connection sizes must be selected according to the system supplier recommendation.

8.14   Control:

Individual control for each indoor unit to be synchronized with the out door unit.

Wired remote controller with digital display and function buttons.

Equipped with real time clock to enable weekly and daily schedules.

Possibility to be connected to a centralized controller or to a BMS system.

8.15   Refrigerant Pipes:

Copper tube for refrigerant piping according to ASTM B280. Units in mm

| Pipe Outside Diameter | Pipe Wall thickness |
| --- | --- |
| 6.4 | 0.8 |
| 9.5 | 0.8 |
| 12.7 | 0.8 |
| 15.9 | 1 |
| 19.1 | 1 |
| 22.2 | 1 |
| 25.4 | 1 |
| 28.6 | 1 |
| 34.9 | 1.3 |
| 41.3 | 1.7 |

8.16	extract Fans

Extract fan units shall be of twin centrifugal cabinet type. with one fan on duty and the other fan as stand by. Fan operation shall be controlled by built in controller to alternate operations and to operate the standby fan, should the on duty fan fails, provided all in accordance with the following requirements, as scheduled on the Contract Drawings and in the positions shown on the Drawings.  All fans shall be of belt driven  motors.

The housing of units shall contain all components of the unit except the terminal box for electrical connections. The housing shall be provided with dust-protected access covers to IP54 of BS5490 for inspection, and replacement, of all components. No electrical component shall be fixed to or supported by any access cover. A galvanised mild steel terminal box shall be securely fixed to the outside of the casing in a suitable position. Units to be located in plant rooms may be supplied in chassis form, where specified. Unless otherwise specified the fans shall be arranged for automatic changeover.

Housing and cowls of externally mounted units shall be weatherproof and manufactured from galvanised mild steel or aluminium alloy sheets, or glass reinforced plastics to BS 3532, assembled with compatible and non-corroding nuts, bolts, washers and ancillary items.

Discharge outlets shall be weatherproof and include guard screens to IP20 of BS5490, to prevent finger contact with electrical and moving parts. Each fan damper shall close when the fan is de-energised. All items shall have a non-corroding finish.

Except where otherwise specified dual fans and motors shall be fitted on a common baseplate supported on anti-vibration mountings.

Backdraught dampers shall have edge seals and shall open and close fully. All blades shall be mechanically linked or close by gravity or light springs and be galvanised mild steel except where specified otherwise.

Fan failure in units of less than 500W fan shaft power shall be sensed and indicated from switches operated by damper blade movement, except where specified to be otherwise. Double throw airflow switches shall be used in units above 500W shaft power.

The unit casing shall be manufactured in aluminium alloy of rectangular section and shall house twin independent removable fan assemblies comprising direct driven double inlet forward curved centrifugal impellers running in metal scrolls. The discharge outlet shall incorporate backdraft shutter. The fans shall be fitted with air flow sensors and shall discharge into a common outlet plenum chamber through a linked shutter system. Motors to BS 5000 shall have ventilated enclosures and sealed for life sleeve bearings. Motors shall be held to scroll frames through resilient mounts. Motors and flow switches shall be pre wired to an electrical isolator casing accessible from external to the unit.

A rectangular inlet spigot shall be fitted to the base complete with flexible connector.

The unit casing shall be closed by a top cover, easily removable for access to the fans for servicing and maintenance purposes. The units shall be acoustically lined and non rusting fasteners shall be used throughout.

8.17	Centrifugal fans

Tubular centrifugal type fan shall be back ward curved or airfoil blades design with non  overloading operating characteristics and high efficiency. The fan shall include a flat wheel backplate with cast iron or fabricated steel hub and accurately formed spun shrouds. The wheel shall be dynamically balanced to commercial tolerances.

Fans shall be suitable for indirect drive by matched vee belts and pulleys. Where the system allows low flow.

Fans shall be selected for slow speed running low sound level and high efficiency. All fans shall be selected to be capable of being operated by at least 10% in capacity over the design volume specified.

Fans shall be provided with 1 speed 2 speed or 3 speed motors as indicated on the equipment schedule with Class “F” insulation with protection to IEC  34 5 Group IPW 54 and integral overheat protection.

Fan casings and scrolls shall be fabricated from heavy gauge mild steel plate adequately stiffened and supported. Fan casings shall be rigid and completely free from vibration and drumming and capable of with standing the pressures involved without leakage or distortion. Fan casings shall be continuously welded construction split as required to pass through available unit access doors.

Fan casings shall be bolted construction for ease of installation, the number of sections being dependent upon the size of the fan and access available for future removal and replacement.

Bearing blocks shall be carried on opposite sides of the fan casing on bearer bars forming a part of a rigid fabricated steel structure integral with the casing.

Fans shall be complete with:

- Backward curved / or airfoil blades

- Inlet cone

- All welded fan casings with reinforced outlets

- Side support frames

- Polished high grade steel fan shaft on with lubricating roller bearings

- TEFC electric motor rated for continuous operations in ambient temperature up to 50C

- Vee belt drive

- Galvanized wire mesh guards constructed and fitted to satisfy all rlevant safety legislation

- Rolled steel channel base frame

- Antivibration mountings

- Flexible inlet and outlet flexible connections

Laundry Exhaust fans components shall be constructed to operate continuously at not less than 200C.

All fan sets shall be finished with one priming coat and two coats of gloss. The impeller shall be finished in a contrasting colour. All fan sets shall be tested at Works and installed strictly in accordance with the manufacturer’s instructions.

8.18	Air  Outlets

- a)	General  Requirements:

Material    :	Powder Coated aluminium  of ARAL colors as approved by Engineer unless other wise specified.

Size            :	as indicated on Drawings.

Manufacturer: 	as far as practicable air outlets are to be the products of one manufacturer.

Approval     :	Approved manufacturers does not necessarily constitute approval of their products. The Contractor shall submit for approval a complete list of proposed air outlets, indicating manufacturer, catalogue number, details of construction and performance.

Noise level :	Size air outlets for minimum noise levels. Not to exceed the allowable noise level at the specified air quantity, as measured on the A scale of a standard noise level meter unless specified otherwise.

Gaskets     :	To be fitted at factory on all air outlets to prevent air leakage around them and dust streaking of walls and ceilings.  To be felt by sponge rubber.

Screws      :	All screws used in fixing air outlets to be chrome or cadmium plated.

Finish        :	Shall be powder coated and as agreed upon with Engineer at time of order. They shall be factory coated of colour approved by the Engineer.

- b)	Ceiling diffusers:

They shall be of the louvred face pattern. Select to give required throw to nearest wall. Terminal velocity is not to exceed 50 feet per minute at specified air quantity. Velometer velocities through diffuser are not to exceed 500 feet per minute.

They shall be flanged suitable for flush mounting to false ceiling and round or square neck sized to fit over the duct. They shall be complete with volume control damper accessible from face of diffuser and equalizing deflectors to provide an even air discharge pattern.

Square and rectangular ceiling diffusers shall be two piece design consisting of mounting frame and removable core attached with spring lock and safety chain.

- c)	Linear and Curved Diffusers

Linear and curved diffusers shall be continuous, single or multiple slot type, with individually adjustable supply air pattern and volume control blades on each slot. Air supply pattern is to be adjustable in 6" lengths through 180 degrees from diffuser face with two way incremental capability from multiple slots.

Noise level is not to exceed 25 NC at specified air quantity measured at vertical position.

Diffusers to be of total length, number of slots and cfm per linear foot run as indicated on Drawings.

Linear and curved diffusers shall be without face flange screw holes, and shall be suitable for ceiling mounting air supply and for air return. Diffusers shall be supplied in standard lengths up to 60 inches. Where longer lengths are specified, multiple lengths shall be joined with special key strips supplied with the diffusers.

Linear diffusers shall be complete with end caps on end sections and one piece diffusers, grid pattern air straighteners and concealed mounting brackets for easy installation without need for special tools.

- d)	Air register.

Air register supply and return shall be selected for correct deflection to suit shape of room. Terminal velocity at end of throw to opposite wall is not to exceed 50 feet per minute at specified air quantity. Velometer velocities through register or grille are not to exceed 500 feet per minute.

Return/Extract air grilles, fixed blade type with blades set at 45 degree deflection parallel to long dimension. Grille net free area is to be not less than 70 % of gross face area. They shall include volume dampers of the opposed blade type.

- e)	Transfer grilles

Transfer grilles to be of the fixed blade type, with blades set at 45 degree deflection parallel to the long dimension. Grille net free area not to be less than 70 per cent of the gross face area.  They shall include double frames.

- f)	Return /exhaust air registers

Register are to have fixed, 1" wide, horizontal louvers set at 45 degree deflection, spaced at 3/4" centres and equipped with vertical, opposed blade, key operated volume control dampers accessible through the face of the register.

- g)	Door grilles

Door grilles  no vision, V-shaped louver type. Grille net free area is to be not less than 70% of the gross face area.

- Grilles shall be installed in an  approved, neat, level, square, tight manner.

- h)	Outlets

Outlets that are installed directly on ducts shall fit to an appropriate sheet metal flange formed integrally from the duct and be fixed with sheet metal screws.

Outlets installed in walls shall be fixed to an appropriate wooden frame provided around the opening. Fixing to frame shall be with chrome plated or cadmium plated wood screws.

Duct collar to finish flush with external surface of frame shall be provided and shall be nailed to the frame to make a tight connection. The frame shall be of a size to be completely concealed by the air outlet flange.

8.19	Manual  Volume Control Damper

Provide dampers of a proprietary manufacture mounted in a flanged or folded section galvanised zinc spray coated steel frame.

Construct damper frames and blades to ensure rigidity and prevent distortion and jamming in operation.

Provide for low velocity air systems, single thickness damper blades.  Provide for high velocity air systems, double thickness, streamline pattern damper blades. The edges of the blades shall be folded and left smooth. Dampers located inside aluminium duct shall contain blades made from aluminium extruded sections .

Each blade shall be securely bolted to solid spindles mounted in low friction sealed for life ball bearings or self lubricating for life, special plastic bearings (Pocan) suitable to withstand temperatures up to 120 degrees C.

Provide single bladed dampers for ducts up to 150 mm. in height and multi bladed dampers, not more 150 mm. wide generally, for ducts and apertures in excess of 150 mm. in height.

All blades of multileaf dampers shall be rigidly fixed to their spindles and inter linked to ensure that one movement of the operating handle shall move each blade an equal amount and differential blade movement does not occur.

- Provide all dampers with external indication of blade position.

Dampers shall be rigid in construction and free from vibration in any position.  Casings shall be air tight. Dampers shall be accurately installed in relation to their quadrants so as to permit free movement of 90 degrees.

Dampers greater than 1200 mm. in height or width shall be built up in two or more sections, suitably interconnected with air tight seals between sections, and mounted into a framed casing having additional bracing members as necessary to avoid flexing large installations shall be site assembled.

Provide accessibly located and external to dampers a substantially constructed, rigid mounting bracket to which a cast quadrant with lockable cadmium plated screws, nuts and washers. The quadrant shall be clearly marked "open" and "shut".

Dampers shall be provided where required for the proper regulation of the ventilation systems. In general, the dampers shall be provided as follows, and at such other points indicated on the Drawings:

1	In all branches serving more than 3 Nos. supply and return registers

2	In all branches serving fresh air to spaces

3	In all main fan supply, recirculation and extract ducts.

4	In all connections to grille and diffuser plenum boxes.

Scribe or indelibly mark the final setting on all dampers and adjusting devices after balancing.

- Standard dampers must always be installed with the blade axles horizontal.

- 8.20	ROOM THERMOSTAT

The AC units shall be controlled by a wall mounted sensor with recessed housing and over lapping cover plate. The housing shall have conduit entry provision and shall be handed to the electrical Sub Contractor with instructions for fixing at the time that conduits are installed.

Interconnecting cables shall terminate at a fixed terminal strip within the housing and all connections to the components mounted on the fascia.

Facilities on the sensor shall include :

·	Fan high, medium and low speed selector

·	ON/OFF switch

·	Temperature setpoint

·	Temperature digital readout

·	Power 'ON' indicator

·	Set back default setting (economy / normal)

·	Reverse auctioning of the temperature controls depending on the temperature of the water supplied to the coil.

- Drawings

Detailed drawings of the complete installation including the housing, fans, filters and structural arrangements, together with detailed circuit diagram and control panel arrangement shall be submitted to the Engineer prior to ordering.  These drawings are for approval prior to manufacture and similar 'as fitted' details are to be provided in the service manual.

9.1  DELIVERYY STORAGE, AND HANDLING

| A. | Deliver insulation, coverings, adhesives, and coatings to site in containers with manufacturer’s stamp or label, affixed showing fire hazard indexes of products. |
| --- | --- |
| B. | Protect insulation against dirt, waters and chemical and mechanical damage. Do not install damaged or wet insulation; remove from project site. |

9.2     PIPING INSULATION MATERIALS

| A. | Piping Insulation: Blocks of tubes molded to conform to pipe , with a minimum density of 110 Kg/m3 and a maximum K-factor of 0.04 w/m c at a mean temperature of 24 C . The temperature range shall be 0 F to 200 F . |
| --- | --- |
| B. | Jackets for Piping Insulation: ASTM C 921, Type I for piping with temperatures below ambient, Type II for piping with temperatures above ambient. Type I may be used for all piping at Installers option. |
| C. | Encase exterior Piping and boiler room piping insulation with sheet metal Jacket with weather-proof construction. |
| D. | Bandage and Wires : As recommended by insulation manufacturer for applications indicated. |
| E. | Adhesives, Sealers, and Protective Finishes: As recommended by insulation manufacturer for applications indicated. |

9.3    DUCTWORK INSULATION MATERIALS

| A. | Fiberglass Ductwork Insulation: Duct insulation shall be flexible blanket of fibrous glass faced on one side with fire-resistant reinforced aluminium foil having a thickness of .025 mm bonded to flame-resistant Kraft paper . The density of the insulation shall not be less than 24 Kg/m3 and a maximum K-factor of .04 w/m C at 24 C mean temperature . |
| --- | --- |
| B. | Duct Insulation Accessories : Provide staples , bands , wires , tape , anchors , corner angles and similar accessories as recommended by insulation manufacturer for applications indicated . |

9.4      INSPECTION

| A. | Examine areas and conditions under which mechanical insulation is to installed. Do not proceed with work until unsatisfactory conditions have been corrected in manner acceptable to Installer. |
| --- | --- |
| B. | Thickness of insulation shall be as recommended by the manufacturer for the temperatures and pipe sizes involved, and in accordance standards of T.I.M.A. |

9.5     DEMOSTIC HOT WATER PIPING SYSTEM INSULATION

| A. | Use 13 mm thick insulation for domestic hot water piping . |
| --- | --- |

HVAC PIPING SYSTEM INSULATION   9.6

| A. | Insulation Omitted: Omit insulation on cold piping within unit cabinets provided piping is located over drain pan; and on unions, flanges, flexible connections, and expansion joints. |
| --- | --- |
| B. | Application Requirements: Insulate the following cold HVAC piping systems: a. HVAC water supply and return piping, 2. Insulate each piping system specified above the following type and thickness of insulation: a. Tube Blocks : 19 mm thick for pipe sizes up to and including 3”, 25 mm thick for pipe sizes over 3”. |
| C. | Insulation of Piping Exposed to Weather and Boiler room Piping : Protect outdoor insulation from weather by installing outdoor protective jacketing sheet metal . |

9.7   DUCTWORK SYSTEM INSULATION

|  | l. Application Requirements: Insulate the following cold ductwork: a. Outdoor air intake ductwork between air entrance and fan inlet or HVAC unit inlet. b. HVAC supply ductwork between f an discharge, or HVAC unit discharge, and room terminal outlet. c. Insulate neck and belle of supply diffusers. d. HVAC return ductwork between room terminal inlet and return fan inlet, or HVAC unit inlet; except omit insulation on ductwork located in return air ceiling plenums. e. HVAC plenums and unit housings not pre-insulated at factory or lined. 2. Insulate each ductwork system specified above with one of the following types and thickness of insulation: a. Fiberglass: 1’’ thick, increase thickness to 2” in machine, fan and equipment rooms. |
| --- | --- |

9.8     INSTALLATION OF PIPING INSULATION

| A. | General: Install insulation products in accordance with manufacturer’s written instructions, and in accordance with recognized industry practices to ensure that insulation serves its intended purpose. |
| --- | --- |
| B. | Install insulation on pipe systems subsequent to installation of heat tracing paintings testing, and acceptance of tests. |
| C. | Install insulation materials with smooth and even surfaces. Insulate each continuous run of piping with full length units of insulation, with single cut piece to complete run. Do not use cut pieces or scrape abutting each other. |
| D. | Clean and dry pipe surf aces prior to insulating. Put insulation joints firmly together to ensure complete and tight fit over surfaces to be override. |
| E. | Maintain integrity of vapour-barrier jackets on pipe insulation, and protect to prevent puncture or other damage. |
| F. | Cover valves, fittings and similar items in each piping system with equivalent thickness and composition of insulation as applied to adjoining pipe run. Install factory molded, pre-cut or job fabricated units (at Installer's option) except where specific form or type is indicated. |
| G. | Extend piping insulation without interruption through walls, floors and similar piping penetrations, except where otherwise indicated. |
| H. | Insulation at strainers shall be neatly terminated at the basket removal flange. |

9.9    INSTALLATION OF DUCTWORK INSULATION

| A. | General: Install insulation products in accordance with manufacturer' a written instructions, and in accordance with recognized industry practices to ensure that insulation serves its intended purpose. |
| --- | --- |
| B. | Install insulation materials with smooth and even surfaces. |
| C. | Clean and dry ductwork prior to insulating. Butt insulation joints firmly together to ensure complete and tight fit aver surfaces to be covered. |
| D. | Maintain integrity of vapour-barrier on ductwork insulation, and protect it to prevent puncture and other damage. |
| E. | Extend ductwork insulation without interruption through walls, floors and similar ductwork penetrations, except where otherwise indicated. |
| F. | Corner Angles: Except for oven and hood exhaust duct insulation, install corner angles on external corners of insulation on ductwork in exposed finished spaces before covering with jacketing. |

9.10    INSTALLATION OF EQUIPMENT INSULATION

| A. | General: Install equipment thermal insulation products in accordance with manufacturer’s written instructions, and in compliance with recognized industry practices to ensure that insulation serves intended purpose. |
| --- | --- |
| B. | Install insulation materials with smooth and even surfaces and on clean and dry surfaces. Redo poorly fitted joints. Do not use mastic or joint sealer as filler for gapping joints and excessive voids resulting from poor workmanship. |
| C. | Maintain integrity of vapour-barrier on equipment insulation and protect it to prevent puncture and other damage. |
| D. | Do not apply insulation to equipment, breaching, or stacks while hot. |
| E. | Apply insulation using staggered joint method for both single and double layer construction, where feasible. Apply each layer of insulation separately. |
| F. | Coat insulated surfaces with layer of insulating cement, trawled in workmanlike manner, leaving smooth continuous surface. Fill in scored block, seams, chipped edges and depressions, and cover over wire netting and joints with cement of sufficient thickness to remove surface irregularities. |
| G. | Cover insulated surfaces with all-service jacketing neatly fitted and firmly secured. Lap seams at least 2". Apply over vapour barrier where applicable. |
| H. | Do not insulate boiler manholes, handholds, cleanouts, ASME stamps, and manufacturer's nameplate. Provide neatly bevelled edge at interruption of insulation. |
| I. | Provide removable insulation sections to cover parts of equipment which must be opened periodically for maintenance; include metal vessel covers, fasteners, flanges, frames and accessories. |

9.11     INSULATION EXPOSED TO WEATHER

| A | Protect outdoor insulation from weather by installation of weather-barrier metal jacketing. Metal jacketing shall be sheet metal . It may be factory-applied or field applied. Joints shall be overlapped a minimum of 2 inches. Securement shall be accomplished by using screws, rivets or stainless steel bands. Any vapour-barrier jacket or coating under the metal jacketing shall not be disturbed or punctured by the use of screws or rivets on the outer jacket. |
| --- | --- |

10 - SPECIALIST SERVICES MEDICAL GASES INSTALLATION

10.01	Scope of Works

The Works shall comprise the complete installation and setting to work of the specialist Services for Medical Gases Installations, as indicated on the Drawings and specified hereunder.

10.02	Medical Gases, Air and Vacuum

The medical gases installations shall comply in all respects. with the under mentioned Specifications and Hospital Technical Mararanda Nos. 2022 and standard specification C-11 issued by DHSS and accepted local standards of good health engineering services.

Medical Gases, Air and Vacuum are to be distributed throughout the Hospital complex to the outlets indicated on the Drawings. The Medical Gases Installation shall be installed in accordance with the following specifications.

10.03	Central Storage Cylinder System

A) Gases to be dispensed from cylinders :

The supply system for Nitrous Oxide shall comprise a centralized battery of cylinders, complete with support racks, headers, automatic manifold distribution panel and a 11 necessary controls, safety devices, alarms, pip work, valves and technical units for distributing the gas to the required positions as indicated on the Drawings, zoom data sheets, schedule of terminal units and rigid ceiling pendants.

Note:

The following shall be supplied from plant installations specified later.

1)	Oxygen liquid storage tank with vacuum insulated evaporator (VIE) and standby cylinders and manifold

2)	N20 with standby manifold

3)	Compressed air plant with stand by manifold Plant

4) 	Vacuum plant

B)  	Location of Cylinders:

The cylinders shall be located in the Medical Gases Manifold room as indicated on the Drawing.

C) 	Initial Complement l of cylinders:

The Contractor shall be responsible for providing the full element of cylinders for each gas as required and these shall be used initially for purging and commissioning and handing over the system in proper working order.

D)      Capacity of System (s):

The capacity of the storage cylinder system(s) shall be as follows providing equal banks of cylinders, one for "duty" and one for "standby".

For Nitrous Oxide, cylinders arranged in two separate banks shall be provide as shown on drawings, each cylinder having a capacity of 9,000 litres.

The manifold system shall include an automatic change over control for the duty and 	standby cylinder bank and manual control for the emergency supply manifold.

E)	Cylinder Support Racks :

The supporting steel work for the cylinders shall hold them in a vertical position against the wall. The angle section shall have neatly formed semi circular cut-outs to space and supports the cylinders in banks. The racks shall be delete with security chains and shall be securely bolted to the walls.

F)       Additional Racks for Spare Cylinders:

The following racks shall be provided and installed in the positions shown on the Block Diagram Drawing.

The racks shall be in accordance with BS. 1319.

2 sets of Oxygen cylinders racks, capacity of each cylinder = 6,800 liter.

2 sets of Nitrous Oxide cylinders. Capacity of each cylinder = 9,000 liter.

Sets of Compressed Air cylinders racks capacity of each cylinder = 6,400 litres.

In the empty cylinder and full cylinder stores similar racks shall be provided for each gas. The racks shall be clearly and permanently identified for each gas.

G)	Automatic Manifold Assembly:

The Manifolds for all the specified gases shall be as far as possible identical in construction and the following clauses refer to the assembles for any of the "gases".

1)Manifold Headers :

Each bank of cylinders shall be located beneath a high pressure Manifold Header securely mounted to the wall at either side of a centrally mounted control panel. The headers shall carry flexible spiral tail pipe on the underside for connecting to the cylinders and each tail pipe shall incorporate a renewable non-return valve on the manifold header to allow removal and replacement of any cylinder without interrupting the supply from others in the same bank.

2) Non-Interchangeability of Cylinder Connections

The screwed connections of the tail pipes to the cylinder valves shall be designed such that cross connection of the pipe for any one gas cannot be made to any cylinder for other gases, the exception being oxygen and air which to BS.341 Part 1 are identical.

3) Testing of Headers:

The manifold and pigtail pipe assembly shall be capable of withstanding a maximum working gauge pressure of 136 bar ( 1980 psi ) and shall be tested to twice this pressure by the manufacturer at his works and a test certificate supplied.

4) De-Greasing :

The assembly shall be degreased and delivered to Site in a sealed polythene bag or cover and labeled to the effect that it is degreased and shall on no account be contaminated by dirt, oil or grease during erection or afterwards.

5) Manifold Control Panel:

Each pair of headers shall connect to a control panel which shall automatically reduce the high pressure gas or air to a low distribution gauge pressure of 4.14 bars + 0.14 bar ( 60 p.s.i.+2 p.s.i.) for gases.

6) Automatic Operation:

The control panel shall dispense gas for each of the two cylinder banks in turn via a common distribution pipe and when the "duty" bank pressure falls to 7 bars (100 p.s.i.) the panel shall automatically switch over to the "reserve"bank, without any interruption o f the supply.

The panel shall incorporate a pressure regulator, a pressure switch and automatic valve to each bank in order to carry out the above operations.

It shall be possible to select either bank of cylinders as the duty bank and to change over manually to the reserve bank despite any electrical supply failure.

A reserve pressure regulator to each bank shall automatically take over if the change over valve fails to operate or if the low pressure regulator fails to open sufficiently. It shall be possible to carry out maintenance work on the pressure regulators and parts for one bank without affecting the supply from the other bank

Automatic panels shall be capable of passing 300 litres per minute at a gauge pressure of 4.14 bars (60 p.s.i.).

7) Pressure Gauges:

The control panel shall incorporate three pressure gauges ; one high pressure gauge to each cylinder bank and one common pressure gauge on the outgoing supply to the distribution pipework.

The gauges shall conform to B5.1780 and be of the safety pattern to Appendix D with special precautions to Appendix E and be graduated in bars and p.s.i.

Each gauge shall carry the name of the gas on the dial face with warning - "USE NO OIL OR GRFASE".

Gauges shall be degreased and maintained in this condition before and after installation.

Isolating valve or cocks shall NOT be provided to gauge connections.

The dials shall be marked with a blue line at the normal working pressure and a red line at the minimum allowable pressure.

8) Control Panel Identification :

Each panel shall carry in large letters on the front the name of the gas being controlled, the letters shall be embossed, engraved or otherwise marked on so indelible. Painting or adhesive lettering shall not be permitted.

9) Heat Manifold for Nitrous Oxide:

On the Nitrous Oxide manifold, electric heating elements shall be incorporated.

10) Electricity Supply:

The manifolds shall be suitable for operating from a 220 volts, single phase , 50 Hertz, A.C. Supply.

Any internal wiring in the panel shall have a flame retardant sheath to comply with I.E.E. Regulation 8.16.

11) Precautions against leakages:

All parts of the Control Panel shall be constructed of materials which will not deteriorate during service and lead to leakages. Diaphragm gaskets of pressure regulators shall not be of fibber but of brass.

h)  Standby Manifold :

Each gas (or air) installation shall include a standby manifold.

The stand manifold shall be complete with reducing set, high and low pressure gauges, relief valve and isolating valve. The Oxygen and Air manifolds shall come "on stream" automatically if the main plant fails. A schematic office arrangement is included at the end of the specifications.

The regulators shall have a nominal working capacity of 300 litre/min. and be set to operate at a gauge pressure of 4.14 bars (60 p.s.i.) for Nitrous Oxide.

j)  Safety Relief Valve:

A self closing safety valve shall be fitted on the distribution pipe between the main manifold control panel and the external isolating valve. This safety valve shall not be housed in the main manifold control panel.

An identical safety valve shall be fitted on the emergency panel.

The valve shall have a flow capacity at least equal to the maximum flow rate of the control panel and shall be set operate at 25% above the distribution pressure.

The valves shall be of a type which can be locked and sealed and shall be of non-ferrous material.

Each Relief Valve shall be coupled to a copper vent pipe one size larger than the distribution pipe and vented to atmosphere at a suitable level and position outside the building. The end of the vent pipe shall terminate in an inverted 'U' bend with wire mesh and a suitable shield. The discharge point shall be finally agreed on Site by the Engineer and Contractor to ensure that there is no danger of fire, injury to personnel, contamination or interference with air intakes or windows. The safety valve and vent pipe shall be supplied and installed in a degreased condition. Weather proof notices shall be fixed at each discharge point stating:

" Danger keep clear , medical gas discharge point "

k) Pressure Regulating on Distribution Main

Pressure regulators shall be fitted on the outgoing main, in duplicate for standby purposes, to control the pressure of the air as it leaves the plant room.

The pressure shall be reduced to a gauge pressure of 4.14 +/-0.14 bar.

l) Pressure Gauges and Safety Valve on Distribution Main

One pressure gauge and one safety relief valve shall be fitted on the outgoing main following the pressure regulating valves. They shall be of the type and size as described for the receiver vessel. The relief valve shall be vented via copper pipework to a safe position.

The gauge shall not have an isolating valve or cook. The dial shall be marked with a blue line at the working pressure and a red line at the minimum allowable pressure.

Similar safety valves and gauges shall be fitted on the pressure side of any regulating valves elsewhere along the distribution main.

m) Electrical Installation Works :

All electrical equipment shall be supplied and installed by the Contractor.

The interconnecting wiring shall be carried out by the Contractor.

11.04 Liquid Oxygen Supply System (VIE)

a) 	Main Plant VIE

The gaseous oxygen distribution pipe work system throughout the Hospital shall be served from a liquid oxygen storage installation designed for medical oxygen systems. The plant shall consist of a bulk storage cylinder vacuum insulated evaporator and shall have a minimum capacity of 3000 litres of liquid oxygen and be capable of supplying the ACD of 1250 1/min plus 25%.

The inner pressure vessel shall be designed and constructed of stainless steel to supply with BS 5500, Category 1 and the outer vacuum jacket of carbon steel designed for the environmental conditions to which the installation will be exposed. The space between inner and outer jackets shall be filled with granular expanded insulant and evacuated to provide a high vacuum and low heat transfer.

Safety devices, control valves and gauges shall be as indicated on Schedule 1 to this section of the Specification.

The equipment shall be protected against over pressure in both gas and liquid phases by pressure relief valves and brusting discs. Provision shall be made by duplication of safety devices for maintenance.

b) 	Vaporizer:

The vaporizer shall be installed adjacent to the VIE and arranged to increase the temperature of the oxygen to ambient level with gas at a pressure of 13-15 bar.

c) 	Oxygen Delivery :

Oxygen gas from the VIE and vaporizer shall be reduced in pressure to 8bar and a manifold provided to which shall be connected the standby cylinders. A pressure regulator downstream shall provide a final output pressure relief valve set at 5 bar shall protect the distribution system against excess pressure.

Pressure switches to operate in conjunction with the alarm system shall be provided connected into a final manifold.

d) 	Standby Manifold:

Emergency standby cylinders and manifold with automatic connections to the system in the event of a liquid oxygen failure shall be provided.

The emergency standby set shall comprise one bank of cylinders ready to automatically supply the distribution pipeline at a required pressure.

e) 	Alarms :

Alarm devices shall be provided as required in Section 11.09.

f) 	Operation:

The internal VIE pressure shall be controlled by a pressure regulating valve which allows liquid oxygen to flow from the bottom of the vessel to a coil where the temperature is increased and the resulting gas returns to the top of the vessel. The regulation valve shall modulate as required to maintain the required gas flow.

For maximum flow conditions liquid oxygen shall be forced by internal pressure through the vaporizer which raises its temperature and produces gaseous oxygen to the distribution system.

g) 	VIE Compound

The equipment shall be installed in a secure compound with 2.4 metre high wall and locked main alarm and escape gates and provided with power for the alarm system and lighting for maintenance and refilling at night. Weatherproof covers shall be provided for the evaporator, control panels and standby manifold.

Liquid oxygen plants are major hazards in the event of a fire and the installation shall be made as safe as possible by careful design and the use of non-flamable materials. Oxygen is heavier than air and therefore there shall be no open ducts, drains or gullies within 6 meters of the compound.

The floor of the compound shall be of concrete and capable of supporting a weight of not less than 75 Kn/m2. A hard standing shall be provided for the tanker immediately adjacent to the compound/fill point not less than 4.5 m x 4.5 m. The hard standing shall be concrete capable of bearing the weight of the road tanker. (Note tarmacadam and similar flammable finishes shall not be used). The hard standing shall be level with the compound floor where they abut and shall slope away from the compound.

Warning notices shall be provided clearly visible to the visiting tanker driver to indicate the type of gas and the maximum operating pressure. An instruction notice shall be provided on the VIE indicate a schematic diagram of the system and give operating, safety and shutdown procedures.

h)	Testing

The completed installation shall be tested at a pressure of 8 bar using nitrogen.

A small quantity of liquid oxygen shall be used for initial cooling of the plant and purging all air and test gas. The completed installation shall be tested and checked for operation of all regulating and safety devices.

j)	Filling:

The installation shall be arranged for routine replenishment from a specially designed road tanker without the need to interrupt the oxygen sto the distribution pipe work. The fill point shall be fitted with an oxygen specific coupling and dust cap.

At the time of Practical Completion of the Contract the VIE shall be complete with liquid oxygen not less than 50% by volume of the capacity of the cylinder.

11.05	MEDICAL SURGICAL AIR SUPPLY SYSTEM

a) 	Configuration of Plant

The plant shall comprise as a minimum:

Identical high pressure compressor after cooler units

One air receiver

A duplex filtration/ dryer system

Non-return valves, isolating valves. gauges and differential pressure switches

A plant operating and indication system

A plant intake system and multi purpose test point

b) 	Capacity of the Plant

The medical air plant shall be capable of producing the required flow (average continuos demand) corrected to NTP with two compressors operating. The pipeline pressure shall be 4 Bar ( nominal pressure) .

The surgical air line shall be capable of providing the required flow (average continuous demand) corrected to NTP with two compressor operating. The pipeline pressure shall be 7 Bar (nominal pressure).

Compressors shall not incorporate water seals.

Each compressor shall produce a minimum of 5 m3 / Kwh at a continuous flow rate of 100% and at 10% of the ACD measured over a 6 hour period.

c)	Air Compressors

Shall be coupled to electric motors to form a complete assembly. The assembly shall incorporate motors with Class ' F ' insulation and Class B temperature rise to BS 2757.

Motors shall be continuously rated, to BS 5000 and BS 4999, and suitable for D.O.L. or assisted frequent starting. They shall be of the 3 phase totally enclosed fan cooled induction type (IP44 for indoor use) and with a maximum speed of 1500 RPM.

d)	Aftercooling

Shall be of the air-blast type so that the air discharge temperature does not exceed 15 "C" above the cooling air inlet. Once through water cooled after-coolers shall not be used .

e)	Air Receiver

Shall be manufactured in accordance with BS 5169 with test certificates provided to the users.

Be provided with suitable lifting lugs and mounting feet which permit access to and adequate drainage from the drainage trap. And it shall have a minimum water capacity of 50% ACD for one minute.

f)	Filtration Dryer System

Shall comprise two independent sub-assemblies either of which may be selected as "DUTY" whilst retaining the second assembly as "STAND BY", each assembly shall comprise :

a-	Separator pre-filter-providing maximum retaining oil content of 0.5 mg/m3 , particle removal down to 1 micron and DOP penetration of less than 0.03 %

b-	Coalescing filter providing maximum remaining oil content of 0.01 mg/m3, particle removal down to 0.01 micron and DOP penetration of less the 0.0001

c-	Pair of dryer columns

d-	Dust filter providing particle removal down to 1 micron and DOP penetration of less than 0.03 %

e-	Activated carbon filter providing removal of hydrocarbon odors and vapors

f-	Dryer control/timing mechanism which ensures that the use of purge air for there regeneration process is related to the pipe-line demand by methods such as:

(i) 	Interrupting process timers in accordance with compressor operation, or with pressure fluctuations in the receiver.

(ii) 	Monitoring of dew point

(iii) 	Monitoring bed saturation

g-	Isolating and safety valves shall be rated at the total throughput of the compressor

The system shall satisfy the air quality requirements at standard temperature and pressure by excluding impurities in excess of:

Dry particulate- 0.01 mg/m3

Oil - 0.5 mg/m3 liquid aerosol and vapour.

Water	- 115	mg/m3 ( dewpoint of 40 " C at atmosphere pressure )

Carbon Monoxide- 5.5	mg/m3 (5 ppm)

Carbon Dioxide - 900	mg/m3 (500 ppm)

The system shall be provided with purge discharge silencers, and shall bear clear identification of each major component.

g)	Pressure Regulator/Filter Assembly

Shall comprise a duplex sub assembly with :

a- 	Duplexed 'sterile' filter assembly providing particle removal down to 0.01 micron and DOP penetration of less than 0,0001%.

b-	Duplex, non-relieving pressure regulator assembly designed to have a static pressure under	no flow conditions of 110% of the

nominal pipeline pressure and a minimum delivery pressure of 90% at the total throughput of the compressor.

h)	Relief Valves

Shall be fitted either integrally or separately as follows :

a- 	One on the delivery pipe downstream of each compressor and upstream of any isolating valve, non-return valve or aftercooler, capable of discharging the total throughput of the compressor

b- 	One on each air-receiver capable of discharging the total throughput of the compressor(s).

c-	Downstream of any pressure regulator other than line pressure regulators

i)	Safety Valves

Shall be immediately downstream of each line pressure regulator. Be to BS 1123 and be arranged to discharge safely so that there is no danger to personnel in the plant room, and be capable of discharging the total throughput of the plant at a pressure of 175% of the nominal pressure and automatically resetting at 125% of nominal pressure.

j)	Automatic Drain Traps.

Shall be installed for the following :

a. 	After coolers

b. 	Air receivers

c. 	Separators

d. 	Coalescing filters either electrically or mechanically operated, and shall be provided with the auto discharge piped to a suitable gulley container or tundish so that the discharge is visible, and shall be provided with a manual drain valve.

k)	Non Return Valve (NRV)

Shall be fitted;

a- 	Downstream of the compressor prior to entering the receiver and after any flexible delivery pipe,

b- 	After the dust filter of each dryer,

c- 	In the Pipeline connecting the plant to the pipeline distribution system, upstream of the emergency/reserve manifold connection to it.

l)	Isolating Valves

Shall be of the manual ball type, and be located:

a- 	On each compressor discharge upstream of NRV,

b-	Upstream and downstream of multiple air-receivers to enable either receiver to be isolated without interrupting the air supply to from the other(s)

c-	Upstream of auto drains,

d- 	Upstream and downstream of each air filtration dryer sub- assembly,

e- 	Upstream and downstream of each individual pressure regulator final filter /relief valve assembly,

f 	At the plant discharge between the NRV and the connection to the pipe line,

g. 	At the locations detailed on drawings,

m)	Pressure Indicators Differential Pressure

Shall comply with BS 1780 or equivalent and be calibrated in bars. The working range not to exceed 65% of full scale range except on differential pressure gauges, and shall have a minimum scale length of 90 mm. In the case of pressure indicators, they shall be located on :

a- 	Compressor Control Unit(s) indicating receive pressure;

b- 	Receiver(s);

c- 	Downstream of each pressure regulator;

d- 	On each dryer column

e- 	On the distribution main in plant room downstream of plant isolating valve ;

f- 	Upstream and downstream of each final filter.

In the case of differential pressure indicators, they shall be located across, or on, each coalescing filter, the dust filter and final filter.

They shall not include isolating valve or cock.

n)	Plant Operating and Indicating System

Shall have indicators with a design life of at least one year when used continuously and be identified as to their function, and shall arise as a minimum:

a- 	Plant control starter unit which provides the overall plant control,

b- 	Filtration/ dryer assembly control unit(s);

c- 	Plant status monitoring ;

d- 	Plant status indicator unit;

e- 	Plant to alarm system interface unit.

The above may comprise separate units, grouped separate units or may be installed in a	common panel provided that the individual starter unit(s) are housed in a separate compartment, these may be located either on the plant room wall or on the plant.

When pneumatic components are installed they shall have ventilated enclosures, bear appropriate identificatfor all functions and indicators and be capable of automatically re-starting on reinstatement of power supply.

o)	Power Control Unit

Shall derive its power supply from a separate sub-circuit from the 'Yellow phase, for each plant, have power supply for each compressor controlled by its an individual sub-circuit, be designed such that no single component failure results in loss of plant output.

Be manufactured and installed in accordance with IIE regulations, be provided with either DUTY/STANDBY selection for each of the compressors or automatic cyclical sequence selection with means for manual override, have means provided to ensure that two or more compressors will not start simultaneously when power is applied and have a warning notice to B.S 5373 and contain as a minimum for each compressor :

a- 	Green mains "supply on indicator

b-	Either "ON" or ON/AUTO" selector switch,	which	when turned "ON" ensures that the maximum and minimum receiver pressure switch(s) continue(s) to control "ON" and "Off" loading of the compressors ;

c-	Green "Compressor called for" indicator, when compressor motor is electrically energized and shall contain a discharge pressure indicator.

p)	Compressor Starter Units

Shall be manufactured and installed in accordance with IEE Regulations, operate their respective compressor(s) only, include safety interlocks as specified by the compressor manufacturer and be designed such that all safety interlocks inhibit plant operation until manually reset by means of reset button.

Contain as a minimum:

a- 	An isolator interlocked with the covers, with circuits and apparatus protected by HRC fuses to BS 88 or suitable circuit breakers to BS 4752 and/or BS 3671;

b- 	Industrial grade ammeter to BS 89 ;

c-	Total hours counter if not included in the plant control unit;

d- 	Green "Mains Supply ON" indicator (if mounted separate from compressor control unit).

q)	Filtration/Dryer Assembly Control Unit

Shall	control	the operation	of the filtration/dryer assembly, have separate power supplies for the 'duty' and stand by' filter/dryer assemblies taken from the same phase and shall contain as a minimum:

a- 	Duty dryer selector switch ;

b- 	ON/AUTO selector switch;

c- 	Individual fused separate acting system to control regeneration for the drier sub-assembly;

d- 	An economy system to control regeneration in accordance with pipeline demand;

e- 	Dewpoint sensor and pressure fault sensing;

f- 	Auto	changeover between each filtration/dryer subassembly, in the event of failure of the operating unit.

Automatic changeover is defined as:

i) 	Electrical and pneumatic isolation of the "Duty" sub-assembly such that it is taken off-stream,

ii) 	Energisation of electrical and pneumatic circuits of "standby" dryer such that it is brought on-stream

iii) 	Activation of appropriate fault indicator unit and associated volt-free contacts.

g-	Green function indicators for each filtration/dryer sub-assembly to indicate:

i) 	Dryer 1 selected

ii) 	Dryer 2 selected

iii) 	Selected dryer- 'Normal'

iv) 	Selected dryer- 'Failed'

be designed such that all fault indications remain until manually re-set by mains of a re-set button, in the event of either dewpoint failure, or other malfunction causing rapid depressurisation, automatically change-over dryers and:

a- 	The assembly to remain in this mode of operation until the fault has been identified and rectified,

b- 	On failure of the power supply, initiate the following:

i) 	Closure of the exhaust and purge valves;

ii) 	Opening of the inlet and outlet valves.

r)	Plant Status Monitoring

Shall be provided to detect faults on the compressed air plant for indication on the Plant Status Indicator Unit and Plant to Alarm Interface Unit as specified thereunder.

s)	Plant Faults

For each compressor, the following indication shall be provided:-

a- 	Control circuit failed

b- 	Overload tripped,

c- 	Aftercooler temperature high,

d- 	Activation of other safety devices supplied by the manufacturer,

e- 	Failure of the compressor to respond within permitted run-up time, eg: depending upon star-delta changeover pressure switch activation.

For the filtration dryer unit:

a- 	dewpoint fault,

b- 	Pressure fault.

t)	Plant Emergency

a- 	Receiver pressure fallen 0.5 bar below the	standby compressor cut in pressure,

b- 	Dewpoint above 26"C at atmospheric pressure (approx. 500 mg/m3).

u)	Pressure Fault (Reserve manifold)

When pressure in any manifold falls below 6.8 bar .

v)	Pressure Fault Pipeline

a- 	Low pipeline pressure- 10%

b- 	High pipeline pressure + 20%

w)	Plant Status Indicator Unit:

Shall be mounted on the plant room wall or within the compressor starter unit or plant control unit, and shall display as a minimum with indicators the following conditions for each compressor:

a- 	Power 'on' as a green signal

b- 	Control circuit failed as yellow signal;

c- 	Overload tripped as a yellow signal;

d- 	After cooler temperature high as yellow signal;

e- 	Activation of other safety devices provided by the manufacturer as a yellow signal;

f- 	Compressor failure as a yellow signal, where the Status Indicator Unit is separate.

For each dryer:

g- 	Power "on" as a green signal

h- 	Dewpoint fault as a yellow signal

i-	Pressure fault as a yellow signal

The unit shall transmit the above conditions (b) to (f) inclusive and (h) and (i) for the dryer, to the Plant to Alarm System Interface Unit as a plant emergency, via a volt free normally closed contact rated at 50V DC 50ma to operate indicators on the Plant to Alarm System Interface Unit. The unit shall have a warning notice to BS 5378.

x) 	 Plant to Alarm System Interface Indicator

Shall display the following:

a-	Green" Normal "

b-	Yellow "Plant 'Fault"

e-	yellow "Plant Emergency"

d-	Yellow "reserve cylinder banks below 6.8 bar pressure;

Be mounted on the plant room wall or in the Plant Control Unit, if mounted in the Plant Control Unit, be electrically isolated from other control or starter circuits, be suitably identified, be supplied from an independent supply, transmit conditions (b) to (e) to the central alarm system, utilize normally energized relays, de-energized under fault condition with contacts having a minimum rating or 50V DC. 50 ma and monitor input line faults where transmitted by external wiring by illuminating a 'red' system fault indicator on the interface unit alarm system.

y)	Air-intake Filter

The intake airpoint shall be located externally at high level at a position free from fumes and dust etc. A label shall be provided to indicate 'Medical Compressed Air Intake'.

Suitable sand and particulate filters shall be installed in the pipeline between the air intake position and the plant. Filters shall be dry medium type to HS 1701 with a dust retaining efficiency of 98% minimum grade CA, when tested in accordance with that standard fitted to the inlet to each compressor.

11.06	Medical Vacuum Plant

a) 	General Requirements:

The Contractor shall supply and install at the position shown on the Block Diagram, a Medical Vacuum Plant having one vertical reservoir vessel served by two identical vacuum pump units and complete with all necessary controls, drainage traps and bacterial filters.

b) 	Degree of Vacuum:

The overall design of the system shall be such that the degree of vacuum in the distribution pipework at the back of the remotest terminal unit is not less than 500 mm. Hg below a standard atmospheric pressure of 760 mm. Hg (360 Hg. absolute).

c) 	Total Flow (Hospital Demand)

The total flow of the system shall be sufficiently capable to meet the maximum A.C.D. (Average Continuous Demand) of the hospital.

d) 	Maintenance

The plant shall be designed and arranged to facilitate easy and efficient inspection and maintenance, to the satisfaction of the Engineer.

e) 	Precautions against Vibration and Noise:

Flexible pipework connections and resilient mountings shall be provided where necessary to prevent the transmission of vibration and noise to the building and distribution pipework. The Contractor be responsible for ensuring rigid connections are not made.

f) 	Builder's Work:

The Contractor shall supply and fix all holding down bolts, anti-vibration mountings and supply details of foundation requirements and hole positions.

g) 	Vacuum Pump Unit:

1) 	Definition:

Each vacuum pump unit shall comprise a rotary type vacuum pump driven by an electric motor mounted together on a common base plate having anti-vibration mountings.

2) 	Duty:

Each vacuum pump unit shall be identical and have a capacity of free air equivalent to twice of volumetric throughput at a vacuum of minus 400 mn. Hg.

The two vacuum pumps shall be arranged so that one pump is duty while the other is on standby and each shall be capable of dealing with 100% of the total Hospital design flow given in 110.05 Sub-Clause c) and running continuously at this load.

The vacuum pump set shall provide a minimum capacity of 200 litres per minute per kilowatt, corrected to NTP, when adiabatice conditions are achieved whilst maintaining a pipeline vacuum of 450 mm Hg.

h) 	Vacuum Pump Exhaust System

1) 	Silencers:

Silencers are not required for the rotary units.

2) 	Location of Discharge Pipes:

The discharge pipes from each pump shall terminate outdoors at high level above the roof and medical gases plant room. A Hazard warning sign shall be provided at this location.

3) 	Weather Protection

The discharge pipes shall be adequately protected cowls or other means from the ingress of water and sand and sited away from windows and air-intakes.

4) 	Back Pressure:

The exhaust system, shall be designed so that the back pressure does not exceed 50 mm. Hg (1.0 p.s.i.) at the peak demand and this figure shall be taken into account when sizing the pumps.

5) 	Permissible Noise levels:

The overall effect of anti-vibration mountings and pumps (both running) shall not produce a sound pressure greater than I.S.O. Rating of 75, measured 1.8 m. ( 6 feet ) away from sides and above the plant measured in free field.

j) 	Vacuum Pump Electric Motor:

Each electric motor shall be continuously rated for the maximum duty to be performed and shall be of T.E.F.C. type for 415 volts , 3phase , 50 Hertz AC supply and conform to BS. 2613 and BS.3979 (Metric Dimensions).

The motor shall directly drive the pump.

k) 	Motor Starters:

Each motor shall have a starter which shall be rated for frequent duty in accordance with BS . 587 and have thermal overload protection.

The starters shall be of the automatic type so that once switched on the motor will be capable of re-starting automatically should the supply be interrupted. This feature shall be indicated by a suitable warning notice displayed on or near the motors. A time-delay shall be incorporated to ensure that the pumps do not start together. 3 phase motors shall have single phasing preventors. Each star delta starter shall be electrically and mechanically interlocked to prevent simultaneous star and delta connection.

1) 	Ammeter:

An industrial grade ammeter to BS.89 shall be connected in the yellow phase connection to each motor.

m)	Vacuum Pump Controls:

1) 	Duty Selection Switch:

The two pumps shall be run alternately so that one is on duty while the other is on standby and a changeover duty switch shall be provided so that manual and automatic selection can be made.

2) 	Hour Counter :

An hour counter shall be provided on each pump to record its total time and assist in even running of the pumps.

3) 	Switches:

Each pump shall have a "hand-off-auto" switch to allow choice of either automatic or hand control.

4) 	Pressure Switches:

The pump shall be controlled by two pressure switches connected to and sensing the vacuum in reservoir.

The "high" pressure switch shall be set to operate the duty motor starter.

The "low" pressure switch shall be set to operate the standby motor starter.

When the pumps are on hand control the "high" pressure switch shall override and control and cut-off the motor when maximum working vacuum is reached.

n) 	Control Cabinet:

1) 	Compartment Arrangement:

The vacuum pump controls shall be arranged together in one metal cabinet with three separate fireproof compartments. The centre compartment shall contain the duty selector switch, wiring and accessories common to both pumps, while the other compartments each contain the controls for one pump and its associated equipment.

2) 	Isolating Switch:

The cabinet shall house a load breaking isolating switch interlocked with the cover and the circuits and apparatus shall be protected by H.R.C. fuses.

3) 	Regulations

Warning notices shall be interlocked in each compartment to warn of the presence of 415 volts.

4) 	Manufacture:

The cabinet shall be manufactured from sheet steel, rustproofed (zintec) or electro-coated rust inhibited and not less than 2.0 mm. (14 S.W.G.) thick and adequately braced.

The cabinet shall have an external finish of semi-gloss stoved or cellulose ename1 to B.S. Colours untreated parts shall have a rust inhibitor coat and an undercoat applied before manufacture.

o) 	Vacuum Reservoir Vessel:

1) 	Type and Design:

Each Vacuum Reservoir Vessel shall be of the vertical type and be designed to conform to BS.5169 Class III (Fusion Welded Steel Air Receivers).

2) 	Capacity:

The capacity of the vessel shall be suitable for the plant and shall allow for the plant to provide the duty required.

The capacity shall be such that the number of start/stop cycles of the pump on duty does not exceed 30 times per hour.

3) 	Safety Requirements:

Where inadvertent reversal of the pump motor occur on 3 phase supply, a pressure switch on the inlet pipe between reservoir and pump shall 1 switch off the motor on sensing a positive pressure. A non-return valve shall also be fitted as a further safeguard. On the inlet to each pump.

4) 	Inspection, Cleaning, Draining:

The reservoir shall have an inspection cover, a cleaning outlet and a manual drain valve.

5) 	Isolating Valves:

Isolating valves of the manual ball type shall be fitted upstream and downstream of each reservoir and arranged so that the pipeline vacuum can be maintained independent of the reservoir (s) .

6) 	Vacuum Gauge:

A vacuum gauge to BS. 1780 shall be fitted on each reservoir calibrated 0-760 mm. Hg and reading 0 at atmospheric pressure.

The gauge shall be complete with isolating valve or cock.

The dial shall be marked with a blue line at the normal working vacuum and a red line at the minimum allowable vacuum.

7) 	Pressure Switch Connections :

Provision shall be made on the reservoir for tappings to suit the pressure switch connections for vacuum pump control.

8) 	Test Certificates:

The reservoir shall have been pressure tested at the manufacturer's works in accordance with BS.5169 to 10.3 bars (150 p.s.i.) gauge.

p) 	Drainage Traps:

1) 	Duty:

The intake to the vacuum vessel from the distribution pipeline shall first pass through a drainage trap, installed in duplicate , each trap being sized to deal with the total maximum flow.

2) 	Sterilizing:

The bowl of the traps shall be sterilizable by the following method(s) :

(i) 	By means of moist steam at 2.2 bar gauge (32 p.s.i.) and 138"C (280"F) in a porous load sterilizer to BS.3970.

(ii) 	By means of dry heat at 160"C (320"F) for at least 60 minuets.

The trap bowls shall either be transparent or have transparent windows.

3) 	Spare Trap Bowls:

Two sets of spare trap bowls shall be included initially to cater for frequency of sterilizing required and to ensure that a sterilized set is available always for change-over purposes.

q)	Bacterial Filters:

1) 	Duty:

A bacterial filter shall be fitted between each drainage trap and the vessel, each filter being capable of dealing with the total maximum flow.

The filter housing shall be distinctly marked with the words "BIO-HAZARD".

2) 	Efficiency:

The penetration of the filters when tested by the sodium flame test in accordance with BS.3928 shall not exceed 0.05% at the design flow.

r) 	Operating of Traps and Filters:

The traps and filters shall be operated on a duty and standbybasis and manually operated valves shall be provided so that either of the sets can be selected and to allow for isolation for maintenance and changing of trap bowls filters.

s)	Standby Vacuum Facilities:

Standby Emergency Vacuum Facilities are not covered under this Contract.

An emergency service from portable electric suction apparatus to BS.4199 should be arranged with the Health Authority.

t)	Electrical Installation Work:

All electrical equipment shall be supplied and installed by the Contractor.

The interconnecting wiring shall be carried out to separate specification by the Contractor.

11. 07	Distribution Park System

a) 	Extent of Pipework:

The Contractor shall supply, install, connect up and test all the pipework and valves required from the supply source to the distribution terminals for each gas , air and vacuum system.

The pipe size and valve positions shall be as given on the Contract Drawings and test procedure as described later.

b)	Pipework Installation:

1) 	Fixing:

All pipework shall be fixed without any springing or forcing.

A clearance of 150 mm. shall be maintained between the pipework and other services. Where pipework crosses other services a clearance of 25 mm. minimum shall be maintained.

2) 	Gradients

Gradients are not required on gas, air or vacuum pipelines.

3) 	Drainage:

A full bore drain cock shall be provided at the bottom of each main vertical run on the air and vacuum pipework and at low points on long horizontal runs.

4) 	Diversion Sets

The use of fittings for diversion sets shall not be permitted and the sets shall be formed from a long length in one piece and cold drawn or hot drawn in a neat manner without buckling or thinning.

5) 	Routing to avoid Fire Risk Areas

The routes of the pipework shall avoid fire risk areas including laundries, boiler houses, generator rooms, incinerator rooms, storage rooms for combustible materials (unless the pipes are to be cased), lift shafts and kitchens.

6) 	Pipework Supports

Pipework shall be supported in accordance to HTM 22, 2022 & C-11 Standards.

Where valves are fitted the pipe shall be supported at both sides of the valve to facilitate valve operation without pipe movement.

Fixing brackets or supports shall be of a suitable non-ferrous material suitably treated to minimize corrosion and prevent electrolytic action.

The Contractor shall drill and plug walls and ceilings as required to fasten the supports. Where roof decking is encountered, the Contractor shall provide cavity fixing devices to fasten the supports.

7) 	Pipework in Floors, Walls, Ceilings:

Pipework in rooms and corridors shall be concealed either behind ceiling panels, or in walls, ducts or trunking. Removable covers or panels shall be provided to allow access to pipework. Pipework

shall not be buried solidly in floors, walls or ceiling except with the approval of the Engineer. Approval will normally be given only for tail pipes in one piece for terminal unit to service duct or ceiling void and for unjointed pipes from control valve to void. The route of the buried pipe should be clearly and continuously marked by chalk, coloured adhesive tape or otherwise, during construction, discourage the driving of nails etc., into or near the pipe. Where pipes are to be installed in partition walls the tail pipes of terminal units shall be in one piece (without joint) from the terminal unit to the service duct or ceiling void. Service ducts or voids should have adequate ventilation to prevent gas concentration in the event of a leak.

Where pipes pass through floors, walls or partitions, copper pipe sleeves, one size larger, shall be built in by the Contractor. Sleeves shall project between 1.5 and 3 mm. beyond finished surfaces and plates shall be fitted. All joints shall be accessible and no joints shall be made so that it is inside the pipe sleeve. In fire compartment walls the space between pipe and sleeve shall be sealed with a flexible fire resisting compound.

Where pipework is to be concealed it shall not be covered over until it has satisfactorily passed all pressure tests.

Pipework in service duct or voids, or in corridors where the pipework is not required to be concealed shall be surface run.

8) 	Special Precautions against Corrosion:

Where pipework is supported by or is liable to come into contact with timber that has been treated with compounds likely to cause corrosion of copper, the pipe shall be protected locally by impermeable materials such as PVC tape or spacers.

9) 	Cleanliness during Installation:

Great care shall be taken during installation to ensure that no extraneous materials are allowed to enter the pipework. Where any section of the pipework is left incomplete shall be sealed immediately with a plastic cap.

10)	Bonding and Earthing:

Wherever possible, pipelines shall be physically separated from the metal sheath and armour of electric cables and from metal conduits, ducts, trunking and bars and earth continuity conductors associated with any cables which operate at low voltage or above.

Where physical separation is impossible or when pipelines are in metal trunking and bed head units, the pipelines shall be bonded to the metal work in accordance with the I.E.E. Regulations.

The entire pipework system for each service shall be earthed by bonding to the Consumer's Earth Terminal, in accordance with the I.E.E. Regulations.

The pipework at each zone service unit valve box shall be bonded on the downstream side of pressure valves and upstream of vacuum valves to the local electrical earth.

c)	Pipework Material and Size:

1) 	Material:

Pipework material for gases, air and vacuum shall be phosphorous de-oxidised non-arsenical copper to BS.6017 Grade C106. In addition to BS. 2871 markings pipes shall be marked 'deg' or 'degreased' to represent compliance with clause 110.OOc).

2) 	Sizes:

Pipework sizes shall be to metric outside diameters in accordance with BS.2871, Part l, Table X.

3) 	Pipes shall be cut with circular cutters (not hacksaws) to prevent ingress of particulate matter.

d) 	Fittings Joints:

1) 	Fittings:

All fittings shall be to BS.6017 grade C106 and manufactured to BS.864 Part 2 from phosphorous de-oxidised non arsenical copper.

2) 	Fluxless Jointing Technique:

Fluxless jointing with an inert gas shield shall be used in accordance with the D.H.S.S. Directive No . WKO (82) 1 dated 27/1/82 .

Copper-copper to BS.1845 and no flux

Copper to brass or gunmetal joints at factory shall utilize a silver brazing material type AG132 to AG18 to BS.1845 and flux as recommended by the manufacturer. The completed assembly shall

be cleaned and delivered to site in a sealed bag for compliance with clause 110.OOc).

3) 	Inert Gas Shielding:

On site fluxless jointing and hot forming of bends shall be performed only when the internal bore is charge with carbon dioxide or nitrogen to BS.4105.

Runs of pipework shall be jointed starting at the joint nearest to the cylinder and progressing to the remote end of the run. Cylinders shall be complete with pressure regulator and flow control device for normal use and high flow flush purge cycle.

The Contractor shall ventilate enclosed areas where a gas shield is being used to ensure that safe working is achieved. Where necessary detection and alarm systems shall be used to avoid potential hazards.

Shield gas cylinders delivered to site shall be recorded and the removal from site also recorded.

4) 	Fittings:

Fittings on moisture eliminators and trap sets for vacuum and compressed air shall be brass compression to fittings, or flanged fittings, as appropriate.

5) 	Valve Joints Capillary or Screwed:

Jointing of valve to the pipelines shall preferably be made with a capillary joint

but the end feed method may be used if necessary and approved by the Engineer.

The finished joint will have to be cleaned in accordance with WKO (82)l.

Screwed joints shall be factory made using silver alloy.

This shall be done with valves dismantled to avoid damage to internal parts

and the same care shall be taken when making the capillary joint to the

pipeline tensure heat from the brazing operation does not damage

diaphragms , seatings etc .

All parts of the valves shall be maintained in a degreased condition.

e)	Demonstration Joints:

Every craftsman working on pipework jointing shall provide a sample joint on two sizes of pipework to demonstrate his competence before any site work is commenced.

Selected joints in the completed installation shall be cut out for checking and the installation reinstated at no extra cost.

Joints	will be satisfactory when brazing alloy has penetrated a minimum of 4 mm at any point and the internal surface is clean an free of oxide.

f) 	Jointing Methods:

All site joints shall be brazed except connections to plant and equipment which may be screwed or flanged.

g) 	Components Cleanliness and Protection:

1) 	Cleaning, Protection and Labelling:

All pipework and fittings for Medical Gas, Air and Vacuum shall be

cleaned at the manufacturer's	works, the pipes shall be individually fitted

with purpose made tightly fitting plastic caps or plugs to protect the bores

before despatch to Site. Pipes shall be delivered in bundles in

protective wrappings and fittings in sealed polythene bags, no capping

required. Larger shall be wrapped and package in cartons.

The cartons, bundles and bags shall be securely and clearly labeled:

"Degreased Materials. For use on Medical Gas Installations.”

The Contractor shall take great care in storing these materials and any

materials contaminated while on Site shall be returned to the manufacturer

for degreasing, at the expense of the Contractor.

2) 	Degreasing Processes:

The pipe shall be degreased internally by steam, then dried, shot-basted and

blown through with medical quality air from cylinders. After a visual

inspection each pipe shall be capped individually at both ends.

If steam cleaning is not economical, pipes above 54mm outside diameter

may be alternatively cleaned using an approved solvent such as methyl

chloride, which will leave no poisonous or explosive residues and the fittings

may also be cleaned by this method. The pipes and fittings shall be dried

out, inspected and capped or sealed, as specified later.

While the degreasing process is primarily concerned with the internal bore

of pipes, care shall be taken to avoid oil or grease on the outside, as being

a possible source of bore contamination.

h) 	Valves on Distribution Pipework:

The Contractor shall supply and fit valves at the positions shown on the Drawings and any deviation from these positions shall be agreed in writing by the Engineer.

1) 	Valve Materials and Types:

All valves shall be non-ferrous material and of the non-lubricated type, to the following details. They shall be capable of withdrawal without cutting of the pipework.

i) 	Medical Gas Valves:

Type			Ball - 90" shut-off

Bores			To suit line size

End Connection	To suit pipework

ii) 	Compressed Air Valves:

Type			Ball - 90" shut-off

Bores			To suit line size

End Connection	To suit pipework

iii) 	Vacuum Valves Type

Type			Ball/Diaphragm

(diaphragm only as main pipeline

valves)

Bores			To suit line size

End Connection	To suit pipework

Valves shall carry the manufacturers identification reference and size and be provided with locking facilities in the open or closed position.

2) 	Direction of Valve Closure:

Wheel head screw valves shall close in a clockwise direction. Lever Ball Valves shall close with a 90" clockwise turn. Wheel valves shall have the direction of closing indelibly cast or engraved on the wheel by means of an arrow and the word "CLOSE".

Lever ball valves shall have "ON"/"OFF" cast or engraved on to show when the valve is open or closed.

3) 	Maker's Identification

Each valve shall carry the manufacturer's serial numbers or identification or valve size.

4)	Pressure Testing and Degreasing:

All valves shall be pneumatically tested by the manufacturers to twice the working pressure and afterwards degreased for medical gas services using a suitable method as given in (110.05) before being individually sealed in polythene bags. Capping or not required.

5)	Certificates:

A certificate shall be supplied by the manufacturer for each valve or batch stating that pressure test and degreasing has been carried out and that any solvents have been completely removed.

i) 	Pressure Regulating Valve Set

Shall be capable of maintaining the indicated delivery pressure within ± 0.14 Bar of the valve setting up to the maximum flow rate of the system.

The delivery pipe lines shall be fitted with a self closing pressure relief valve to B5.6759: Part 2 of a type that can be locked or sealed and set to lift at a pressure related to the system and to comply with Specification C110.

The valves shall be of brass or bronze and be designed and degreased for medical gas use.

The relief valve shall have a flow of capacity at least equal to that of the pressure regulator immediately upstream of it. The discharge pipe shall be at least one size larger than the main pipe line. The discharge pipe shall be vented to atmosphere in an area where the discharge pipe will not create a hazard and where it is not liable to unsure personnel and clear of any opening or air intake. The vent terminal shall be turned down and fitted with a fine gauge filter. A warning label shall be fitted adjacent to each discharge point.

j) 	Area Valve and Service Units (AVSU) :

1) 	Location:

The Contractor shall supply and install lockable special purpose valve boxes for all the medical gas, air and vacuum valves located outside manifold and plant rooms and not contained in ducts or ceiling voids.

2) 	Purpose:

The boxes shall render the valves tamper proof and shall have transparent breakable panels to facilitate emergency operation of the valve. The valve boxes shall incorporate a physical break facility and a gas specific NIST connector on the inlet and outlet side of the valve.

3) 	Mounting Height:

The valves shall serve both emergency and maintenance purposes and because of the former requirement the box and valve shall be mounted at a centre height of 1.22 metres above floor level in a position not obstructed in any way by other equipment. Boxes for different gases grouped together may be fixed one above another in which case the mean height is to be 1.22 m.

4) 	Details:

Valve shall be tested and certified for a working pressure of 18 Bar and shall be cleaned as clause 11 g).

A removable section upstream and downstream of the valve shall allow insertion of a blank plate for isolation of the pipelines. One blank plate for each valve shall be clearly visible when deployed.

N.I.S.T. connectors up and down stream of the blanking plates shall have self sealing check valves and captive screwed caps.

5) 	Mounting Depth

The boxes shall be set into the wall with any projection being kept to a minimum and surface mounted boxes shall be avoided if at all possible. The Contractor shall ascertain the nature of the wall into which the box will fit and shall provide a final fix bezel to conceal the wall joints.

6) 	Standardized

The design of box offered shall be of a standardized pattern throughout the installation and have the following features:

i) 	Ease of access for fitting valve or maintenance.

ii) 	Designed so that pipework can be fitted easily either by having a split box or other suitable method.

iii) 	Ventilation to obviate a possible build up of gas in case of a leak.

iv) 	Non-interchangable keys so that a maintenance permit to work system is operated .

v)	Keys in duplicate.

vi)	Keys and locks with numbers engraved on.

vii) 	Arrows indicating the direction of flow.

viii) 	Breakable transparent panel (pull-out panel not acceptable ).

ix) 	Non-interchangeability of box	covers if this could wrongly identify-covers to be highned on.

x) 	Boxes shall accommodate one valve only ganging will not be permitted.

7) 	Multiple AVSUs :

Where two or more AVSUs are located together the individual boxes shall be enclosed in a common recessed housing complete with decorative front cover, pre connected pipework,alarm pressure sensors and local alarm panel. Each housing shall have a matching make up section extending to above ceiling level.

k) 	Valves in Ducts or Ceiling Voids

The valves shown on the Drawings in ducts or cupboards are intended for maintenance purposes only and are not required to be in valve boxes, providing the valves are lockable in the open and closed position. Suitable locking arrangements and duplicate non-interchangeable keys shall be provided so that such valves can be included in any permit to work scheme.

Care shall be taken not to install valves in cupboards or ducts which are poorly ventilated or in cupboards used for other materials which could be affected by leakages. Any pipe runs so situated shall be drawn to the attention of the Engineer before proceeding on Site.

j) 	Identification of Valves:

An engraved label of white "Traffolyte" or similar material shall be permanently fixed adjacent to each valve box to indicate the service and give the following information:

In Red letters:			Engraving Required:

1) 	Service			e.g. "OXYGEN"

2) 	Area Served		e . g . "WARD 1"

3)	Emergency Instructions e.g. "IN EMERGENCY BREAK AND

CLOSE VALVE ''

In Black 			Letters:

Valves				e. g. "VALVE ABC 678"

This number is for maintenance purposes and is to be agreed later on Site.

Valves in ducts or cupboards shall be similarly identified except for emergency instructions.

The titles of area served shall be finally agreed on site and the lables shall be installed before the systems are tested and commissioned in order to prove their correctness.

k) 	Terminal Units:

1) 	Extent of Work:

The Contractor shall supply, install and connect to the distribution pipework all the terminal units required at the positions shown approximately on the Drawings.

This excludes rigid pendants which are covered under a separate section. See Section 110.07 110.07 (Sub-Clause a) for location of pendants.

2) 	Definition:

All terminal units shall be defined as a single outlet point for a specific gas and shall be a separate unit for that one gas only. The units shall comply with BS.5682: 1984 .

Each terminal unit shall be identified on a fixed bezel for the service connected.

3) 	Fascia Plate:

Multiple terminal units at one location may be housed under a common fascia plate but it shall not be possible to mount the fascia plate incorrectly and reverse or alter the identification of the services. The units shall be mounted on a common back plate to ensure accurate centering of the units and allow precise fitting of the fascia plate so that the probes enter freely:

Identification of the service shall not appear facia plate.

4) 	Mounting Order:

The Terminal Units when viewed facing the units shall be mounted in the following order horizontally from left to right:

02. N20. MA4. H.P. AIR VAC. WAGE

5) 	Type:

The terminal units shall be either of the flush mounted type set into the wall or of the type to be mounted in bed head trunking as detailed on the drawings and described hereunder. The Contractor shall ensure proper liaison between the bedhead trunking manufacturer and the medical gases equipment supplier, with particular regard to the installation of tail pipes and outlets, and facia plates.

6) 	Mounting Heights:

The mounting height of the terminal units above floor level shall be as follows:

i) 	For Flush Mounted Units 	1.3 m. to centre of Unit.

ii) 	For "Rail" System		1.5 m. to centre of Unit.

7) 	Exact Positioning of Terminal Points:

The exact positions of the terminal units relative to the beds, operating tables etc., shall be agreed with the engineer before installation commences.

Due regard shall be given to ensure that nursing staff can couple up equipment easily, that short routes for flexible pipes to apparatus can be achieved without obstructing movement of staff or equipment round the patient and that access to the units for maintenance is easy without disruption to patients or other services. Terminal outlets shall be located so that flaw meters etc when plugged in are not obstructed other fittings.

8) 	Essential Design Features of Units:

Terminal Units shall be designed to incorporate the following features:

i) 	The ability to accept, retain and release the inserted probe by means of a quick release mechanism designed for single-handed operation.

ii)	Valves:

- 	A maintenance valve on the inlet to the unit which automatically losses to isolate when the socket assembly check unit is removed.

- 	A self-sealing check valve which is opened by the probe and on withdrawal closes before secondary lock engages.

iii) 	Non-swivel type terminal socket to probe connection so that secondary equipment such as a flow meter is not tilted during use. (Only on wall mounted units. Not on ceiling pendants).

iv) 	The terminal socket and check valve shall only accept the correct probe for the specific "gas" and not allow interchangeability with or partial operation by probes for any other service.

v) 	It shall not be possible to interchange the parts of a unit for one gas with those for a different gas and so enable a probe to be connected to the wrong position.

vi) 	Fascia plates which are not marked with the name of the gas shall not be used unless the design is such that interchangeability of fascia plates between the different gas terminal units is impossible.

vii) 	The front face round the terminal socket shall be exposed and shall carry "gas" name and colour.

viii) 	Identification by shape-incorporation of the probe is not an essential feature but if adapted by the manufacturer the following shapes shall be used

Service						Shape

Oxygen						Hexagonal

Nitrous Oxide					Round

Medical Air 4					Round with one

BAR						Flat

Medical Air 7 Bar				Round with one

Flat

Medical Vacuum				Square

ix ) 	The manufacturers and batch number.

9) 	Identification Colours and Wording Units:

The following names and colours shall apply:

Service			Colour			Wording

Oxygen			White			Oxygen

Nitrous Oxide		French Blue		Nitrous Oxide

Medical Air 4 Bar	White & Black		Medical Air 4 Bar

Surgical Air 7 Bar	White & Black		Surgical Air 7 Bar

Quarters

Medical Vacuum	Primrose BS.		Vacuum

10.E53

The name and colour shall be of a permanent method and it shall not be possible to transfer either to a different terminal.

The colour shall be of laminated plastic or other self coloured material and the words engraved in a contrasting colour.

Painting of the colour or wording is not permissible.

10) 	Pressure Loss Across Terminal Units:

The terminal Units shall be capable of passing the following flow rates without exceeding the stated pressure losses across the terminal units. (See following Table.)

Nominal		Maximum		Maximum

Gauge			Rate of			Permissible

Pressure		Flow			Loss across

Service		at back of		Req'd at		Terminal Unit

Terminal		This

Unit			Pressure

_____________________________________________________________

Bar		p.s.i	Litre/min.	Bar		p.s.i

at STP

_____________________________________________________________

Medical Gases		3.9		57	40		0.034		0.5

Nitrous Oxide/Oxy	3.9		57	275		5.55		8

Medical Air 4 Bar	3.9		57	50		0.04		6

Surgical Air 7 Bar	6.9		100	350		0.34		5

Medical Vacuum	Minus 400 mm.	40		100mm. Hg 

Hg Below standard atmospheric pressure of 760 mm Hg.

The above figures relate to the performance required of the terminals units.

11.08 	 Rigid Pendants for Operating Theaters

a) 	Location

The Contractor shall supply, install and connect to the distribution pipework in each operating theatre.

These fittings shall be in addition to the wall-mounted terminal units.

Terminal units shall be identical to wall units except that the non swivel facility is not required.

Any flexible tube shall use NIST connectors.

Access panels to connection points shall be provided with ventilation grilles or slots to prevent accumulation of gas in the event of a leak.

b) 	Pendant Types:

1) 	Primarily for Anesthetists Continuing:

-02,1-N20, 1 Vacuum, 1-4 bar air,1-Waste Anaesthetic gas 1-13A switched socket outlet, 1-adjustable low voltage switched socket outlet.

2) 	Primarily for surgical team containing. 2-Vacuum, 2-7 bar medical air (Nominal).

c) 	 Locations of Pendants:-

As shown on drawings.

d) 	Cleanliness:

All pendants shall be designed prevent minimum lodgement of dirt, dust, etc., and be easy to keep clean. The materials of construction shall have complete freedom from rusting, scaling or deterioration and may be enamelled finish, stainless steel, or heavily chromed finish.

e) 	Order of Arrangement of Terminal Connections:

On multi-point pendants, the order of arrangement of the terminal connection shall be as follows :

Oxygen. Nit. Oxide.	Comp. Air Vacuum Wage.

For pendants and columns the above order clockwise when looking up at the unit with wage in centre.

f)	Headroom Clearance:

All fittings shall provide a clearance of 2.0 m. above finished floor level.

g) 	Structural Requirements for Pendants:

The Contractor shall ensure that the requirements for the structural strength of walls or ceilings to which the pendants are to be fastened, is adequate and advise the Engineer if modifications are required.

h) 	Positioning of Pendants:

The exact positioning of the pendants shall be detailed before the installation commences".

j)	Electrical Services in Pendants:

The pendants shall carry electrical services which shall be in solid galvanized conduit separate from the medical service pipes.

The electrical fittings shall be provided are as follows:

1-13A switched socket outlet.

1Adjsutable switched socket outlet.

The electrical fittings shall be arranged in a neat manner to fit in with the medical terminal outlets and shall afford easy access for coupling up equipment. An access panel shall be provided to terminals blocks.

The electric supply to the fittings shall be 220 volt and 0-24 volt and the fittings shall be wired by the Contractor from a suitable distribution point.

Electrical components and cables shall be segregated by compartments and flexible conduit.

11.09	Identification of Pipelines

a) 	Permanent Identification:

The Contractor shall carry identification of the installation(s) by colour coding in accordance with Data Sheet 10.11/12 and BS.1710 (1971).

The identification shall comprise:

1) 	Colour banding applied at valves, junctions, either side of walls, floors and at intervals of about 2 m. on short runs up to 4 m. on long straight runs.

2) 	'The name of the service printed on colour band in a contrasting colour.

3) 	An arrow at each colour band showing direction of flow.

Letters to be minimum of 6 mm. high.

Self-adesive plastic labels or tapes of approved manufacturer may be used as an alternative to painting.

Where valves are in valve boxes and identified by ' Traffolyte' labels, colour banding is not required.

b) 	Temporary Identification:

During installation of piping, individual pipes, valves junction and ends shall be identified as the work progresses. This identification shall be at intervals similar to final identification requirements and may be made with removable labels. These temporary identification labels must be subsequently replaced by the permanent ones at an appropriate stage.

11.10	Warning and Alarm System

a) 	Extent of Work:

The Contractor shall supply, install and commission the following Warning and Alarm System which shall be connected to BMS ,comprising a combination of flashing lights audible Alarm, generally as Listed on Schedule.

b) 	Alarm Panel/Indicating Units:

A Main Indicating Unit shall be installed in the Telephone Exchange to monitor all the services in one chained unit.

Sub-Units shall be instal led in the following locations :

Sub-Units in at entrance of the departments are to be 2 lights/gas triggered by pressure switches laated danstream of the main area valve.

The alarm panels shall have sheet steel cases with stoved enamel finish and lockable hinged access doors to all components. A fused connection unit (3 amp. fused) shall be provided	adjacent to each panel to provide a 240 volts 50 Hz supply.

The panels and remote sensor etc. shall operate at extra low voltage .

Panels shall be designed for easy cleaning with no recesses or ledges to harbour dust and dirt.

Each panel shall incorporate a power pack comprising transformer, rectifier and battery designed to operate under alarm conditions for a period of not less than 4 hours after mains failure. The battery shall be of a type with average device shall be incorporated to prevent the system operating before the generator starts after power failure (i.e.20 seconds).

Alarm panels shall provide the visual and audible signals indicated on schedules 3/1 and 3/2.

The main alarm panels shall have interface facilities for multiplex signal transmission and reception. An interface unit with common alarm

terminals for each services shall be provided to transmit alarm signals to the Building Management System (BMS).

Local alarm panels shall operate independently and shall have a single pair of contacts to transmit an alarm signal to the BMS Local panels, shall be provided as shown on drawings located by the AUSU.

c) 	Electrical Power:

Each alarm unit work on low voltage D.C. current stepped down from a 220 Volt single phase supply via a double wound earth screened transformer.

d) 	Essential Features of Flashing Light Units:

The Main Unit and Sub-Units shall be of similar construction and embody the following features:

1) 	A solid state electronic components .

2) 	Translucent coloured panels for each service engraved with the fault" or normal conditions .

3) 	Two L.E.D.s in duplex on a 'plug in' board behind each panels each panel.

4) 	A green panel to indicate that the unit is normal.

5) 	A standardized size and type of Lamp throughout the system.

6) 	Its suitable for rapid on/off flashing operation with long life.

7) 	A lamp test button on each unit to test the audible Warning and all lamps on the unit simultaneously.

8 ) 	Audible alarms as indicated in Schedule No. 2.

9) 	An muting switch operation of which will silence the a audible alarm and cause the lights to continue flashing. After 15 minutes the audible alarm shall again sound unless the fault has been rectified. A 'follow' on' alarm after the mute button has been rated shall re activate the alarm. After the 'fault ' has been recified all systems shall automatically return to ' normal'.

e)	Working of Main and Sub-Units- "Flashing" System"

The units shall indicate the condition of all the monitored service simultaneously and for each service more than one panel may be indicated at a time.

The audible alarm on each unit shall be common to all the services and be arranged to re-set automatically after being muted, or if muting is not carried out, after the fault is rectified.

f) 	Arrangement of Panels on Units:

The order in which the services shall be arranged the panels shall be that adopted for terminal units :

When facing the panels the service shall be in the following order reading left to right:

OXY NIT.OXIDE. AIR VACUUM

g) 	Engraving of Fascia Panels of Units:

The fascia panels of the units shall be engraved with the name of the service, either at the top or bottom of each column of translucent panels.

The function of the various press buttons and switches shall also be engraved on the fascia panels.

All engraving shall be picked out in a contrasting indelible colour.

h) 	Monitoring Equipment:

The Contractor shall include for supplying and fixing all necessary Sensing Devices, operating Switches and Relays on the plant for the initiation of the Warning and Alarm signals.

Absolute reliability and long life of contacts in relay units shall be an essential feature of the equipment.

The alarm terminal block shall be remote from and electrically isolated from all other terminals and energized from a separate source.

All external circuits shall be fully monitored for open and closed circuit faults with 'end of line' resistors or diodes. Any fault on a circuit shall inan alarm condition. Sensing and monitoring devices shall be located at positions where testing and maintenance procedures can be easily carried out.

j) 	Setting of Sensors :

The sensing devices associated with the main alarm alarms shall operate as follows:

Oxygen Plant:

VIE low - 25% liquid by volume.			low

VIE Empty, Reserve in use.				Refill immediately

Reserve Cylinders-below 68 Bar.			Change Cylinders

Pipeline pressure incorrect.				Pressure Fault

Nitrous Oxide :

Duty Bank empty and operating			Change Cylinder

Standby bank below 14 bar				Change immediately

Reserve bank below 14 bar				Reserve Fault

Pipeline pressure incorrect				Pressure Fault

Medical Air Plant 4 Bar and Surgical Air 7 bar :

Plant Fault (Temperature high, dew point on dryer	Plant Fault

etc.)

Plant failure						Plant Emergency

Reserve Cylinders below 68 B			Reserve Fault

Pipeline Pressure Incorrect				Pressure Fault

Medical Vacuum:

Plant Fault (Change over to Standby,			Plant Fault

temperatures incorrect oil level etc.).                       Plant emergency

Plant Failure

Incorrect Pressure Fault                                          Pipeline Pressure

For pipeline pressure fault the setting of sensors shall be as follows:

Pressure Lines (7 Bar) above 875 KPa (925-840 KPa) or below 700 Kpa (756-684 KPa)

Pressure Lines (4 Bar) above 500 KPa (530-478 KPa) (432-390 KPa)

Vacuum - below 420 mm Hg (440 - 40 nm Hg)

Figures in brackets indicate acceptable tolerance .

The sensing devices associated with the local alarm shall operate as follows : -

7 Bar system High pressure operate 	840	KPa	High

reset		770 	KPa 	Pressure

Low pressure operate 		610	KPa 	Low

reset		660 	KPa 	Pressure

4 Bar system High pressure operate 		480	KPa High

reset		440 	Kpa 	Pressure

Low pressure operate 			350 	KPa	Pressure

reset			380 	Kpa 	Pressure

Vacuum System Low Vacuum operate 	440	mbar 	Pressure

reset		467	mbar 	Fault

11.11	Waste Anesthetic Gas Systems

A) 	General:

The system shall be an active type with either flush mounted integrated air breather units in the wall or integrated air break units in the medical gas rigid ceiling pendants. The basic design of the system shall be to BS. 6834 : 1987.

b) 	Air Mover :

The air movers shall be multistage units designed to provide continuous extract rate from each integrated air break unit of 75 litres/minute. The air movers shall be located as shown the Drawings.

c) 	Air Remover Control:

Each air mover shall be controlled by an ON/Off switch, which shall be flush mounted adjacent to each terminal unit. (For pendants on an adjacent wall).

The local switch units shall incorporate a green neon indicator light which illuminates only when the adjacent switch is 'ON' and air flow switch is operated.

d)	Exhaust from Air Mover:

The exhaust pipework shall be in copper pipe to the same standard as the medical gas pipeline system and shall discharge at each discharge at a safe position to atmosphere. A notice shall be provided at each discharge point to indicate "warning waste anesthetic gas discharge".

e)	Pipework and Fittings:

The pipework and fittings shall be copper except connections to valves and air mover which may be brass .

The pipework and fittings shall be of the same standard as the medical gas system but jointing may be carried out using soft solder.

f)	Pipeline Identifications:

The pipeline systems shall be identified as Waste Anaesthetic gas Systems and should incorporate flow direction arrows.

g) 	Integrated Air Break Units:

1) 	Ceiling Pendant Mounted Units:

The Units shall be located inside the medical gas pendants and shall terminate with 30 mm. female taper connection.

The air break shall be manufactured from brass and suitably chrome Plated.

The design shall allow a patient or equipment to be connected without a suction level in excess of 15 pascals being created at the 3o mm inlet taper at the design extract rate of 75 litres/minute.

The air break should have sufficient volume allow for impulses of gas from equipment.

2) 	Wall-mounted Units:

The performance details shall be the same as specified in 110.10

The integrated air break unit shall be mounted flush in the wall in a suitable box with the 30 mm. female inlet taper mounted horizontally and not protruding more than 25 mm. through the fascia plate.

The wall units shall be mounted adjacent to the medical gas terminal units.

11.12	Commission and Testing

a) 	General Requirements:

The Contractor shall allow for commissioning and testing of the complete installations generally in accordance with Commissioning Manual No.l5 - "Medical Gases and Suction System" published by H.M.S.O. The Manual covers	Pre-Commissioning Examinations and Tests, Commissioning Examinations and Tests and Handing Over Procedures. The Contractor shall satisfy himself that the installation is in all respects fit for use and conforms to the Specifications before inviting the Commissioning Engineer to witness the commissioning Tests. He shall do this by carrying out any pressure, flow-rate and anti-confusion tests necessary for that purpose.

b) 	Test Equipment:

The Contractor shall provide all test instruments listed in the commissioning.

Manual Sheet 15.1.7 and any other equipment not specifically listed but obviously necessary to carry out the tests.

In addition to the items listed, male probes shall also be provided for each installed gas, air or vacuum system, to operate the terminal units. The probes shall incorporate the anti-confusion identification shapes as given in Clause (110.06) of the Specifications or alternatively be marked with the "gas" name.

The accuracy of the test instruments shall be checked and certified by the Contractor to the reasonable satisfaction of the Engineer before any commissioning tests are carried out.

The Contractor shall also provide special "Flow Rate and Delivery Pressure Test Units" to check delivery at each terminal unit. The test units are to be as described on Schedules Nos. 3&8 and are calibrated to pass air equivalent to required "gas" flow rates.

The test units shall remain the property of the Contractor and not be chargeable to the Contract.

c ) 	Permit-toWork :

On new installations a permit-to-work procedure will not be required.

d) 	Pre-Test Examinations and Purge:

1) 	Pre-Test Examinations:

In addition to	the checks listed in D.H.S.S. Commissioning Manual 15 Sheets 15.2.6. it shall also be confirm that pipe diameters and mounting order of terminal units agree with Drawings and specifications.

2) 	Pre-Test Purging of Pipework:

Purge the pipelines with Medical Quality Cylinder Air at 8 bar (116 p.s.i.) gauge.

Gas used for purging at S.T.P. shall include impurities not in excess of:

Dry particulate - 0. Ol img/m2

Oil - 0.5 mg/m3 liquid aerosol and vapour)

Water - 115 mg/m3 dew points of 40' C at atmospheric pressure

Carbon Monoxide - 5.5 mg/m3 (Sppm) Carbon Dioxide - 900 mg/m3 (500 ppm)

This shall be done before Terminal Units are connected and before connections are made to main folds or plant. On no account shall industrial air be used for purging or tests.

All valves shall be fully open during the purging operations which shall continue for a sufficient length of tine to ensure that pipes are clear.

If any excess materials are ejected from the pipework, or blockages are encountered, the pipework shall be dismantled and examined, at the Engineer's discretion.

e)	Pressure Testing of Distribution Pipework Valves:

Pressure testing of the carcasing should be carried out before manifolds and theatre fittings are connected and before the "working parts"of the terminal unit are fitted:

1) 	Open fully all valves on distribution pipework.

2) 	Connect cylinder of Medical Quality Air to the System. Points of connection as in Clause (110.03).

3) 	All the systems may be under test at the same time if thought expedient and safe, additional cylinders to be provided.

4) 	The air test pressure to the pipelines shall be controlled afollows:

i) 	For Medical Gases, at 10.5 bars (150 p.s.i.) gauge for systems working at (4.14 ) bars ( 60 p.s.i.) gauge.

ii) 	For Compressed Air, at 10.5 bars (150 p.s.i.) gauge for all system.

iii) 	For Vacuum, at 6.9 bars (100 p.s.i.) gauge.

5) 	The system(s) shall be fully charged with air and the cylinder valve then closed and cylinder disconnected.

6) 	The test pressure shall be held for 24 hours.

7) 	Leakage shall be detected by means of soap solution applied to joints, valves etc.

8) 	All leaks shall be rectified and test repeated until the pressure can be held for 24 hours.

9) 	Ultrasonic leak detectors may be used instead of the method described in 7.

f) 	Checking Valves for Internal Gas Tightness:

All valves on the systems shall be checked for internal " gas tightness ".

With the pipeline full of air at the test pressure, commence at the terminal unit end, close each valve in sequence and release the pressure on the downstream side. Leaks should occur during a 15 minute test period on each valve.

g) 	Testing of Relief Valve Settings:

Before pressure tests on the pipelines are started, safety relief valves should be removed and outlets blanked off. After completing pressure tests, re-fit relief valves and test with air at 125% of normal pipe working pressure at which point the valve should discharge.

h) 	 Pressure Testing of Complete Installation (s):

On copulation of all previals tests, each system shall be finally tested using air at the nominal working pressure of the system and with all terminal units and theatre fittings connected:

1) 	Open main isolating valves between manifold or plant and distribution pipework.

2) 	Open isolating valves on terminal units and special fittings.

3) 	Open all valves on distribution pipework.

4) 	On Manifold Systems, connect cylinder of medical quality air to the manifold and test at working pressure for 24 hour period during which a leakage of up to 2 p.s.i. is allowed.

5) 	On Compressed Air Plant installations, use the compressors to charge the system and test for 24 hours as above.

6) 	On Vacuum System, connect cylinder of medical quality air to position as in Clause (110.03) Sub-Clayse in plant roan and test at 0.7 bar (10 p.s.i.) gauge for 24 hours as above.

7) 	The Vacuum System shall then be subjected to a vacuum test using the pumps to exhaust down to 5 50 mm. Hg gauge (210 Hg absolute). With the pumps switched off and the Vacuum Plant isolated, the pressure shall not rise more than 10 mm. Hg in one hour and the test shall be held for 24 hours. If the pressure rise is exceeded the system shall be checked for leakage and after rectifying re-tested until the pressure loss can be held within the limit specified.

8) 	The correct operation of any reducing valves on the systems shall be checked during these tests.

9) 	During the above pressure tests, once the system are fully charged with air the valves at the source of supply shall be closed.

j)	Testing for correct connections throughout the installation (Anti-Confusion Test) and correct valve zoning:

1) 	Checking for correct Pipework Connection (Anti-Confusion Test):

i) 	Connect pipework to terminal units and manifolds or plant.

ii) 	Ensure that all valves are fully open at the same time on all the installed pipework and terminal units.

iii) 	Ensure that all valves isolating plant or manifold from pipelines are closed.

iv) 	Connect cylinder of medical quality air regulated to the Oxygen system designed working pressure to the Oxygen system and by means of an oxygen probe check that air is being delivered to every oxygen terminal unit or special fitting. At the same time using probes for the other gases, air and vacuum Prove that air is not being delivered to these positions. The air shall be introduced into the system at the following positions:

or Oxygen connect into standby.

For compressor plant connect into standby manifold.

For vacuum connect into position behind main isolating valve throughout specially provided valve.

Special adaptors or probes shall be provided by the Contractor as necessary to allow air cylinders to be connected to the different "gas" connections.

v)	The results of these tests shall be recorded for each terminal unit in the from of Schedule 10.

2) 	Check for Correct Valve Zone Control:

On proving that all Oxygen pipelines are connected to correct positions follow by checking that all isolating valves on the oxygen system	actually control the department or area specified on the valve label and shown not the Contract Drawings :

i) 	Close the valve being checked.

ii) 	Release downstream air through oxygen terminal units.

iii) 	Check for non delivery of air through each oxygen terminal unit to be isolated the valve.

iv)	Ensure that valves are reopened after these tests.

3) 	Repeat Tests for Other "Gases":

i) 	Disconnect air cylinder from Oxygen system.

ii) 	Release air from oxygen system.

iii) 	Repeat tests in Clause (110.10) Item 1 and 2 for other gases, air and vacuum. In each case a cylinder of medical quality air is connected to the system and regulated to the system working pressure for the pressure gas installations and at a gauge reassure of 0.7 bar (10 p.s.i.) for vacuum installations.

iv)	During each test, check all other terminal units for non-delivery of air.	This shall include checking all include service outlets such as town gas, etc., which follow the same routs the medical gas systems.

The Contractor shall ensure that all valves on these services r in fully on during the tests and the supply is cut off or disconnected so that any cross connections to medical gas pipes are discovered.

4) 	Rectifying Errors:

The Contractor shall rectify any cross-connections or wrong valve zoning as soon as discovered, without proceeding any further with tests. At the same time, the Contractor shall ensure that pipe diameters and identification is correct in such cases. The whole test procedure shall then be gone through again commencing at the beginning. All rectification work shall be carried out at no extra cost to the Client.

During the tests any leakages shall be rectified or noted for future attention, although these tests are not intended to prove soundness.

k) 	Checking Flow Rates Delivery Pressures:

1) 	Test Requirements

Two separate tests, with quite different purposes are involved. Test 1 is to ensure that each terminal unit is capable of providing the flaw and pressure for which it is designed. Test 2 is to ensure that the whole installation is capable of providing the flow for which the installation is designed, while at the rate of flow the pressure at the terminal unit should be not less than the design pressure.

Both tests shall be carried out using Test Units described in Clause (110.10) Item 3) and 4).

2) 	Test Gasses and Pressures:

The actual working gases shall not be for these tests. The pressure in the distribution pipework after the reducing valves for these tests shall be as follows:

For manifold systems or oxygen from plant use medical quality air at (4.14) bars (60 p.s.i) gauge +/- 0.14 bar (2 p.s.i)

For compressed airplant use the plant to provide air at 7.2 bars (105 p.s.i.) gauge +/- 0.17 bar (2.5 p.s.i.).

For vacuum use the plant to provide 400 mm. Hg gauge at the back of the terminal units.

The supply of air or vacuum shall not be cut off during the tests.

3) 	Test 1 Test of Flow Rate at Each Terminal Unit:

One test unit, of appropriate rating with pressure gauge attached, shall be connected into each terminal unit in turn and the flows shall not be less than that given in the following Table:

Oxygen				:		40	litres/min

Nitrous Oxide			:		15	litres/min.

Surgical Air			:		350	litres/min.

Medical Air 4 Bar		:		50	litres.min.

While this test is being conducted each terminal unit shall be superficially examined for any mechanical defect. No leakage

should occur with the probe inserted or removed. It must not be possible to insert any probe other than that for which the terminal unit is designed.

4) 	Test 2 Total Flow Rate and Delivery Pressure Test:

The appropriatetotal number and size of test units without pressure gauges should be connected simultaneously into representative terminal units distributed over the whole installation.

The Contractor should then check the terminal unit pressure at vulnerable or representative points as directed. This should be done by substituting for the ordinary test unit one incorporating a pressure gauge. The pressure indicated shall not be less than that given in the following table.

All terminal units and special fittings shall be tested as above, to the satisfaction of the Engineer.

Note:

If, during the tests, the test gauge pressure is not below the figures given, the required conditions will normally be met in practice, because of the reservoir capacity of the pipeline itself.

Maximum

Gauge			Acceptable

Flow Rate		Pressure		Pressure on

Service		Litres/min. at Back of				Gauge of Remarks

at S.T.P.		Terminal		Test Unit

Unit

--------------------------------------

bar	p.s.i		 bar p.s.i

-----------------------------------------------------------------------------

Medical Gases		40/20/15	3.9	57		3.9	56.5

Medical Compressed	250		6.9	6.6		95 (See note below)

Air

Medical Compressed	65/50		6.9	100		6.8	99

Air

Medical Compressed	65/50		3.9	57		3.9	56

Air

Medical Vacuum	40/20 		40 mm. Hg		300mm. Hg mm.

l) 	Checking Operation of manifold Changeover Valves:

The operation of manifold changeover valves shall be checked using a small cylinder of medical cylinder of medical air or the "working" gas, connected to each side of the manifold and discharging to carefully sited position while the operation of the changeover valve and pressure gauges is checked both sides of the manifold.

m) 	Plant Operation Tests:

1) 	Check on Oxygen/Air Units for correctness and/or efficiency of:

i) 	Compressor and module operation

ii) 	Safety valves and pressure controls

iii) 	Sequencing

iv) 	Warning devices

v) 	Changeover to standby manifold automatically

2) 	On manifold installations check that:

i) 	The manifold changeover valve automatically operates when the pressure falls below the equivalent of empty cylinders on either side.

ii) 	Both standby regulators operate correctly in the event of changeover valve failure.

iii) 	The gauges are marked for the gas which is being controlled by the manifold.

iv) 	All heaters (where fitted) operate correctly.

3) 	Check Vacuum Plant for correctness and/or efficiency as follow

i)	Rotation of motors

ii)	Current at full load

iii) 	Vibration and noise not excessive within specified limits

iv) 	All automatic devices

n) 	Signaling System Tests:

The while of the alarm signalling system shall be tested by simulating all the fault conditions appropriate to the system installed.

Check that all items have been correctly installed.

Check that visual and audible alarms operate correctly at the required positions and can be seen and heard distinctly.

Check that muting switches operate correctly.

Check lamp test system and " system alarm" circuits .

Check that indicating panels and switches are marked up correctly.

Repeat signals to the BMS system shall be checked for correct indication.

o) 	Purging Medical Gas System with working gas :

Upon completion of all tests using air, Medical Gas System shall be charged with "working" gas.

This may be arranged to be done a short while before hand over so that gases are left standing in system which may not be used for some time.

The initial full complement of cylinders for each gas as specified previously shall be connected to the manifolds.

The Contractor shall demonstrate during this stage of commissioning that all tail pipe connections are correct and that the support racks are suitable.

The operation of nonreturn valves on the manifold at the tail pipe connection and flow of gas from each position shall be proved isolating all cylinders but one and checking that gas pressure is maintained by this cylinder. The test shall be repeated for each cylinder in turn.

The systems shall then be purged with the gases and the discharge temporarily piped to a suitable safe position outdoors via flexible lengths of hose with probes to operate the terminal units.

The working gas may be introduced either from the manifold or plant supply, or through the three valve arrangement from cylinders if these valves have been provided.

p) 	Checking of gases and air at terminal units:

The Contractor shall demonstrate to the satisfaction of the Engineer the acceptability of the gases or air delivered from the terminal units or special fittings.

1) 	For medical gases this shall identify that the correct gas is being delivered to the correct terminal positions.

2) 	For medical air supplied from cylinders this shall identify that air is being delivered to the correct terminal positions.

3) 	For medical air supplied by compressor plant this shall identify that air is being delivered to the correct terminal positions and prove that the air is dry to requirements of paragraph 110.03 Sub-Clause f), Item (10) and pure to the requirements of 110.03 Sub-Clause f), Item (12). The Contractor shall provide all apparatus or instruments to carry out the above checks.

q) 	 Witnessing of tests and hand-over meeting:

All the foregoing tests shall be satisfactorily carried out by the Contractor and witnessed by the Engineer before the systems are demonstrated by the Owner at the handover meeting. When each system has been approved and accepted by the Owner, Schedule 9 should be jointly signed by the Engineer and the Owner, and retained as a permanent record.

r) 	Pressure variation during tests:

It should be noted that variations in temperature will have an effect on the pressure during tests, in accordance with the gas laws.

This should be taken into account when taking pressure readings, for example a pressure drop due to a temperature drop and not a leak and conversely a leak may not be apparent if the temperature has increased.

# END OF SECTION