## COVER
BILL OF QUANTITIES ( BoQ)
FOR
IOM MHAC FACILITY AT NO. 1 SASEGBON STREET, IKEJA GRA- LAGOS.
(MECHANICAL & ELCTRICAL WORKS)
CLIENT
IOM, NIGERIA
SEPTEMBER, 2023.

## Description of Prelims
GENERAL REQUIREMENTS and TECHNICAL SPECIFICATIONS
1.0 GENERAL
1.1 Scope
The purpose of the Preliminaries and General Requirements is to identify what items are needed for the mobilisation of the contractor from the date of Site Possession and what items are required to be implemented throughout the contract until the issuance of Substantial Completion Certificate
1.2 Reference to other Sections
Throughout the Specifications and Bills of Quantities, references are occasionally made to other sections. All such references are intended solely for the convenience of those using the documents, and the absence of a reference in no manner excludes the application of every other section in the Specifications which may, in the opinion of the Engineer, have any bearing upon the point in question, the intention being that the Contract Documents shall be read and applied as a whole.
1.3 General Scope of works
The Contractor shall furnish, except as otherwise expressly provided in the Contract, all materials, equipment and labour to complete the works in accordance with the terms of this Contract, Conditions of Contract, General Requirements, Specifications, Bill of Quantities and Drawings.
Without in any way limiting the scope of the foregoing, the works shall include all necessary clearing and grubbing; excavation; backfilling; ditching; sheeting; shoring, bracing and supporting; preparing and maintaining access roads; surveying and field investigations; supplying, transporting and installing necessary material and equipment; testing and supplying and placing all construction materials necessary for the works.
2.0 CONTRACTOR TO INVESTIGATE
No plea for ignorance of conditions that exist or that may thereafter exist or of conditions or difficulties that may be encountered in the execution of the works as a result of non-cognizance of local conditions, laws and regulations and/or failure to make the necessary examinations and investigations shall be accepted as an excuse for any failure or omission on the part of the Contractor to fulfil his contractual obligations.
The Contractor shall also make all the investigations necessary to thoroughly inform himself regarding all facilities for access to the site, characteristics of the site. Conditions affecting supply of labour, water, electricity for temporary lighting and power as well as any local regulations and restrictions and generally any matters which may affect his prices as no claim on the ground of lack of knowledge in any respect will be entertained.
3.0 SITE CONDITIONS
3.1 General
The contractor should be aware of any restrictions that may affect the site and should therefore factor in his cost such restrictions.
3.2 Protection and diversion of existing services
The contractor shall be responsible for notifying the service authorities and the Engineer of his intention to expose the services and where so required by the service authority shall not commence operations until the service authority is represented on the Site.
The Contractor shall excavate, protect until backfill and backfill in a manner so as not to damage the services. As soon as a service is encountered in the excavation whether previously located or discovered during the course of excavation for the Permanent Works the Contractor shall forthwith call the attention of the Engineer and the appropriate service authority thereto. The Contractor shall be responsible for maintaining all such services including natural and artificial watercourses encountered by him in the construction of the Works and shall make good any damage caused directly or indirectly by his activities.
3.3 Traffic Arrangements
The Contractor shall seek information on and comply with all requirements and recommendations regarding traffic safety measures. The Contractor shall arrange alternative temporary access with the owners or tenants of properties and shall submit details of such agreed temporary access arrangements where necessary.
3.4 Disposal of surplus materials
Surplus material and debris arising from the Works shall be dumped in agreed disposal sites at the expenses of the Contractor. The Contractor shall indemnify the Employer against any claims arising from unauthorized disposal of such materials.
3.5 Water Control
Without prejudice to other stipulations in the Contract, all constraints related to the presence of or risks caused by water, all additional work which may prove necessary on this account, all damage caused by water, all pumping in all structures not mentioned in the Contract which the Contractor may find he has to build for water control purposes shall be at the expense of the Contractor.
Before any works are begun, the Contractor shall submit to the Engineer's approval the methods and arrangements he proposes to apply in order to protect the Works, unless these are imposed by the designs incorporated in the Contract. Such Engineer’s approval shall not relieve the Contractor of his obligations and responsibilities under this Section.
4.0 REGULATIONS
The Contractor shall comply with all provisions of the rules, regulations and orders of local authorities where the site is located. The Contractor shall co-operate with the relevant authorities in promptly furnishing any information that may be required by such authorities. It shall be the obligation of the Contractor to keep himself informed of these rules, regulations and orders.
5.0 STANDARDS, CODES AND ABBREVIATIONS
General Standard specifications and codes of the following listed authorities wherever cited herein are referred to by use of the abbreviations shown below. All materials and workmanship shall comply with requirements of these standards.
E.N | European Standards
CYS | Cyprus Standards
B.S. | British Standards
T.S. | Turkish Standards
D.I.N | German Standards [Deutsches Institute fur Normung]
A.S.T.M. | American Society for Testing of Materials
I.S.O | International Standard Organization
Where reference is made to a Specifications by one of the above mentioned it is understood that the latest revision thereof shall apply.
6.0 COST ITEMS
The contract shall implement the following preliminaries and general requirements and shall price these accordingly in the bills of quantities.
Description | Implemented by
Contractor’s site facilities | At mobilisation
Temporary power and light | At mobilisation
Temporary water | At mobilisation
Site delimiting barriers (upon instructions from Engineer) | At mobilisation
Health & Safety plan and implementation | At mobilisation
Setting Out (Upon instructions from Engineer | Before commencement
The above items are listed in the bills of quantities as Preliminaries and General Items and the contractor shall price these accordingly considering all costs. Breakdown of the prices may be required by the Engineer for approval.
MOBILISATION
7.0 TEMPORARY FACILITIES
Starting from the date of site possession the Contractor shall implement and shall bear all the cost of installation of all temporary facilities within the plot of the works, their maintenance and upkeep until the time to remove these facilities from the site.
Contractor shall establish his temporary facilities in the plot in such a way so as not to disrupt his works. Once these are removed, locations where these were situated will be restored to its original shape and form. Thus, the contractor has to record the condition before installing the site facilities.
7.1 Contractor Site Facilities
The Contractor shall provide and maintain on the site prefabricated, modular and portable and located within the delimited area of the site and within the plot:
- ONE office; at least 5m2
- Resting/eating room for the site personnel; at least 10m2
- Sanitary facilities (toilets and washbasins) – at least 1 no
- Additional covered areas can be installed for storage of materials.
The Contractor shall submit layout of the distribution of the site facilities, photos/sketches of the types and dimensions to the approval of the Engineer.
Contractor’s site facilities must be kept clean and maintained properly. All consumables associated with above facilities shall be borne by the Contractor. These facilities are not for sleeping during non-working hours.
Items that are going to be used for the works such as scaffolds, machinery/equipment, materials, etc. are not eligible to be included under the mobilisation items.
The site facilities shall be furnished and equipped as the contractor deems fit. The workbook must be prepared and made ready.
After 30 days of the substantial completion being issued, the contractor will remove all from the site and take all the items.
If there is a need to install site facilities outside the plot of the project, the contractor shall investigate and obtain all permissions and consents from the owner and/or caretaker and/or relevant authorities. The same conditions as above will apply.
8.0 TEMPORARY POWER AND LIGHT
The Contractor shall arrange to get temporary power to the site and bear all costs associated with these. The Contractor shall furnish all wiring, lamps, switches, fuses, receptacles, etc., as may be required for his work. Temporary power and light circuits shall be thoroughly insulated and waterproof. The temporary power and light system shall be subject to the inspection and approval of the electricity authority.
All charges for connection and usages will be borne by the contractor.
After 30 days of the substantial completion being issued, the contractor will disconnect all the temporary connections.
9.0 TEMPORARY WATER
The Contractor shall arrange to get temporary mains water to the site and bear all costs of plumbing, piping, pumping, etc. and other costs associated with these. If there is no mains connection to the site the contractor shall cart in potable water and store in polyethylene tanks. This water shall be sued for the site activities. After 30 days of the substantial completion being issued, the contractor will disconnect all the temporary connections and/or remove the water setup.
10.0 TEMPORARY SITE DELIMITING BARRIERS
The Contractor shall install temporary site delimiting barriers if the site does not have existing perimeter walls and/or fences.
If the site is not delineated the Contractor shall obtain the services of a licensed topography firm to establish the plot boundaries.
These barriers will be premade in metal and shall be transported and installed on concrete pads. Height of the barriers will be 2m. Fabric material will cover the barriers, the colour of which will be instructed. Maintenance of the barriers and the fabric throughout and until the time to remove is the responsibility of the contractor and all costs associated with these shall be borne by the contractor.
After 30 days of the substantial completion being issued, the contractor will remove the temporary barriers and fabrics.
11.0 HEALTH & SAFETY
The Contractor shall implement the HS Plan prepared by the designated HS officer and elaborate on the health safety risk matrix submitted at the bidding stage.
The HS Officer shall supervise all aspects of health & safety on site and shall report every TWO WEEKS on any activity pertaining to health & safety. Report should be written in good English and should be proof-read before submission.
The HS Officer shall sign the report.
Upon approval of the report relevant payment shall be made against each report.
11.1 Health & safety requirements
The Contractor’s HS Officer shall prepare a Health and Safety Plan and shall include all matters related to construction site health and safety. Responsibility and liabilities lie with the HS Officer and the Contractor. The Contractor shall be responsible for the safety of all workmen and other persons entering the Works and shall, at his own expense (where not otherwise stated) take all measures necessary to ensure their safety. Provision of proper safety and emergency regulations include fire, gas (if any) and electric shock prevention, stretchers and first aid boxes, together with rescue facilities generally, for each place of working.
Notices written in relevant languages shall be erected at points likely to be used by the public and warning the public of the existence of the Works. These notices shall be in addition to any statutory requirements.
Personal protective equipment shall be available and used by the personnel including: safety helmet, eye protection, ear protection, hand protection, foot protection, harnesses and belts.
Provision and maintenance of suitable lighting to provide adequate illumination of the Works with appropriate spares and standby equipment.
Provision of good and safe access to any part of the Works.
11.2 First Aid
The Contractor shall provide and maintain at the site a completely equipped first-aid kit, as required by Health & Safety requirements, in a clean orderly condition, which shall be readily accessible at all times to all his employees and the Engineer & his staff. The Contractor shall designate at least two employees who are properly trained to be in charge of the first aid. At least one such employee shall be available to render first-aid at all times that work is being carried on.
First aid certificates of these employees must be provided to the Engineer.
In locations of rural settings and out of any town and especially in the hot/warm period (April – November) vials of serum against snake bites must be provided and maintained accordingly.
11.3 Prevention of noise
The Contractor shall take noise intensity readings as required by the Engineer and shall submit the results to the Engineer. The Contractor shall comply with measures required by the Engineer to keep noise and disturbance to the reasonable minimum. The hours of usage of any noisy machinery or plant for the above purpose shall be controlled by the Engineer or by his agent all in conformity with the relevant regulations currently in force.
11.4 Fire prevention
The Contractor shall make arrangements and provide sufficient number and type of fire-fighting equipment to the satisfaction of the Engineer. The Contractor shall remove all rubbish and surplus material of a flammable nature and take such other steps as the Engineer may require but this shall not relieve the Contractor of any of his obligations under the Contract.
PRELIMINARIES
12.0 SETTING OUT
12.1 Reference points, lines and levels
The Contractor shall carry out site surveys and will establish relevant Benchmarks and Reference Points at appropriate locations on the site of the works.
The Contractor shall be responsible for transferring the lines and levels from these points to all points of construction. The Contractor must set the line, levels and grade by means of surveyor's instruments or other approved means.
The setting out by the Contractor shall include, but shall not be limited to, the preparation of topographical maps including coordinates system and/or axis, the installation of centre line stakes, grade and offset stakes, sight rails and batter boards.
The Contractor shall be responsible for the true and proper setting out of the works and for the correctness of the position, levels, dimensions and alignment of all parts of the works and for the provision of all necessary instruments and labour in connection therewith. The checking of the setting out of any lines or levels by the Engineer shall not in any way release the Contractor from his responsibility for the correctness therefore. The Contractor shall carefully protect and preserve all Benchmarks, Reference Points and other items used in setting out the works. The Contractor shall prepare a Setting-Out Report and submit for the approval of the Engineer.
WORKS
13.0 WORK PROGRAMME
This work programme shall show clearly how the works shall be organized by section and the corresponding proposed progress on the main items, structures and sub-trades of the Contract. The Work program shall indicate the area of work, the plot number, the number of construction crews, plant and equipment to be employed, etc.
The Engineer may require the Contractor to revise his proposed schedule at any time, as provided for in the General Conditions. The Contractor is advised that he shall not be permitted to work haphazardly throughout the whole area of the Contract but shall be required to complete several items of one section insofar as possible, before permitting that working crew to start working in another work of the next section.
14.0 WORK TO CONFORM
All work shall conform during its progress and on its completion, truly to the lines, levels and grades shown on the Drawings and shall be built in a thoroughly substantial and workmanlike manner, in accordance with the Drawings and Specifications subject to such modifications and additions as may be deemed necessary by the Engineer during its execution and in no case shall any work in excess of the requirements of the Drawings and Specifications be paid for unless ordered in writing by the Engineer.
15.0 PROTECTION & REPAIR OF PROPERTY, STRUCTURES & UTILITIES
No responsibility shall be assumed by the Employer for the correctness or completeness of the Drawings with respect to existing utilities, pipes, catch basins, chambers or other objects either under-ground or on the surface and should plots of such be found incorrect or incomplete the Contractor shall have no claim on that account.
The Contractor shall, at his own cost and expense, and in a manner approved by the Engineer sustain in their places and protect from injury any conduits, cables, pipes, roadways, buildings and all other structures or property in the vicinity of his work, whether above ground or underground, or which appear within the excavations.
He shall, at all times, have sufficient quantities of timber and plank, chains, etc. on the site, and shall use the same as required for sheathing or sheet piling and bracing the sides, roofs and ends for excavations, and for sustaining or supporting any and all structures that are endangered.
When the construction is adjacent to or on residential property the excavation, disposal of the material, and backfill operations shall be performed in such a manner as to restore the properties to their original conditions as nearly as practicable as determined by the Engineer.
Any stones, trees, brush or other deleterious matter left by construction operations shall be removed by the Contractor by hauling to approve disposal areas or by means acceptable to the Engineer before final replacement of the soil. The Contractor shall carry on his operations in such sequence and in such manner as to minimize disturbance to the public and to interfere as little as possible with the operations of property users.
16.0 WORK PROTECTION
It shall be a requirement of this Contract that the Contractor erect protection around the Wreck as specified. Until the Wreck is protected fully the contractor shall not undertake any cutting, welding, grinding in the room of the Wreck.
The Contractor will remove from the site of the works any machine or tool unsuitable for the works specified, or of insufficient efficiency and will replace them by approved equipment without being entitled to any extra payment for transport, loss of working hours, or any other damage or loss caused by replacing the equipment.
17.0 PROTECTION, REPAIR AND MAINTENANCE OF CONSTRUCTION
All newly constructed work shall be carefully protected from injury in any way. No wheeling or walking or placing of heavy loads on it shall be allowed and any portion damaged shall be reconstructed by the Contractor at his own expense. Should any of the floors or other parts of the structures become heave, cracked or otherwise damaged all such damaged portions of the work shall be completely repaired and made good by the Contractor at his own expense and to the approval of the Engineer. If in the final inspection of the works, any defects, faults or omissions are found, the Contractor shall carry out repairs and/or replacement by proper materials and workmanship without any cost to the Employer.
18.0 DRAWINGS
The works are to be built of the materials and to the sizes, dimensions and grades as called for in the Specifications and Contract Drawings and such other Drawings as may be added from time to time by the Engineer during the progress of the work. The only drawings referred to in these Specifications are the drawings provided by the Employer to the Contractor.
Additional working drawings showing details in accordance with which the work is to be constructed will be furnished from time to time by the Contractor and shall then become a part thereof after approval of the Engineer. The Contractor shall be governed by figured dimensions, as given on the Drawings. Where required dimensions are not shown in figures, the Contractor shall obtain such portion of the work to which they refer.
19.0 ELEMENTS FOR RE-USE
The dismantling and/or removal of the existing construction and/or structures elements shall be done with extreme care to avoid destruction/damage and in order to appreciate its exact condition. Existing element such as wood, timber, iron, I-beam, stone, adobe, tiles, marble and/or similar building element can be proposed for re-use if in good condition. If it is established by the Contractor and approved by the Engineer that the element has lost its technical, structural and load-bearing characteristics it shall be removed from the site and shall not be proposed re-use for any rehabilitation works.
Any element acceptable for re-use proposed and/or recommended by the Contractor and/or Engineer, shall be recorded, measured and properly stored in accordance with its nature and corresponding storage requirement. All elements for re-use shall be reconditioned, cleaned, protected, and painted as per specifications before installation.
The works for checking, investigating, and storing buildings elements for re-use are included in the present scope of works. The Contractor will be responsible for damages that may occur to any existing building element during dismantling and/or removal; any damages to building elements will be repaired and/or the element replaced at the Contractor's expenses.
20.0 RESPONSIBILITY FOR MATERIAL
The contractor has to present the list of materials, which will be used during the construction, while submitting a proposal. All information; test result, documents, etc... related to materials will be submitted with the proposal, The Contractor shall be responsible for all material furnished by him and shall replace at his own expense all such material found defective in manufacture or damaged in handling after delivery by the manufacturer. This shall include the furnishing of all material and labour required for the replacement of installed material discovered defective prior to the end of the guarantee period.
21.0 MATERIALS AND WORKMANSHIP
All materials furnished under this Contract shall be new, of best quality, first-class in every respect and purchased from a known and approved manufacturer/supplier. The material shall be installed, constructed and finished in a workmanlike manner. Materials shall be suitable for the service intended and selected and fabricated in accordance with the best Engineering practice. Unless otherwise specified herein, all materials shall conform to the appropriate standard specification requirements.
22.0 SUBMISSION OF SAMPLES AND DATA
In addition to any specific provision in the Contract for the sampling and testing of materials, the Contractor shall submit to the Engineer, as he may require, samples, drawings, catalogues, diagrams and other descriptive data for all mechanical, electrical, structural, architectural and such other materials and equipment as may be designated by the Engineer and which the Contractor proposed to incorporate in the Works. Such samples, if approved, will be retained by the Engineer.
No materials or goods, of which samples have been submitted, shall be used in the Works, unless and until such samples have been approved in writing by the Engineer. The Engineer may reject any materials and goods which in his opinion, are inferior to the samples thereof previously approved and the Contractor shall promptly remove such materials and goods from the Site, at his own expense.
23.0 TESTS
23.1 General
The Contractor shall afford the Engineer all facilities, assistance, labour and appliances necessary for the convenient supervision of testing, weighing, or analysis of all materials or goods. The Contractor shall provide and execute the tests of any materials or goods or as the Engineer may require, and shall arrange for tests to be undertaken at independent laboratory/ies. Should the Engineer not inspect any materials or goods at the place of manufacture, the Contractor shall obtain Certificates of Test from the suppliers of such materials and shall submit to the Engineer.
23.2 Manufacturer's Certificate Of Compliance
In the case of standard labelled stock products of standard manufacture which have a record of satisfactory performance in similar work over a period of not less than 2 years, the Engineer may accept a statement from the Manufacturer attested by a certificate that the product conforms to the applicable Specifications. In the case of materials for which such practice is usual, the Engineer may accept the manufacturer's certified mill and laboratory certificate.
23.3 Cost of Tests
The costs of all tests made by the Contractor and/or at the Engineer's instructions on all materials as requested in the Contract and the cost of tests on finished work as specified in the contract shall be borne by the Contractor.
24.3 Acceptance of Materials
The approval by the Engineer of any material or equipment shall in no way relieve the Contractor of any of his responsibilities for meeting all of the requirements of the Specifications and shall not prevent subsequent rejection if such material or equipment is later found to be defective or not conforming to the Specifications.
24.0 "OR EQUAL" CLAUSE
Whenever a material or article required is specified or shown on the drawings by using the name of the propriety product or of a particular manufacturer or vendor, any material or article which will perform adequately the duties imposed by the general design will be considered equal and satisfactory provided the material or article so proposed is of equal substance and function in the Engineer's opinion. It shall not be purchased or installed without his written approval.
25.0 PROTECTION OF FINISHES
The Contractor shall take every care to prevent damage to the works and shall ensure that adequate protection is given to all works from the activities of following trades and any third party.
Vulnerable parts of the works particularly liable to damage shall be protected as may be reasonably required by the Engineer and shall be deemed to be insured against damage in accordance with the conditions of contract.
26.0 CLEANING
The debris accumulated on the working platform and on the roofs shall be removed through dustproof canals, which shall be constructed by the Contractor. The rubbles and other debris shall never be thrown down from the roof and from the working platform. The Contractor shall be sensitive on this subject and shall do the clearing frequently. The Contractor, before leaving the site after the completion of the works, shall clear the site. This clearing shall be done before leaving the storage area also

## Summary
#REF!
For
GENERAL SUMMARY
|  | NGN |  | USD
1 | Mechanical Installations | 0 |  | 0
2 | Electrical Installations | 0 |  | 0
3 | Bill No. 4 - Provisional Sums (Builder's Works) | 0 |  | 0
| NET BUILDING COST | 0 | 0 | 0
| CONTINGENCY (3%) | 0 | 0 | 0
|  | 0 | 0 | 0
| Estimated Construction Cost (N) | 0 | 0 | 0

## Mechnicals BoQ
ITEM | ELEMENT NO. 1: PRELIMINARIES | QTY | UNIT |  | FIXED | TOTAL |  | FIXED | TOTAL
| DESCRIPTION |  |  |  | RATE (N) | COST (N) |  | RATE ($) | RATE ($)
769.1
1 | Interpretation Procedures, Mobilisation and Site Organisation | Sum | [6 empty] | 0
2 | Commissioning and Testing of entire installation and Provision of certificates | Sum | [6 empty] | 0
| TO SUMMARY |  |  |  |  | 0 |  |  | 0
ITEM | BILL NO. 1- AIR-CONDITIONING EQUIPMENT | QTY | UNIT | BASIC | FIXED | TOTAL | BASIC | FIXED | TOTAL
| DESCRIPTION |  |  | RATE (N) | RATE (N) | COST (N) | RATE ($) | RATE ($) | RATE ($)
1 | SPLIT AIR-CONDITIONING UNITS
A | High wall mounted mini-split air-conditioning unit, indoor and
outdoor c/w installation, mounting & fixing accessories
including refrigerant & condensate pipework, cable
and remote controller
i | Symbol: WSU1 | 41 | Nos | 270000 |  |  | #REF! | 0 | 0
Make: Daikin, LG, Panasonic or an approved equal
Model No.: FTNV25B; RNV25B
Refrigerant: R410A
Capacity: 2.64kW
ii | Symbol: WSU2 | 29 | Nos | 330000 |  |  | #REF! | 0 | 0
Make: Daikin, LG, Panasonic or an approved equal
Model No.: FTNV35B; RNV35B
Refrigerant: R410A
Capacity: 3.52kW
iii | Symbol: WSU3 | 23 | Nos | 420000 |  |  | #REF! | 0 | 0
Make: Daikin, LG, Panasonic or an approved equal
Model No.: FTNV50B; RNV50B
Refrigerant: R410A
Capacity: 5.28kW
iv | Symbol: WSU4 | 2 | Nos | 500000 |  |  | #REF! | 0 | 0
Make: Daikin, LG, Panasonic or an approved equal
Model No.: FTNV60B; RNV60B
Refrigerant: R410A
Capacity: 6.45kW
B | Ceiling mounted cassette air-conditioning unit, indoor and
outdoor c/w installation, mounting & fixing accessories
including refrigerant & condensate pipework, cable
and remote controller
i | Symbol: CSU2 | 13 | Nos | 550000 |  |  | #REF! | 0 | 0
Make: Daikin, LG, Panasonic or an approved equal
Model No.: FCRN50EXV; RN50CGXV9/Y
Refrigerant: R410A
Capacity: 5.36kW
C | Floor standing air-conditioning unit, indoor and
outdoor c/w installation, mounting & fixing accessories
including refrigerant & condensate pipework, cable
and remote controller
i | Symbol: FSU | 11 | Nos | 2000000 |  |  | #REF! | 0 | 0
Make: Daikin, LG, Panasonic or an approved equal
Model No.: FVRN140AXV; RR140DGX/Y
Refrigerant: R410A
Capacity: 16.12kW
1./1 | To collection | 0 TOTAL: 0; 0 TOTAL: 0
ITEM | BILL NO. 1(CONTD)- AIR-CONDITIONING EQUIPMENT | QTY | UNIT | BASIC | FIXED | TOTAL | BASIC | FIXED | TOTAL
| DESCRIPTION |  |  | RATE (N) | RATE (N) | COST (N) | RATE ($) | RATE ($) | RATE ($)
0
2 | AIR HANDLING UNITS + OUTDOOR UNITS
Make: LG, Panasonic, Daikin or approved equal
i | AHU -1 | 1 | Nos | 13100000 |  |  | #REF! | 0 | 0
| Recirculating AHU DX Coil | FIXED: 0; TOTAL: 0
| Total cooling capacity - 22kW | FIXED: 0; TOTAL: 0
| Sensible load - 16.3kW | FIXED: 0; TOTAL: 0
| AHU Shall be supplied complete with Inlet box, Panel filter, HEPA | FIXED: 0; TOTAL: 0
| filter, Fan section cooling coil, damper, AHU Comm. Kit and all | FIXED: 0; TOTAL: 0
| necessary accessories for a complete installation | FIXED: 0; TOTAL: 0
[8 empty] | 0 | 0
ii | Outdoor unit | 1 | Nos | 13100000 |  |  | #REF! | 0 | 0
Make: LG, Panasonic, Daikin or approved equal
Cooling Capacity: 22.4KW
1./2 | To collection | TOTAL: 0
COLLECTION
| 1./1 | TOTAL: 0
| 1./2 | TOTAL: 0
| TO SUMMARY | TOTAL: 0; TOTAL: 0
ITEM | BILL NO. 2 - VENTILATION EQUIPMENT | QTY | UNIT | BASIC | FIXED | TOTAL | BASIC | FIXED | TOTAL
| DESCRIPTION |  |  | RATE (N) | RATE (N) | COST (N) | RATE ($) | RATE ($) | RATE ($)
1 | Wall mounted extractor fan | 20 | Nos | 55000 |  |  | #REF! | 0 | 0
Symbol: WEF1
Model; Xpelair GX6
Capacity:- 266m³/hr
2 | Symbol: IEF1 | 2 | Nos | 160000 |  |  | #REF! | 0 | 0
Model; Xpelair XID125
Capacity:- 96l/s
Aceesories: mounting kits and fan controller
3 | Symbol: IEF2 | 1 | Nos | 190000 |  |  | #REF! | 0 | 0
Model; Xpelair XID150
Capacity:- 113l/s
Aceesories: mounting kits and fan controller
4 | Symbol: IEF3 | 1 | Nos | 250000 |  |  | #REF! | 0 | 0
Model; Xpelair XID200
Capacity:- 190l/s
Aceesories: mounting kits and fan controller
| TO SUMMARY | TOTAL: 0; TOTAL: 0
ITEM | BILL NO. 3 - GRILLES & DIFFUSERS | QTY | UNIT | BASIC | FIXED | TOTAL | BASIC | FIXED | TOTAL
| DESCRIPTION |  |  | RATE (N) | RATE (N) | COST (N) | RATE ($) | RATE ($) | RATE ($)
1 | Extract grilles | 32 | Nos | 15000 |  |  | #REF! | 0 | 0
Symbol EG
Size: 200 x 200mm
2 | External louvres
Fixed blade external louvres c/w opposed blade damper, insect
screen, lower rain lip and fixing accessories
Make: Trox
Material: Extruded Aluminium
finish: polyester powder to Architects spec
i | Symbol: EL1 | 3 | Nos | 20000 |  |  | #REF! | 0 | 0
Size: 300x300
ii | Symbol: EL2 | 1 | Nos | 22500 |  |  | #REF! | 0 | 0
Size: 400x300
3 | Square Ceiling Supply Diffuser
Complete with OBD & plenum
Make - Trox
i | Symbol: SD | 5 | Nos | 37500 |  |  | #REF! | 0 | 0
Flow rate -
Neck size - 300 x 300mm
4 | Return grille - Non vision | 2 | Nos | 75000 |  |  | #REF! | 0 | 0
Complete with OBD & plenum
Make - Trox
Symbol: RG
Size - 900 x 600mm
5 | Access Panel | 13 | Nos | 40000 |  |  | #REF! | 0 | 0
Size: 600 x 600mm
6 | Door Transfer Grille
Make :- Trox
Finish:-polyester powder coated to Archictect's specification.
i | Non vision door transfer grille | 10 | Nos | 30000 |  |  | #REF! | 0 | 0
Symbol:- DTG
Size: 500 x 250mm
| TO SUMMARY | TOTAL: 0; TOTAL: 0
ITEM | BILL NO. 4 - REFRIGERANT PIPEWORK | QTY | UNIT | BASIC | FIXED | TOTAL | BASIC | FIXED | TOTAL
| DESCRIPTION |  |  | RATE (N) | RATE (N) | COST (N) | RATE ($) | RATE ($) | RATE ($)
1 | AIR-CONDITIONING PIPING INSTALLATIONS
A | AHU SYSTEM
Supply and install insulated refrigerant pipework as stated below
for the AHU system
Refrigeration pipework shall be Maksal RC & RL tube (R410
compatible) - Straight pipes
Insulaltion shall be Armaflex AC class O 25mm thickness
Insulated refrigerant pipework shall be wrapped with off white vinyl tape
1 | Copper pipes
|  |  |  | 0 |  | 0 |  | 0
i | B - 9.52mm | 8 | " | 6360 |  |  | #REF! | 0 | 0
|  |  |  | 0 |  |  |  | 0
|  |  |  | 0 |  |  |  | 0
ii | E - 19.05mm | 8 | " | 14300 |  |  | #REF! | 0 | 0
|  |  |  | 0 |  |  |  | 0
0
iii | Allow for all fittings and piping accessories necessary | QTY: 1; UNIT: Lot; FIXED: 0; TOTAL: 0
| for a complete installation | FIXED: 0
0
0
B | SPLIT UNITS | FIXED: 0
| Refrigerant pipes c/w accessories: | FIXED: 0
| Supply, install, test and charge the following copper pipe | FIXED: 0
| refrigerant lines for the split units with all necessary fittings and | FIXED: 0
| materials as specified. | FIXED: 0
| MAKE: MAKSAL | FIXED: 0
i | 6.35mm internal diameter original copper refrigerant pipe | 1050 | m | 3000 |  |  | #REF! | 0 | 0
0
ii | 9.52mm internal diameter original copper refrigerant pipe | 670 | " | 4300 |  |  | #REF! | 0 | 0
0
iii | 12.70mm internal diameter original copper refrigerant pipe | 520 | " | 6000 |  |  | #REF! | 0 | 0
0
iv | 19.05mm internal diameter original copper refrigerant pipe | 138 | " | 10000 |  |  | #REF! | 0 | 0
0
v | 4mmsq, 3-core flexible cable for interconnection | 1304 | " | 3000 |  |  | #REF! | 0 | 0
0
vi | 6mmsq, 5-core flexible cable for interconnection | 138 | " | 4500 |  |  | #REF! | 0 | 0
4./1 | To Collection | TOTAL: 0; TOTAL: 0
ITEM | BILL NO. 4 (CONTD) - REFRIGERANT PIPEWORK | QTY | UNIT | BASIC | FIXED | TOTAL | BASIC | FIXED | TOTAL
| DESCRIPTION |  |  | RATE (N) | RATE (N) | COST (N) | RATE ($) | RATE ($) | RATE ($)
vii | 75mm corrugated upvc sleeves | 1442 | Nos | 2000 |  |  | #REF! | 0 | 0
0
viii | 20mm internal diameter amarflex insulation for refrigerant pipes- | 2884 | m | 1000 |  |  | #REF! | 0 | 0
| Class O, 10mm thickness | FIXED: 0
0
ix | 32mm internal diameter amarflex insulation for condensate pipes- | 1300 | " | 850 |  |  | #REF! | 0 | 0
| Class O, 10mm thickness | FIXED: 0
0
x | Installation material such as insulation tapes, Tangit gum, Plugs | QTY: 1; UNIT: Lot; FIXED: 0; TOTAL: 0
| and clips etc. | FIXED: 0; TOTAL: 0
[8 empty] | 0 | 0
xi | Allow for refrigerant gas | QTY: 1; UNIT: Lot; FIXED: 0; TOTAL: 0
0
2 | CONDENSATE DRAIN PIPES & FITTINGS | FIXED: 0
| (Pipework shall be rigid uPVC BS EN 1453) | FIXED: 0
a | Pipes | FIXED: 0
i | 32mm | 1300 | Nos | 600 |  |  | #REF! | 0 | 0
0
a | 90° Bends | FIXED: 0
i | 32mm | 400 | " | 250 |  |  | #REF! | 0 | 0
0
b | 135° Bends | FIXED: 0
i | 32mm | 200 | " | 250 |  |  | #REF! | 0 | 0
0
iii | Tees | FIXED: 0
| 32 x 32 x 32mm | 150 | " | 300 |  |  | #REF! | 0 | 0
4./2 | To Collection | TOTAL: 0
COLLECTION
| 4./1 | TOTAL: 0
| 4./2 | TOTAL: 0
| TO SUMMARY | TOTAL: 0; TOTAL: 0
ITEM | BILL NO. 5 - DUCTWORK | QTY | UNIT | BASIC | FIXED | TOTAL | BASIC | FIXED | TOTAL
| DESCRIPTION |  |  | RATE (N) | RATE (N) | COST (N) | RATE ($) | RATE ($) | RATE ($)
1 | Insulated galvanized sheet metal ductwork | 10 | sq.m | 20000 |  |  | #REF! | 0 | 0
| i. Sheetmetal guage and fabication of ducts shall be as | BASIC: 0; FIXED: 0
| specified by HVCA DW144 for different cross sectional area | BASIC: 0; FIXED: 0
| ii. Duct withinin the Auditorium shall be circular and exposed | BASIC: 0; FIXED: 0
| iii. Insulation shall be Kimmco 25mm thickness | BASIC: 0; FIXED: 0
0
2 | Non Insulated galvanized sheet metal ductwork | 50 | sq.m | 14000 |  |  | #REF! | 0 | 0
| i. Sheetmetal guage and fabication of ducts shall be as | BASIC: 0; FIXED: 0
| specified by HVCA DW144 for different cross sectional area | BASIC: 0; FIXED: 0
0
3 | Insulated flexible duct 100mm dia |  | m | 4000 |  |  | #REF! | 0 | 0
|  |  |  | 0 |  |  |  | 0
4 | Acoustic lining | 2 | sq.m | 2500 |  |  | #REF! | 0 | 0
0
5 | Allow for flexible connectons to grilles | QTY: 1; UNIT: Lot; TOTAL: 0
0
6 | Allow for flexible connectons to equipment | QTY: 1; UNIT: Lot; TOTAL: 0
0
7 | Allow for brackets, hangers, dampers, saddle & supports | QTY: sum; TOTAL: 0
| TO SUMMARY | TOTAL: 0; TOTAL: 0
ITEM | BILL NO. 6 - MISCELLANEOUS ITEMS | QTY | UNIT | BASIC | FIXED | TOTAL | BASIC | FIXED | TOTAL
| DESCRIPTION |  |  | RATE (N) | RATE (N) | COST (N) | RATE ($) | RATE ($) | RATE ($)
1 | Allow for refrigerant gas | QTY: Lot; TOTAL: 0
0
2 | Allow for condensate pipework (Insulated) | QTY: Lot; TOTAL: 0
0
3 | Allow for cable tray/ladder for refrigerant pipework (exposed | QTY: Lot; TOTAL: 0
| and in ceiling void | TOTAL: 0
0
4 | Allow for communication/control cabling | QTY: Lot; TOTAL: 0
0
6 | Allow for Nitrogen gas, welding gas etc | QTY: Lot; BASIC: 0; FIXED: 0; TOTAL: 0
| TO SUMMARY | TOTAL: 0; TOTAL: 0
SUMMARY
| Preliminaries | TOTAL: 0; TOTAL: 0
| Bill no. 1: - Air-conditioning Equipment installation | TOTAL: 0
| Bill No 2: Ventilation equipment | TOTAL: 0
| Bill No 3: Grilles & Diffusers | TOTAL: 0
| Bill No 4: Refrigerant pipework | TOTAL: 0
| Bill No 5: Ductwork | TOTAL: 0
| Bill No 6: Miscellaneous items | TOTAL: 0
| SUB-TOTAL | TOTAL: 0; TOTAL: 0

## BoQ- Electricals
ITEM | ELEMENT No. 1 - ELECTRICAL SERVICES: PRELIMINARIES
| DESCRIPTION | QTY | UNIT |  | TOTAL |  | TOTAL
|  |  |  | RATE (N) | COST (N) | RATE ($) | AMOUNT ($)
A | Interpretation Procedures, Mobilization and Site Organization | Sum |  |  |  |  | 0
B | Commissioning and Testing of entire installation and provision of Test Certificates | Sum |  |  |  |  | 0
0
Pg 1/1 | TO SUMMARY |  |  |  | 0 |  | 0
ITEM | ELEMENT No. 2 - ELECTRICAL SERVICES: MAINS SUPPLY & DISTRIBUTION AND EARTHING
| DESCRIPTION | QTY | UNIT |  | TOTAL |  | TOTAL
|  |  |  | RATE (N) | COST (N) | RATE ($) | AMOUNT ($)
Supply, Install and connect the following:
4 | ATS/GENERATORS' PANEL
Free standing 600V, 1600A rated busbars, LV Panel
comprising 2 MAIN SECTIONS
A | Generators' panel.
Comprising:
INCOMER SECTION
3No. 1000A 4P motorised MCCB
Generators' synchronisation and load sharing controllers
BUS BARS
2000A 4P
MAIN OUTGOING SECTION
1No. 2000A 4P motorised ACB (may or may not be required)
complete with the following:
I | Mains sensing unit with overload protection
ii | Genarators' synchronisation and load sharing controllers
iii | Generator engine monitoring and control system.
iv | Generator selector switch
v | Electrical Interlock system with manual override facility
vi | Multimeters
B | ATS PANEL
2000A 4p ACB Automatic Transfer switch Soft Load Transfer with
2 incomer & outgoing features complete Voltage, Frequency,
Time Delay settings, Indication & Controls and remote signalling
to remote auto-startup generators with the following
i | Mains sensing unit from VT in MV panel with overload protection
C | Provide outdoor type wall mounted lamps indication of PHCN
| supply availability including wiring | 1 | No |  | 0 | 0 | 0
Pg 2/1 | To Collection |  |  |  | 0 |  | 0
ITEM | ELEMENT No. 2 - ELECTRICAL SERVICES: MAINS SUPPLY & DISTRIBUTION AND EARTHING
| DESCRIPTION | QTY | UNIT |  | TOTAL |  | TOTAL
|  |  |  | RATE (N) | COST (N) | RATE ($) | AMOUNT ($)
Supply, Install and connect the following:
5 | Power Transformer
1250KVA, 11000/415V, three phase, 50Hz, Dyn11 step-down, double-
wound, Hermetically sealed mineral oil immersed type transformer
suitable for outdoor installation. Unit shall be equipped with DGPT2
or Bucholtz and Winding Temperature protection devices.
Unit to be complete with tank with silica-gel breather.
Windings shall be of Cu/Cu.
complete with the following:
i | Factory type testing certificate
ii | Certified International short circuit type testing certificate e.g. ASTA
| e.g. Schneider, Siemens, ABB, Elco or approved equal | 1 | No |  | Excluded
6 | Main LV Panel
Free standing 600V, 2000A rated busbars, Main LV
Panel comprising
INCOMING:
1Nos, 2000A 4p fixed ACB
complete undervoltage, overcurrent, and earth leakage protection
phase sequence control with surge arresters and shunt trip facility
etc. Local LEDs fault indicators. Multi meters etc.
Outgoing ways
comprising of 1600A main load busbars,
All switches are complete with release operation coils
- 2No 630A TP MCCB
- 5No 200A TP MCCB
- 1No 160A TP MCCB
- 5No 125A TP MCCB
- 7No 63A TP MCCB
- 5No 50A TP MCCB
- 7No 32A TP MCCB
- 4No 20A TP MCCB
- 2No 63A 2P MCCB
POWER FACTOR CORRECTION COMPARTMENT
Low voltage 11-step automatic bulk power factor correction capacitor
comprising with power factor control and indication:
- 3Nos. 50kVar self healing capacitor using metallised film
technology with safety device
- Ditto but with 2No. 25kVAr capacitance
- Ditto but with 2No. 20kVAr capacitance
- Ditto but with 2No. 10kVAr capacitance
- Ditto but with 2No. 3kVAr capacitance
- Control equipment c/w DIN removable fuses and carriers per
switching stage, suitable rated reactive sensing microrelays per
switching stage, Hand/Off/Auto selector switch per switching stage
and set of control fuses
- Complete power and control wiring as shown on drawings
| e.g. ABB, Schneider | 1 | No |  | 0 | 0 | 0
LV Panels
Supply install and connect the following.
Panels to be Schneider, Siemens, ABB or equal approved equal
Each panel shall be complete with support system suitable for the
specified mounting arrangement.
Refer to specification sheets and drawings for additional details for
each panel.
Pg 2/2 | To Collection |  |  |  | 0 |  | 0
ITEM | ELEMENT No. 2 - ELECTRICAL SERVICES: MAINS SUPPLY & DISTRIBUTION AND EARTHING
| DESCRIPTION | QTY | UNIT |  | TOTAL |  | TOTAL
|  |  |  | RATE (N) | COST (N) | RATE ($) | AMOUNT ($)
Supply, install and connect:
7 | SMB-A, comprising of
Incomer:
Free standing 630A TP MCCB with 21kA 630A rated busbars and
SPD 40kA rated surge arresters, Multimeter, Imported enclosure,
floor stand brackets and other details as shown on drawings etc.
Outgoing:
- 13No 100A TP MCCB
- 1No 63A TP MCCB
- 2No 32A TP MCCB
| e.g. ABB, Schneider | 1 | No |  | 0 | 0 | 0
8 | SMB-B, comprising of
Incomer:
Free/Wall standing 125A TP MCCB with 21kA 125A rated busbars
and SPD 40kA rated surge arresters, Multimeter, Imported
enclosure, floor stand brackets and other details as shown on
drawings etc.
Outgoing:
- 5No 63A TP MCCB
- 1No 32A TP MCCB
| e.g. ABB, Schneider | 1 | ,, |  | 0 | 0 | 0
9 | SMB-C, comprising of
Incomer:
Free/Wall standing 125A TP MCCB with 21kA 125A rated busbars
and SPD 40kA rated surge arresters, Multimeter, Wiring to integral distribution
panel, Imported enclosure, floor stand brackets and other details as shown on
drawings etc.
Outgoing:
- 4No 63A TP MCCB
- 1No 32A TP MCCB
| e.g. ABB, Schneider | 1 | ,, |  | 0 | 0 | 0
10 | SMB-D, comprising of
Incomer:
Free/Wall standing 125A TP MCCB with 21kA 125A rated busbars
and SPD 40kA rated surge arresters, Multimeter, Imported
enclosure, floor stand brackets and other details as shown on
drawings etc.
Outgoing:
- 24No 20A 2P MCB
- 5No 32A 2P MCB
- 2No 20A TP MCB
- 4No 32A TP MCB
Integral Distribution Board
Incomer:
50A TP MCB with 10kA 50A rated busbars as shown on drawings
Outgoing:
- 2Nos 10A 1P MCB
- 8Nos 20A 1P MCB
| e.g. ABB, Schneider | 1 | ,, |  | 0 | 0 | 0
11 | SMB-E, comprising of
Incomer:
Free/Wall standing 125A TP MCCB with 21kA 125A rated busbars
and SPD 40kA rated surge arresters, Multimeter, Imported
enclosure floor stand brackets and other details as shown on
drawings etc.
Outgoing:
- 24No 20A 2P MCB
- 5No 32A 2P MCB
- 2No 20A TP MCB
- 4No 32A TP MCB
| e.g. ABB, Schneider | 1 | ,, |  | 0 | 0 | 0
12 | SMB-F, comprising of
Incomer:
Free/Wall standing 160A TP MCCB with 21kA 160A rated busbars
and SPD 40kA rated surge arresters, Multimeter, Imported
enclosure floor stand brackets and other details as shown on
drawings etc.
Outgoing:
- 15No 32A TP MCCB
| e.g. ABB, Schneider | 1 | ,, |  | 0 | 0 | 0
Pg 2/3 | To Collection |  |  |  | 0 |  | 0
ITEM | ELEMENT No. 2 - ELECTRICAL SERVICES: MAINS SUPPLY & DISTRIBUTION AND EARTHING
| DESCRIPTION | QTY | UNIT |  | TOTAL |  | TOTAL
|  |  |  | RATE (N) | COST (N) | RATE ($) | AMOUNT ($)
Supply, install and connect:
Controls
13 | Lighting Panel/Kiosk
Indoor wall mounted lighting kiosk comprising:
- 63A TPN MCCB incomer with 63A rated busbars
- 63A TPN contactor (NO)+auxilliary contacts with operating coil
- 2A SP MCB
- photoelectric kit
- manual override switch (ON/OFF or push button)
- transparent fronted steel cabinet c/w integral earth bar
- LED indicators
- 32A rated busbars with 6No. 20A SP MCBs for outgoing circuits
| e.g. ABB, Siemens | 1 | ,, |  | Excluded | 0 | 0
Distribution Boards
14 | 100A TPN 12 way distribution board 'G2LP', 'G4LP', 'G5LP', G2P', 'F1LP' & 'F2LP'
| c/w type C MCBs and integral isolator 63A TPN 300mA RCD c/w transparent cover e.g. Legrand, Hager | 6 | ,, |  | 0 | 0 | 0
15 | 100A TPN 8 way distribution board 'G1LP', 'G3LP', 'F3P', 'F3LP' and 'F4LP'
| c/w type C MCBs and integral isolator e.g. Legrand, Hager | 6 | ,, |  | 0 | 0 | 0
16 | 100A TPN 6 way distribution board 'UP2' and 'UP3'. | 2 | ,, |  | 0 | 0 | 0
c/w type C MCBs and integral isolator e.g. Legrand, Hager
17 | 63A TPN 4 way distribution board 'UP1', 'UP4', 'UP5', 'GHLP'. 'PHLP', | 9 | ,, |  | 0 | 0 | 0
SPLP', 'T1LP', 'T2LP' and 'T3LP' c/w type C MCBs and integral isolator
e.g. Legrand, Hager
18 | 63A SPN 4 way distribution board 'DTLP', 'WTLP' and 'UP6' | 3 | ,, |  | 0 | 0 | 0
c/w type C MCBs and integral isolator e.g. Legrand, Hager
Isolating Switches
Supply install and connect the following. All isolators are to be
4 pole rotary type with transparent front cover suitable for
outdoor mounting. Outdoor isolators must be complete with mounting brackets
suitable for free standing positions if required e.g. Legrand
19 | 200A TPN | 10 | ,, |  | 0 | 0 | 0
20 | 125A TPN | 4 | ,, |  | 0 | 0 | 0
21 | 63A TPN | 3 | ,, |  | 0 | 0 | 0
22 | 32A TPN | 24 | ,, |  | 0 | 0 | 0
23 | 20A TPN | 7 | ,, |  | 0 | 0 | 0
24 | 32A SPN | 6 | ,, |  | 0 | 0 | 0
25 | 20A SPN | 50 | ,, |  | 0 | 0 | 0
26 | 2000A TPN Switchfuse c/w HRC fuses e.g. Merlin Gerin, BIL | 1 | ,, |  | 0 | 0 | 0
Pg 2/4 | To Collection |  |  |  | 0 |  | 0
ITEM | ELEMENT No. 2 - ELECTRICAL SERVICES: MAINS SUPPLY & DISTRIBUTION AND EARTHING
| DESCRIPTION | QTY | UNIT |  | TOTAL |  | TOTAL
|  |  |  | RATE (N) | COST (N) | RATE ($) | AMOUNT ($)
Supply, install and connect:
Inverters
27 | 5kVA 3ph input & output at 400V, 50Hz free standing Hybrid Solar Inverter unit
c/w line conditioner, backup battery with battery circuit breaker, battery
monitoring and deep discharge protection device, by-pass switch with 7-hour
Autonomy on full load complete with battery string 3 year life, battery rack,
| wiring and autochangeover device etc. APC, Liebert | 1 | No |  | Excluded | 0 | 0
28 | 40kVA 3ph input & output at 400V, 50Hz free standing Inverter unit c/w line
conditioner, backup battery with battery circuit breaker, battery monitoring and
deep discharge protection device, by-pass switch with 7-hour Autonomy on full
load complete with battery string 3 year life, rack wiring and autochangeover
| device etc. APC, Liebert | 1 | ,, |  | Excluded | 0 | 0
29 | 50kVA 3ph input & output at 400V, 50Hz free standing Inverter unit c/w line
conditioner, backup battery with battery circuit breaker, battery monitoring and
deep discharge protection device, by-pass switch with 7-hour Autonomy on full
load complete with battery string 3 year life, rack wiring and autochangeover
| device etc. APC, Liebert | 2 | ,, |  | Excluded | 0 | 0
30 | 80kVA 3ph input & output at 400V, 50Hz free standing Inverter unit c/w line
conditioner, backup battery with battery circuit breaker, battery monitoring and
deep discharge protection device, by-pass switch with 7-hour Autonomy on full
load complete with battery string 3 year life, rack wiring and autochangeover
| device etc. APC, Liebert | 5 | ,, |  | Excluded | 0 | 0
Cables
Supply install and connect the following.
All cables to be Coleman, Kabelmetal, Nigerchin, BICC, Pirelli, NOCACO or equal
All cables are to be supplied complete with lugs, glands, cleats etc.
31 | 12kV 3x1c 50mm2 XLPE/PVC cable from 11kV panel to 1250kVA
| transformer | 12 | m |  | Excluded | 0 | 0
32 | 1c 70mm2 PVC/PVC insulated cables as cpc for 31 above | 12 | ,, |  | Excluded | 0 | 0
33 | 1c 500mm2 PVC/PVC cables from:
| - 1250KVA Transformer to ATS Panel | 288 | ,, |  | 0 | 0 | 0
| - ATS panel to the main LV Panel | 24 | ,, |  | 0 | 0 | 0
0
34 | 1c 500mm2 PVC/PVC cpc cables for 33 above | 40 | m |  | 0 | 0 | 0
35 | 1c 240mm2 PVC/PVC cables from:
| - Gen 1 to Generator Panel | 600 | ,, |  | Excluded | 0 | 0
| - Gen 2 to Generator Panel | 720 | ,, |  | Excluded | 0 | 0
| - Gen 3 to Generator Panel | 780 | ,, |  | Excluded | 0 | 0
[6 empty] | 0 | 0
36 | 1c 240mm2 PVC/PVC cpc cables for 35 above | 175 | m |  | Excluded | 0 | 0
37 | 1c 185mm2 PVC/PVC per circuit cables from MLVP to SMB-A
| located on ground floor main building. | 440 | ,, |  | 0 | 0 | 0
38 | 1c 95mm2 PVC/PVC cables as CPC for item 37 above | 55 | ,, |  | 0 | 0 | 0
39 | 4c 95mm2 PVC/PVC cables from:
| - MLVP to X-RAY 1 Inverter and Equipment Isolators | 100 | ,, |  | 0 | 0 | 0
| - MLVP to X-RAY 2 Inverter and Equipment Isolators | 120 | ,, |  | 0 | 0 | 0
| - MLVP to X-RAY 3 Inverter and Equipment Isolators | 120 | ,, |  | 0 | 0 | 0
| - MLVP to X-RAY 4 Inverter and Equipment Isolators | 70 | ,, |  | 0 | 0 | 0
| - MLVP to X-RAY 5 Inverter and Equipment Isolators | 70 | ,, |  | 0 | 0 | 0
40 | 1c 50mm2 PVC/PVC cables as CPC for item 39 above | 480 | ,, |  | 0 | 0 | 0
41 | 4c 70mm2 PVC/PVC cables from:
| - MLVP to SMB-F | 55 | ,, |  | 0 | 0 | 0
42 | 1c 35mm2 PVC/PVC cables as CPC for item 41 above | 55 | ,, |  | 0 | 0 | 0
Pg 2/5 | To Collection |  |  |  | 0 |  | 0
ITEM | ELEMENT No. 2 - ELECTRICAL SERVICES: MAINS SUPPLY & DISTRIBUTION AND EARTHING
| DESCRIPTION | QTY | UNIT |  | TOTAL |  | TOTAL
|  |  |  | RATE (N) | COST (N) | RATE ($) | AMOUNT ($)
Supply, install and connect:
43 | 4c 50mm2 PVC/PVC cables from:
| - MLVP to SMB-B Inverter and Isolator | 140 | m |  | 0 | 0 | 0
| - MLVP to SMB-C Inverter and Isolator | 100 | ,, |  | 0 | 0 | 0
| - MLVP to SMB-D Inverter and Isolator | 70 | ,, |  | 0 | 0 | 0
| - MLVP to SMB-E | 60 | ,, |  | 0 | 0 | 0
44 | 1c 25mm2 PVC/PVC cables as CPC for item 43 above | 370 | ,, |  | 0 | 0 | 0
45 | 4c 35mm2 PVC/PVC cables from:
| - SMB-A to G1LP | 80 | m |  | 0 | 0 | 0
| - SMB-A to G2LP | 60 | ,, |  | 0 | 0 | 0
| - SMB-A to G2P | 60 | ,, |  | 0 | 0 | 0
| - SMB-A to G3LP | 40 | ,, |  | 0 | 0 | 0
| - SMB-A to G4LP | 5 | ,, |  | 0 | 0 | 0
| - SMB-A to G5LP | 40 | ,, |  | 0 | 0 | 0
| - SMB-A to F1LP | 80 | ,, |  | 0 | 0 | 0
| - SMB-A to F2LP | 80 | ,, |  | 0 | 0 | 0
| - SMB-A to F2P | 80 | ,, |  | 0 | 0 | 0
| - SMB-A to F3LP | 35 | ,, |  | 0 | 0 | 0
| - SMB-A to F3P | 45 | ,, |  | 0 | 0 | 0
| - SMB-A to F4LP | 40 | ,, |  | 0 | 0 | 0
46 | 1c 16mm2 PVC/PVC cables as CPC for item 45 above | 645 | ,, |  | 0 | 0 | 0
47 | 4c 16mm2 PVC/PVC cables from
| - MLVP to External lighting kiosk | 15 | ,, |  | Excluded | 0 | 0
| - MLVP to Power House DB 'PHLP' | 15 | ,, |  | Excluded | 0 | 0
| - MLVP to Gate House DB 'GHLP' | 35 | ,, |  | Excluded | 0 | 0
| - MLVP to Sputum Building DB 'SPLP' | 75 | ,, |  | Excluded | 0 | 0
| - MLVP to Water Treatment Plant Isolator | 90 | ,, |  | Excluded | 0 | 0
| - SMB-B to UP1 | 60 | ,, |  | Excluded | 0 | 0
| - SMB-B to UP2 | 30 | ,, |  | Excluded | 0 | 0
| - SMB-B to UP4 | 30 | ,, |  | Excluded | 0 | 0
| - SMB-C to UP3 | 40 | ,, |  | Excluded | 0 | 0
| - SMB-C to UP5 | 5 | ,, |  | Excluded | 0 | 0
48 | 1c 16mm2 PVC/PVC cables as CPC for item 47 above | 395 | ,, |  | Excluded | 0 | 0
49 | 4c 10mm2 PVC/PVC cables from
| - MLVP to Toilet Building DB 'T1LP' | 100 | ,, |  | 0 | 0 | 0
| - MLVP to Toilet Building DB 'T2LP' | 125 | ,, |  | 0 | 0 | 0
| - MLVP to Toilet Building DB 'T3LP' | 70 | ,, |  | 0 | 0 | 0
50 | 1c 10mm2 PVC/PVC cables as CPC for item 49 above | 295 | ,, |  | 0 | 0 | 0
51 | 2c 16mm2 PVC/PVC cables from
| - MLVP to DOT Building DB 'DTLP' | 60 | m |  | Excluded | 0 | 0
| - MLVP to Water Treatment Plant Building DB 'WTLP' | 90 | ,, |  | Excluded | 0 | 0
| - SMB-C to Sputum Building DB 'UP6' | 90 | ,, |  | Excluded | 0 | 0
52 | 1c 16mm2 PVC/PVC cables as CPC for item 51 above | 240 | ,, |  | Excluded | 0 | 0
Pg 2/6 | To Collection |  |  |  | 0 |  | 0
ITEM | ELEMENT No. 2 - ELECTRICAL SERVICES: MAINS SUPPLY & DISTRIBUTION AND EARTHING
| DESCRIPTION | QTY | UNIT |  | TOTAL |  | TOTAL
|  |  |  | RATE (N) | COST (N) | RATE ($) | AMOUNT ($)
53 | 4c 6mm2 PVC/PVC cables from
| - MLVP to Borehole Pump Isolator | 90 | m |  | Excluded
| - MLVP to Diesel Pumps Isolator | 55 | ,, |  | Excluded
| - MLVP to Water Transfer Pumps Isolator | 90 | ,, |  | Excluded
| - MLVP to Fire Hosereel Pumps Isolator | 90 | ,, |  | Excluded
| - MLVP to CU-VRV3/2 | 45 | ,, |  | Excluded
| - SMB-F to FSUs | 450 | ,, |  | Excluded
54 | 1c 6mm2 PVC/PVC cables as CPC for item 53 above | 820 | ,, |  | Excluded
55 | 4c 4mm2 PVC/PVC cables from
| - MLVP to CU-VRV2/2 | 65 | ,, |  | 0 | 0 | 0
| - MLVP to AHU 1 | 65 | ,, |  | 0 | 0 | 0
| - MLVP to AHU 2 | 75 | ,, |  | 0 | 0 | 0
56 | 1c 4mm2 PVC/PVC cables as CPC for item 55 above | 205 | ,, |  | 0 | 0 | 0
Supply, install and connect:
All cabling indicated below to laboratory equipment in TB and General
laboratories are provisional and subject to re-measurement.
57 | 5c 6mm2 PVC/PVC cables from SMB-D and SMB-E to
| - 2x3no. Autoclave machines | 90 | m |  | 0 | 0 | 0
| - 2x1no. Water Distiller | 30 | ,, |  | 0 | 0 | 0
58 | 5c 4mm2 PVC/PVC cables from SMB-D and SMB-E to
| - 2x2no. BioSafety Cabinets | 40 | ,, |  | 0 | 0 | 0
59 | 3c 6mm2 PVC/PVC cables from SMB-D and SMB-E to
| - 2x1no. Epp. Refrigerated Centrifuge | 30 | ,, |  | 0 | 0 | 0
| - 2x1no. Hettich Rotina 420r Refrigerated Centrifuge | 30 | ,, |  | 0 | 0 | 0
| - 2x1no. BD BACTEC MGIT 960 | 30 | ,, |  | 0 | 0 | 0
60 | 3c 4mm2 PVC/PVC cables from SMB-D and SMB-E to
| - 2x6no. GeneXpert Machine, 4 modules | 90 | ,, |  | 0 | 0 | 0
| - 2x6no. Medical Refrigerator | 90 | ,, |  | 0 | 0 | 0
| - 2x1no. Ultra low Freezer | 30 | ,, |  | 0 | 0 | 0
| - 2x1no. NUVE Refrigerated Centrifuge | 30 | ,, |  | 0 | 0 | 0
| - 2x2no. Incubator | 40 | ,, |  | 0 | 0 | 0
| - 2x2no. Vortex Mixter | 40 | ,, |  | 0 | 0 | 0
| - 2x1no. Fluorescent Microscope | 30 | ,, |  | 0 | 0 | 0
| - 2x1no. Weighing Balance | 30 | ,, |  | 0 | 0 | 0
| - 2x2no. BD BACTEC MIGIT 320 | 40 | ,, |  | 0 | 0 | 0
uPVC ducts and Cable trays for Power Cables
61 | 150mmW x 50mm galvanised perforated cable tray/cable ladder
c/w all accessories such as bends,tees, end caps, couplings, supports,
| brackets etc. e.g. Cablofil | 100 | m |  | 0 | 0 | 0
62 | Ditto but 500mmW x 100mm | 400 | ,, |  | 0 | 0 | 0
63 | Ditto but 500mmW x 100mm | 100 | ,, |  | 0 | 0 | 0
64 | 150mm diameter uPVC pipe c/w all accessories | 1700 | ,, |  | 0 | 0 | 0
65 | 100mm diameter uPVC pipe c/w all accessories | 450 | ,, |  | 0 | 0 | 0
66 | 50mm diameter uPVC pipe c/w all accessories | 250 | ,, |  | 0 | 0 | 0
uPVC ducts and Cable trays for ELV Cables
67 | 300mmW x 50mm galvanised wire mesh type cable tray/cable ladder
c/w all accessories such as bends,tees, end caps, couplings, supports,
| brackets etc. e.g. Cablofil | 350 | m |  | 0 | 0 | 0
68 | Ditto but 500mmW x 100mm | 50 | ,, |  | 0 | 0 | 0
69 | 100mm diameter uPVC pipe c/w all accessories | 75 | ,, |  | 0 | 0 | 0
70 | 75mm diameter uPVC pipe c/w all accessories | 300 | ,, |  | 0 | 0 | 0
Pg 2/7 | To Collection |  |  |  | 0 |  | 0
ITEM | ELEMENT No. 2 - ELECTRICAL SERVICES: MAINS SUPPLY & DISTRIBUTION AND EARTHING
| DESCRIPTION | QTY | UNIT |  | TOTAL |  | TOTAL
|  |  |  | RATE (N) | COST (N) | RATE ($) | AMOUNT ($)
Supply, install and connect:
Earthing
All cables to be Coleman, Kabelmetal, BICC, Pirelli, NOCACO or approved equal
All cables are to be supplied complete with lugs, glands, cleats etc.
71 | 1c 70mm2 PVC/PVC cable from 1.25MVA Transformer direct to the earth pits | 20 | m |  | Excluded | 0 | 0
72 | 1c 70mm2 PVC/PVC cable from 1.25MVA Transformer to the Main Earth Terminal | 20 | ,, |  | Excluded | 0 | 0
73 | 1c 70mm2 PVC/PVC cable from HV Panel to the Main Earth Terminal | 15 | ,, |  | Excluded | 0 | 0
74 | 1c 240mm2 PVC/PVC cable from base frame of generators
| G1, G2 & G3 to Generaors earth bar (included in item 36) | 0 | ,, |  | Excluded | 0 | 0
75 | 1c 500mm2 PVC/PVC cable from MLVP to the Main Earth Terminal | 10 | ,, |  | 0 | 0 | 0
76 | 1c 500mm2 XLPE/PVC cable from the Main Earth Terminal to
| earth electrodes in main earth pits | 20 | ,, |  | 0 | 0 | 0
77 | 1000mm2 Main Earth Terminal c/w insulators and channel base
| suitable for connecting all earth terminals | 2 | set |  | 0 | 0 | 0
78 | Concrete inspection pit comprising:
2no 1.2m long copper earth rods with coupling, driving head and
cable-to-rod lugs to achieve
| an earth resistance =< 0.2 ohms e.g. Furse | 10 | No |  | 0 | 0 | 0
79 | Allow for provisional sum of N250,000.00 for additional earthing | sum |  |  | Excluded
Fire barriers
80 | Allow provisional sum for the provision of fire barriers throughout
the building in electrical risers and services traversing horizontally
| between 2 zones of fire compartmentalisation | Lot |  |  | Excluded
| Page 2/9 |  |  |  | 0 |  | 0
Collection
| Page 2/1 |  |  |  | 0 |  | 0
| Page 2/2 |  |  |  | 0 |  | 0
| Page 2/3 |  |  |  | 0 |  | 0
| Page 2/4 |  |  |  | 0 |  | 0
| Page 2/5 |  |  |  | 0 |  | 0
| Page 2/6 |  |  |  | 0 |  | 0
| Page 2/7 |  |  |  | 0 |  | 0
| Page 2/8 |  |  |  | 0 |  | 0
Pg 2/9 | TO SUMMARY |  |  |  | 0 |  | 0
ITEM | ELEMENT No.3 - MAIN BUILDING - ELECTRICAL SERVICES: MAIN BUILDING: LIGHTING INSTALLATION
| DESCRIPTION | QTY | UNIT |  | TOTAL |  | TOTAL
|  |  |  | RATE (N) | COST (N) | RATE ($) | AMOUNT ($)
Supply, install and connect:
Cables, Conduit etc. in Final Circuits
-All cables to be Coleman, Kabelmetal, Nigerchin, NOCACO or approved equal
- All fittings are to LED and to be complete with suitable drivers and emergency
Kits, fixing accessories as required. C
- Colour temperature shall be of the 'Cool White' range (6000K) unless otherwise
stated.
- All recessed fittings are to be terminated with either flexible cables or multicore
cables in flexible conduits.
- Certain Luminaires, particularly in the X-RAY rooms are to be dimmable and
DALI compatible
- All luminaires are to have power factor correction of 90% minimum.
1 | 20mm dia upvc conduit wired using 1.5mm2 PVC cables as shown on
drawing to each lighting fittings and extract fan outlets c/w separate CPC
| (earth wire) per circuit accessory boxes etc. on a 'per point basis' . | 645 | No |  | 0 | 0 | 0
Lighting Fittings
2 | 1200mm 36W LED linear fitting with IP66 diffuser 3600LM
| e.g. Philips Smartbright Waterproof G3 WT068C or approved equal | 10 | ,, |  | 0 | 0 | 0
3 | Ditto but with built-in 3 hour emergency module. | 4 | ,, |  | 0 | 0 | 0
4 | Recessed downlight with 14W LED fitting, 1680LM IP54 e.g. Philips, Ledvance or
| approved equal | 31 | ,, |  | 0 | 0 | 0
5 | Ditto but with built-in 3 hour emergency module. | 6 | ,, |  | 0 | 0 | 0
6 | Recessed downlight with 25W LED fitting, non-dimmable version 3150LM
| e.g. Philips, Ledvance or approved equal | 6 | ,, |  | 0 | 0 | 0
7 | Surface circular decorative fitting with opal glass bowl and 20W Led fitting
| to IP66 e.g. Philips, Ansel or approved equal | 14 | ,, |  | 0 | 0 | 0
8 | 600 x 600mm recessed modular fitting with 40W LED panel light fitting |  |  |  |  | `
| e.g. Philips or approved equal | 335 | ,, |  | 0 | 0 | 0
9 | Ditto but with built-in emergency lighting kit e.g. Philips or approved equal | 95 | ,, |  | 0 | 0 | 0
10 | 600 x 600mm recessed mounted modular fitting with 40W LED panel light fitting
| dimmable version for use in X-ray room e.g. Philips or approved equal | 15 | ,, |  | 0 | 0 | 0
11 | Ditto but with built-in emergency lighting kit e.g. Philips or approved equal | 5 | ,, |  | 0 | 0 | 0
[6 empty] | 0 | 0
12 | 600 x 600mm surface mounted modular fitting with 40W LED panel light fitting
| for use in TB & General laboratory rooms e.g. Philips or approved equal | 72 | ,, |  | 0 | 0 | 0
13 | Ditto but with built-in emergency lighting kit e.g. Philips or approved equal | 13 | ,, |  | 0 | 0 | 0
14 | Wall mounted emergency imprinted exit sign with appropriate directional arrow
| for maintained mode e.g. Thorn Voyager | 17 | ,, |  | 0 | 0 | 0
15 | Ceiling/Recessed mounted emergency imprinted exit sign with appropriate
| directional arrow for maintained mode e.g. Thorn Voyager | 5 | ,, |  | 0 | 0 | 0
Pg 3/1 | To Collection |  |  |  | 0 |  | 0
ITEM | ELEMENT No.3 - MAIN BUILDING - ELECTRICAL SERVICES: MAIN BUILDING: LIGHTING INSTALLATION
| DESCRIPTION | QTY | UNIT |  | TOTAL |  | TOTAL
|  |  |  | RATE (N) | COST (N) | RATE ($) | AMOUNT ($)
Supply, install and connect:
Wiring Accessories
All plate switches are to be complete with matching conduit boxes
16 | 1-gang, plateswitch with 1-way 10A sp and white moulded cover plate
c/w screw plug
| e.g. Legrand or approved equal | 78 | No |  | 0 | 0 | 0
17 | 1-gang, plateswitch with 2-way 10A sp and white moulded cover plate
c/w screw plug
| e.g. Legrand or approved equal | 30 | ,, |  | 0 | 0 | 0
18 | 2-gang, plateswitch with 1/2-way 10A sp and white moulded cover plate
c/w screw plug
| e.g. Legrand or approved equal | 12 | ,, |  | 0 | 0 | 0
19 | Flush 10A intermediate single module switch with white moulded
| cover plate and support frame e.g. Legrand Mallia or approved equal | 4 | ,, |  | 0 | 0 | 0
20 | Flush 1-gang 2-way Power rotary dimmer 100-500W/VA switch with white moulded
overplate suitable for dimming of LED fittings
| e.g. Legrand or approved equal | 5 | ,, |  | 0 | 0 | 0
21 | 13A fused switched flex outlet with neon light and white moulded
| coverplate c/w screw plug e.g. Legrand or approved equal | 17 | ,, |  | 0 | 0 | 0
| Page 3/2 |  |  |  | 0 |  | 0
Collection
| Page 3/1 |  |  |  | 0 |  | 0
| Page 3/2 |  |  |  | 0 |  | 0
Pg 3/2 | TO SUMMARY |  |  |  | 0 |  | 0
ITEM | ELEMENT No. 4 - MAIN BUILDING - ELECTRICAL SERVICES: POWER INSTALLATION
| DESCRIPTION | QTY | UNIT |  | TOTAL |  | TOTAL
|  |  |  | RATE (N) | COST (N) | RATE ($) | AMOUNT ($)
Supply, erect and connect the following:
Conduit, Cables, Accessory boxes for Final Circuits
Conduit Cables, Accessory boxes for Final Circuits
1 | 25mm dia upvc conduit wired in ring and radial circuits using 1c 2.5mm2 PVC
cable to each 13A SSO c/w separate CPC (earth wire) per circuit
| accessory boxes etc. on a 'per point' basis. | 552 | No |  | 0 | 0 | 0
2 | 25mm dia upvc conduit wired in radial circuits using 1c 4mm2 PVC cable to each
20A dp outlet for airconditioners, water heaters, hand dryers c/w separate CPC
| (earth wire) per circuit accessory boxes etc. on a 'per point' basis. | 165 | ,, |  | 0 | 0 | 0
3 | 25mm dia upvc conduit wired in radial circuits using 1c 6mm2 PVC cable to each
45A dp cooker control unit c/w separate CPC (earth wire) per circuit
| accessory boxes etc. | 1 | ,, |  | 0 | 0 | 0
Wiring Accessories
4 | Flush 13A twin-gang switch socket outlet with white
| moulded coverplate for raw power outlets e.g. Legrand 7300 76 | 331 | No |  | 0 | 0 | 0
5 | Surface mounted 13A 2-gang switch socket outlet, weatherproof
| type to IP56 with RCD protection e.g. MK 56233 WHI | 4 | ,, |  | 0 | 0 | 0
6 | 13A 2-gang switch socket outlet with red moulded coverplate
| for UPS/Inverter power outlets e.g. Legrand | 135 | ,, |  | 0 | 0 | 0
7 | 13A fused unswitched flex outlet with white moulded coverplate
c/w fuse base for permanently connected equipment e.g Fire Alarm control panel
Public Address center, CATV Headend equipment etc.
| e.g. Legrand or approved equal | 5 | ,, |  | 0 | 0 | 0
8 | Flush 20A dp switch with neon c/w white moulded coverplate for water heaters
| and marked 'Water Heater' e.g. Legrand or approved equal | 2 | ,, |  | 0 | 0 | 0
9 | Flex outlet plate for 5 above. | 2 | ,, |  | 0 | 0 | 0
10 | 20A dp switch with flex outlet and neon for airconditioners and hand dryers
c/w screw plug and neon light (hand dryers are provided with 20A connectors
| concealed in back box behind the equipment) e.g. Legrand or approved equal | 163 | ,, |  | 0 | 0 | 0
11 | Flex outlet plate concealed behind AC unit for 10 above. | 103 | ,, |  | 0 | 0 | 0
12 | 45amp DP cooker control unit c/w pilot lamp & 13 socket outlet
| e.g. Legrand Mallia or approved equal | 1 | ,, |  | 0 | 0 | 0
13 | Flush connection unit with flex outlet concealed behind Cooker unit for 12 above | 1 | ,, |  | 0 | 0 | 0
14 | Flush wall 300 x 300mm uPVC Adaptable box | 6 | ,, |  | 0 | 0 | 0
15 | 3 compartment concealed flush floor outlet comprising of
the following:
- 13A 2-gang SSO with white moulded case coverplate-raw power
- 13A 2-gang SSO with red moulded case coverplate for UPS/Inverter
- 2 x Dual RJ45 outlets with Cat 6 connectors
| e.g. Legrand, MK | 26 | ,, |  | 0 | 0 | 0
16 | Patient bedhead panel c/w lights with switch, power and data sockets | 25 | ,, |  | 0 | 0 | 0
Pg 4/1 | TO SUMMARY |  |  |  | 0 |  | 0
ITEM | ELEMENT No. 5 - MAIN BUILDING - ELECTRICAL SERVICES: ELV - WIREWAYS ONLY
| DESCRIPTION | QTY | UNIT |  | TOTAL |  | TOTAL
|  |  |  | RATE (N) | COST (N) | RATE ($) | AMOUNT ($)
Supply, erect and connect the following:
TELEPHONE SYSTEM
Conduit & Accessory boxes
1 | Allow for complete wireways comprising of 25mm dia uPVC conduit system c/w
draw wires in each conduit run to each voice outlet box from Telecoms cabinets
locations in Server room on first floor and other zones as shown on the drawings
| on a 'per point' basis. | 122 | No |  | 0 | 0 | 0
DATA SYSTEM
Conduit, Cables & Accessory boxes
2 | Allow for complete wireways comprising of 25mm dia uPVC conduit system c/w
draw wires in each conduit run to each voice outlet box from Telecoms cabinets
locations in Server room on first floor and other Telecoms closets as shown on
| the drawings on a 'per point' basis. | 210 | ,, |  | 0 | 0 | 0
FIRE DETECTION AND ALARM SYSTEM
Conduit, Cables & Accessory boxes
3 | Allow for complete wireways comprising of 25mm dia uPVC conduit system
c/w draw wires in each conduit run to each trigger device and sounder on each
| floor from Fire Alarm control panel location on ground floor lobby area (Stream 2) | 135 | ,, |  | 0 | 0 | 0
on a 'per point' basis.
CENTRAL TV SYSTEM
Conduit, Cables & Accessory boxes etc.
4 | Allow for complete wireways comprising of 25mm dia upvc
conduit system c/w draw wires in each conduit run to each coaxial TV
outlet box from TV headend position located in Server room as shown on the
| drawngs on a 'per point' basis. | 30 | ,, |  | 0 | 0 | 0
SURVEILLANCE SYSTEM
Conduit & Accessory boxes
5 | Allow for complete wireways comprising of 25mm dia uPVC conduit system
c/w draw wires in each conduit run to each camera location
from Network Video Recorder located in Server room room on first floor
| on a 'per point' basis. | 60 | ,, |  | 0 | 0 | 0
DISABLED EMERGENCY INDICATION SYSTEM
Conduit & Accessory boxes
6 | Allow for complete wireways comprising of 25mm dia upvc conduit system
c/w draw wires in each conduit run to panic button and sounder/strobe locations
in 4no. Disabled Toilet locations from Emergency Indication control panel location on ground
| on ground floor lobby area and Guard house | 12 | ,, |  | 0 | 0 | 0
ACCESS CONTROL SYSTEM
Conduit, Cables & Accessory boxes
7 | Allow for complete wireways comprising of 25mm dia upvc conduit system
c/w draw wires in each conduit run to access control door locations in the
| building from local controller and central access server location in Server room | 18 | ,, |  | 0 | 0 | 0
PUBLIC ADDRESS SYSTEM
Conduit, Cables & Accessory boxes
8 | Allow for complete wireways comprising of 25mm dia upvc conduit system
c/w draw wires in each conduit run to each loudspeaker and desktop control
console position from Power Amplifier position in Server room c/w accessories
| & draw boxes, couplers, locknuts etc on a per point basis | 75 |  |  | 0 | 0 | 0
Pg 5/1 | TO SUMMARY |  |  |  | 0 |  | 0
ITEM | ELEMENT No. 6 - MAIN BUILDING - ELECTRICAL SERVICES: LIGHTNING PROTECTION SYSTEM
| DESCRIPTION | QTY | UNIT |  | TOTAL |  | TOTAL
|  |  |  | RATE (N) | COST (N) | RATE ($) | AMOUNT ($)
Supply, erect and connect the following:
1 | 20mm x 3mm bare HDHC copper tape e.g Furse TC 030 | 1200 | m |  | 0 | 0 | 0
a | Suitable saddles (self-adhesive for roofing sheets) for the above e.g. CP205 | 2400 | No |  | 0 | 0 | 0
2 | 1000mm x 15mm dia high multi-point air terminal for fixing to tree top located
| within building envelope e.g. RA225 | 1 | ,, |  | 0 | 0 | 0
a | suitable brackets for rigidly fixing for the above | 20 | ,, |  | 0 | 0 | 0
3 | 25mm x 3mm PVC covered copper tape for use as down conductor
| (colour to match building exterior wall) e.g. Furse TC125 | 133 | m |  | 0 | 0 | 0
a | D.C. clips for the above e.g. Furse CP210 | 266 | No |  | 0 | 0 | 0
4 | Test clamp e.g. Furse CN105 | 19 | No |  | 0 | 0 | 0
5 | Allow for cald welding of supports, test clamps to steel stanchions | Lot |  |  |  |  | 0
6 | 1c 70mm2 BCEW copper cable ring earth electrode | 340 | m |  | 0 | 0 | 0
7 | Lightweight inspection pit with plastic base and comprising:
a | - 2No 1.2m long, 12.7mm dia copperbond earth rods
b | - coupling, driving head and tape-to-rod clamps
to achieve an overall earth resistance of <= 10 ohms
| e.g. Furse PT006+RB105+CG170+ST100+CR105 | 19 | ,, |  | 0 | 0 | 0
8 | Allow for bonding to all exposed metalwork on the roof and ground floor levels. | Lot |  |  |  |  | 0
Pg 6/1 | TO SUMMARY |  |  |  | 0 |  | 0
ITEM | ELEMENT No. 7 - TOILET BUILDINGS (1,2&3) - ELECTRICAL SERVICES: LIGHTING, POWER INSTALLATION AND ELV WIREWAYS
| DESCRIPTION | QTY | UNIT |  | TOTAL |  | TOTAL
|  |  |  | RATE (N) | COST (N) | RATE ($) | AMOUNT ($)
Supply, erect and connect the following:
LIGHTING INSTALLATION
Cables, Conduit in Final Circuits
All cables to be Coleman, Kabelmetal, Nigerchin, NOCACO or approved equal
1 | 25mm dia upvc conduit wired using 1.5mm2 PVC cables as shown
on drawings to each lighting fitting and extract fan outlet c/w
separate CPC (earth wire) per circuit accessory boxes etc. on a
| 'per point basis' | 31 | No |  | 0 | 0 | 0
Lighting Fittings
2 | Recessed downlight with 14W LED fitting, 1680LM IP54 e.g. Philips, Ledvance or
| approved equal | 19 | ,, |  | 0 | 0 | 0
3 | Ditto but with built-in emergency lighting kit e.g. Philips or approved equal | 9 | ,, |  | 0 | 0 | 0
Wiring Accessories
All plate switches are to be complete with matching conduit boxes
4 | Surface mounted 10A 1-gang 1-way switch weatherproof type
| c/w screw plug e.g Legrand or approved equal | 3 | ,, |  | 0 | 0 | 0
5 | 13A fused switched flex outlet with neon light and white moulded
| coverplate c/w screw plug e.g. Legrand or approved equal | 3 | ,, |  | 0 | 0 | 0
POWER INSTALLATION
Conduit, Cables, Accessory boxes for Final Circuits
6 | 25mm dia upvc conduit wired in radial circuits using 1c 4.0mm2
PVC cable to each 20A double pole switch for hand dryers
| c/w separate CPC (earth wire) per circuit accessory boxes, etc | 9 | ,, |  | 0 | 0 | 0
Wiring Accessories
7 | 20A dp switch with flex outlet and neon for hand dryers (hand dryers are
provided with 20A connectors concealed in back box behind the equipment)
| e.g. Legrand or approved equal | 9 | ,, |  | 0 | 0 | 0
Pg 6/1 | TO SUMMARY |  |  |  | 0 |  | 0
SUMMARY
1 | ELEMENT no 1: Preliminaries |  |  |  | 0 |  | 0
2 | ELEMENT no 2: Mains Supply, Distribution & Earthing |  |  |  | 0 |  | 0
3 | ELEMENT no 3: Lighting Installation |  |  |  | 0 |  | 0
4 | ELEMENT no 4: Power Installation |  |  |  | 0 |  | 0
5 | ELEMENT no 5: ELV Wireways |  |  |  | 0 |  | 0
6 | ELEMENT no 6: Lightning Protection System |  |  |  | 0 |  | 0
7 | ELEMENT no 7: Toilet Buildings |  |  |  | 0 |  | 0
[5 empty] | 0 |  | 0
| Add Provisional sums | [5 empty] | 0
Add Contigency sums
| TOTAL TO FORM OF TENDER |  |  |  | 0 |  | 0

## B4.3 (hidden)
BILL NO. 4.3 PLUMBING INSTALLATIONS (EXTERNAL WORKS)

## BoQ- Builders Work
S/N | DESCRIPTION | QTY | UNIT | RATE (NGN) | AMOUNT (NGN) | RATE (USD) | AMOUNT (USD)
| BILL NO. 4 - BUILDER'S WORKS AND PRIME COST SUMS |  |  |  |  | 765
BUILDER'S WORK ASSOCIATED WITH BUILDING SERVICES
A | Allow for cutting chases in dry walls, block walls, steel floors for pipes, conduits etc and concealing works associated mechanical, electrical, ELV, plumbing and other specialist services in walls, floors and ceilings as may be required. |  | Sum |  |  | 0 | 0
B | Allow for the construction of internal manholes associated with building services. |  | Sum |  |  | 0 | 0
BILL NO. 4 - BUILDER'S WORKS AND PRIME COST SUMS
|  | To General Summary |  |  | 0 |  | 0