## Cover
The United Nations Office for Project Services (UNOPS)
Detailed Design of the Kidney Building Annex -
Homs Grand Hospital
Lot 1: Main Building-first floor
Bill of Quantities
2024-01-22
Consultant: Sub-Consultant:

## Div01
Division 01: General Requirements
Item No. | Description | Unit | Quantity | Rate (USD) | Amount (USD)
0
PRELIMINARIES
The General Requirements are applicable to the whole of the works.
| All Requirements specified in the contract conditions and technical specifications. |  |  |  | 0
| General Requirements or otherwise indicated in the Contract Documents, are not necessarily listed in the Bill of Quantities, the cost of General Requirements shall be deemed to be included in the unit rates of the BOQ items and will not be paid separately. |  |  |  | 0
| The Contractor is deemed to include in his prices, all costs to comply with the instructions, rules and specifications stipulated or observed by the Local Government Authorities, insurances, guarantees, testing & commission, permits, bonds, .. Etc. |  |  |  | 0
| The Contractor shall perform all works required in this section. Including, but not limited to coordination, related works, occupancy requirements, and all other requirements; as per the specifications: |  |  |  | 0
0
IMPORTANT NOTES
0
* | It is the contractor's responsibility to reinstate any works to it’s original situation after completing the structural modifications. |  |  |  | 0
* | The contractor is fully responsible to protect all existing structures in site during construction, including existing buildings, retaining walls, and any other existing structure, and to perform any necessary tests. |  |  |  | 0
0
0
0
0
0
0
0
|  | Carried to Summary |  |  | 0 | 0

## Div02
Division 02: Site Construction | [6 empty] | d | Demolish | 0
Item No. | Description | Unit | Quantity | Rate (USD) | Amount (USD) |  | a | ARCH | 0
| DIVISION 2: SITE CONSTRUCTION | [5 empty] | s | STR | 0
| Preambles | [5 empty] | f | Façade | 0
* | The Bidders are requested to refer the General Notes, Pricing Preambles, Drawings, Specifications, Conditions of Contract, Special Conditions of Contract, all other relevant documents and to visit the site prior to pricing of the following items. | [5 empty] | r | ROOF | 0
[7 empty] | sb | Service B. | 0
* | The Contractor is held responsible on the following: (a) Removing the demolished material out of the site to an approved dump location within a maximum of three days. (b) Coordinate his daily activities and the work schedule throughout the renovation period with the Client and the Employer’s Representative. (c) Responsible for the method of demolitions and any damage or subsequent damage to the existing or adjoining structures. (d) Take all necessary measures to protect and minimize environmental hazards including pollution, noise, dust, etc. (e) Noise and dust from the works shall be kept to the minimum possible. To reduce dust supply of clean water shall be used to dampen the site. (f) Take all necessary precautions to prevent anything emanating from or associated with the works from being deposited on areas outside the contractor’s site areas. | [5 empty] | st | Site | 0
* | The Rate includes the following works: (a) Provision for hindrance due to current situations. (b) Safety provisions. (c) All the requirement to complete the work in accordance with Engineers' instructions. (d) All direct, indirect works and expenses required for the completion of the coming items. (e) All necessary scaffolding, tarpaulins and dust sheets, protecting existing work from damage by workmen or the weather and removing all temporary coverings and screens on completion.
* | All dismantled materials must be stored in a place related to the contractor until to be reinstalled (the needed materials) at the new locations according to Engineers' instructions. All above items must be approved from Engineer to determine the time and location. Cart away the depressed materials and all required as per engineering instructions.
* | Dispose: includes dispose and remove out of Site the damaged and broken out parts and debris, as per Statement of Method approved by the Engineer that includes, but not limited to, disposal working hours, movement paths, staff & equipment, gender safeguard, protection against pollution.
Carried forward
Division 02: Site Construction
Item No. | Description | Unit | Quantity | Rate (USD) | Amount (USD)
1 | SECTION 02220 - Demolition
If the owner wishes to take any of the materials/items from the existing site before demolishing, the Contractor shall hand over the selected material/item to the owner and deliver them to the approved location.
The Contractor shall remove the product and dispose of contaminated soil to the places permitted by the competent authorities and according to their instructions.
The Contractor shall bear all costs related to the dismantling, handling , demolishing and disposal works.
Dismantle: includes dismantling with care, storing the dismantled parts in a secured and adequate storage area
Handing to Client: includes handing to the client in a tidy manner all of the dismantled parts and devices which are in acceptable condition and are not intended to be reinstalled.
Dispose: includes dispose and remove out of Site the damaged and broken out parts and debris, as per Engineers instruction.
* | Prior to demolition works, the contractor shall submit a method statement to undertake the works without causing damages to the existing elements. The method statement must be approved by the engineer prior to starting the demolition works. Upon the completion of the demolition works, the engineer may request the contractor to conduct any tests to prove soundness of the relevant existing structural elements.
* | On all demolition plans the proposed dimension zone are based on the new design requirements. However, some zone might require additional demolish on due to impracticality in construction or difficulty in reinstalling new structural elements.
1.1 | Careful dismantling and removing of the following existing items, to be handed over to the hospital management for storage or maintenance and possible reuse |  |  |  | 0
a. | All existing HVAC system and all related duct work | LS | 1 |  | 0 | d
b. | All existing sanitary fixtures and related pipe work (supply and drain) | LS | 1 |  | 0 | d
c. | All existing sewage and rainwater pipe work and manholes | LS | 1 |  | 0 | d
d. | All existing cold and hot water, fire fighting, and desalinated water pipe work | LS | 1 |  | 0 | d
e. | All existing heating radiators and related pipe work | LS | 1 |  | 0 | d
f. | All existing electrical tubes, wiring (lighting, power, nurse call, etc.), boxes and cable trays | LS | 1 |  | 0 | d
g. | All existing internal walls including wall tiles where exists | LS | 1 |  | 0 | d
h. | All existing floor tiles | LS | 1 |  | 0 | d
i. | Existing wall tiles (where exists on non demolished walls) | LS | 1 |  | 0 | d
1.2 | Careful demolishing of the following existing items, to be transported as per local regulations to disposal sites
a. | Existing non-structural internal partitions as indicated in the proposed plans | LS | 1 |  | 0 | d
|  | Carried to Summary |  |  | 0 | 0

## Div04
Division 04: Masonry Works | [6 empty] | d | Demolish | 0
Item No. | Description | Unit | Quantity | Rate (USD) | Amount (USD) |  | a | ARCH | 0
[5 empty] | 0 |  | s | STR | 0
1 | SECTION 04220-Concrete Unit Masonry | [5 empty] | f | Façade | 0
| Block work shall be set out and built to the respective dimensions, thicknesses and heights required and the Contractor shall set out courses, openings and the like with approved setting out rods. The hollow and solid concrete blocks shall be sound and free from cracks, broken edges, honeycombing, and other defects that would interfere with the proper placing of block or impair the strength or performance during construction. The average compressive strength of the blocks shall not be less than 35 kg/cm2 for hollow block and 60 kg/cm2 for solid block. The blocks shall be of first class, regular in shape, size and color. The drying shrinkage of the blocks when unrestrained, shall not exceed 0.1%. Also, the water absorption of the blocks shall be not more than 10% by mass. The blocks shall be laid on a full bed of mortar and bonded with each other by toothing alternate courses and the joints between the blocks shall be filled with mortar before the next mortar bed is laid. Whole blocks shall be used except where it is necessary to cut closers. The blockwork courses shall be kept horizontal and matching perpends shall be in vertical alignment. The blocks should overlap the block below it by half of its length (half bond). Not more than 100 cm height of masonry shall be constructed at a time. The blocks shall be kept in a moist condition for 14 days. After curing, the blocks shall be dried before being used for work. Cement mortar for blockwork and stonework shall be mixed in the proportions of (1:3) (cement: sand). | [5 empty] | r | ROOF | 0
| Rates shall include: (1) Preparation of surfaces of floor slab, columns (steel or RCC) and wall surfaces for proper bonding and for control joint details as given in drawings. (2) All labor, scaffolding, safety nets, working platforms, and other necessary requirements to execute the work to the given standards and to complete the work as per specification. (3) Supplying hollow or solid cement block from good and approved factory in perfect dimension and build it in good manner. (4) Laying out the block units, spreading 2.5cm thick mortar under the blocks, also the work includes: (Lifting, handling, placing, buttering the "ears" of the blocks with mortar, wiping any excess mortar off, keeping the work level and plumb). (5) Jointing and sealing the gaps between masonry and other structural members, i.e., Columns, beams, slabs etc., provide openings as required, finish around the same. (6) Installing reinforced concrete lintels above doors and windows, lintels should extend beyond the opening at each end by at least 15 cm and Reinforced concrete bond beams and stiffener columns in walls as detailed in structural drawings. (7) Curing with water properly for not less than seven days. (8) Movements, Expansion joints. (9) Work must be true to horizontal lines and perfect plumb. Vertical joints are required to be truly vertical and align vertically with those of alternate courses. (10) Cement mortars, reinforced concrete infill (B250) between columns and block walls (10-20 cm wide) with 2ø8mm/40cm horizontally and 2ø10mm vertically according to drawings, pipes encasement, false columns 20x20 cm/4.0m among the parapet wall with 4ø12mm and bituminous paper between block work and drop beams and all requirements needed to finish the works according to the drawings, specification and to the Engineers' instructions. (11) Supplying and installing bituminous paper between block work and drop beams and testing as well as all requirements needed to finish the works. | [5 empty] | sb | Service B. | 0
[5 empty] | 0 |  | st | Site | 0
0
0
|  | Carried Forward |  |  | 0
Division 04: Masonry Works
Item No. | Description | Unit | Quantity | Rate (USD) | Amount (USD)
| Brought forward from previous page |  |  |  | 0
1.1 | Hollow concrete block walls, 100mm thick.
a | For main Building | m2 | 350 |  | 0 | a
1.2 | Hollow concrete block walls, 150mm thick.
a | For main Building and parapet | m2 | 80 |  | 0 | a
1.3 | Hollow concrete block walls, 200mm thick.
a | For main Building | m2 | 35 |  | 0 | a
0
2 | SECTION 04400 - Natural Stone Works
2.1 | Marble sills and thresholds Supply and install first class Italian Carrara marble or equivelant, light grey color , 30mm thick, for windows' sills , doors thresholds and wherever needed, bedded in cement and sand mortar 1:3, pointed using special pre­mix grout, all as per drawings and specifications. Color to be approved by the Engineer .
for windows sills, door thresholds and wherever needed
a. | For main building | m2 | 35 |  | 0 | a
0
|  | Carried to Summary |  |  | 0 | 0

## Div05
Division 05: Metal Works | [6 empty] | d | Demolish | 0
Item No. | Description | Unit | Quantity | Rate (USD) | Amount (USD)
1 | SECTION 05520 - Handrails and Railing
1.1 | Supply and install steel handrails, comprising of 40 mm dia. vertical steel pipe, 20 mm dia. horizontal steel rod, top rail of 50 mm dia. steel pipe, fixed to the stair upstand by 80mm dia. x10 mm thick steel plate , including painting zinc phosphate primer and painted with semi gloss oil paint hammer finish, welding, caps, accessories, bolts, plates and all necessary fittings and fixings, complete as as per drawing and specifications.
a. | to internal stairs , Height 900mm | L.m | 35 |  | 0
0
[5 empty] | 0 | d
[5 empty] | 0 | d
[5 empty] | 0 | d
[5 empty] | 0 | d
[5 empty] | 0 | d
[5 empty] | 0 | d
[5 empty] | 0 | d
[5 empty] | 0 | d
[5 empty] | 0 | d
[5 empty] | 0 | d
|  | Carried to Summary |  |  | 0 | 0

## Div06
Division 06: Wood and Plastic | [6 empty] | d | Demolish | 0
Item No. | Description | Unit | Quantity | Rate (USD) | Amount (USD) |  | a | ARCH | 0
[5 empty] | 0 |  | s | STR | 0
1 | SECTION 06400 - Architectural woodworks | [5 empty] | f | Façade | 0
| SECTION 06416: Solid Surfacing Countertops | [5 empty] | r | ROOF | 0
1.1 | Supply and fix the following counters, desks, cabinets including all required related works, accessories, fixing, welding, painting, all as per drawings and specifications | [5 empty] | sb | Service B. | 0
| The Contractor shall refer to enlargment drawings for more details. The contractor shall provide workshop drawing clarifyiny the fixing method, required sub-structure, finishing materials, dimensions, accessories, hardware, etc. subject to engineer's approval. | [5 empty] | st | Site | 0
0
a. | Exam/treatment room counter 12mm Acrylic Solid Surface Countertop with lower cabinets, (450X450)mm sink,mixer, and drain connection L=0.9m,W=0.6m,H=1m | NO. | 1 |  | 0 | a
b. | Exam/treatment room Wall Mounted Cabinets L=0.9m,W=0.3m,H=0.6m | NO. | 1 |  | 0 | a
c. | Straff lounge counter 12mm Acrylic Solid Surface Countertop with Lower Cabinets, (450X450)mm sink,mixer, and drain connection L=1.6m,W=0.6m,H=1m | NO. | 1 |  | 0 | a
d. | Straff lounge Wall Mounted Cabinets L=1.6m,W=0.3m,H=0.6m | NO. | 1 |  | 0 | a
e. | Nurse station/Staff base Counter L=9.9m W=0.6m,H=1m | NO. | 1 |  | 0 | a
f. | Clean workroom/Meds counter 12mm Acrylic Solid Surface Countertop with Lower Cabinets, (450X450)mm sink,mixer, and drain connection L=1.7m,W=0.6m,H=1m | NO. | 1 |  | 0 | a
g. | Clean workroom/Meds Wall Mounted Cabinets L=1.7m,W=0.3m,H=0.6m | NO. | 1 |  | 0 | a
h. | Soiled workroom counter 12mm Acrylic Solid Surface Countertop with Lower Cabinets, (450X450)mm sink,mixer, and drain connection L=1.8m,W=0.6m,H=1m | NO. | 1 |  | 0 | a
i. | Soiled workroom counter Wall Mounted Cabinets L=1.8m,W=0.3m,H=0.6m | NO. | 1 |  | 0 | a
j. | Nourishment counter 12mm Acrylic Solid Surface Countertop with Lower Cabinets, (450X450)mm sink,mixer, and drain connection L=1.8m,W=0.6m,H=1m | NO. | 1 |  | 0 | a
k. | Nourishment counter Wall Mounted Cabinets L=1.8m,W=0.3m,H=0.6m | NO. | 1 |  | 0
0
|  | Carried to Summary |  |  | 0 | 0

## Div07
Division 07: Thermal and Moisture Protection | [6 empty] | d | Demolish | 0
Item No. | Description | Unit | Quantity | Rate (USD) | Amount (USD) |  | a | ARCH | 0
[7 empty] | s | STR | 0
1 | SECTION 07140 - Fluid Applied Waterproofing
1.1 | Fluid applied waterproofing Supply and apply three perpendicular coats fluid applied proofing, all as per structural drawings, specifications and approval of the Engineer.
For foundation and vertical surfaces and wherever required.
a. | for wet areas | m2 | 135 |  | 0 | a
|  | Carried to Summary |  |  | 0 | 0

## Div08
Division 08: Openings | [6 empty] | d | Demolish | 0
Item No. | Description | Unit | Quantity | Rate (USD) | Amount (USD) |  | a | ARCH | 0
[7 empty] | s | STR | 0
| Notes: | [5 empty] | f | Façade | 0
| Steel and Wood Doors | [5 empty] | r | ROOF | 0
| The items shall include supply, fabricate, test and installation of doors made out of approved quality class I treated timber to be finished as per the given specification and drawings. Discarding materials with defects that impair quality of carpentry construction and that are too small to use in fabricating carpentry with minimum joints or optimum joint arrangement. The rate should include frame cover mold, architrave, middle Push plates and bottom kick plates (stainless steel 316 -Norris 1mm the), all accessories and hardware, door handle, hinges 10cm height, door stopper, required fully tempered clear glass of 8mm thickness, and all other needed fittings according to specifications, drawings and Engineers' instructions. The work includes sanding sealer, prime coats, at finishing (paint or laminated). The contractor shall submit shop drawings for the approval of Engineer, prior to fabrication. The contractor shall refer to all relevant specifications and drawings prior to pricing and it shall be his responsibility to complete the works to the entire satisfaction of the Engineer at no additional cost. All samples shall be provided for Engineers' approval prior to purchase of material. The contractor shall check the measurement of openings physically at the site before fabricating the doors and windows. | [5 empty] | sb | Service B. | 0 | 5
| Rates shall include: (1) Supply, fabricate and installation of doors, windows, made out of approved quality timber Jak or equivalent to be finish as per the respective specification and drawings. (2) Hoisting, fixing in position and drilling. (3) Cutting and fitting around obstructions, Bedding and painting. (3) Nails, screws, glue, etc. (4) Flushed doors and frames shall be primed with sanding seller, two coats of putty. (5) Pressure impregnating, termite protecting, seasoning and planning all timber and sand papering to receive final finish. (6) Final Finish (7) All necessary ironmongery union / Yale or approved equivalent supplied by authorized dealer appointed by the manufacturer and approved by the Engineer and as per schedules. Samples of ironmongery should be submitted for approval prior to purchase. (8) Supplying and fixing steel frame and all the necessary installation and completion of the work duly instructed the engineer. The width of frame taking into account the thickness of the wall and thickness of the plastering or ceramic on both sides. (9) Fixing brass fixing screws, lock sets with 3 keys match with master key system. (10) Preservative treatment for back of door and door frame in contact with masonry or concrete. (11) All external windows and doors to be fully surrounded and bonded to adjacent structure with EPDM membranes to agreed details. | [5 empty] | st | Site | 0
1 | SECTION 08100 : Metal Doors and Frames
Steel Doors and frames
1.1 | Supply and install powder-coated flush steel doors, comprising of 1.25 mm thick hot-dipped galvanized steel sheet door leaf, 2 mm thick hot-dipped galvanized steel sheet door frame, including welding, fixing, fittings, accessories, hardware sets and all required as per drawings and specifications.
For main building
a. | SD01, 1.0x2.2m, Fire-rated 90 minutes | No. | 3 |  | 0 | a
1.2 | Supply and install powder-coated flush steel doors, comprising of 1.6 mm thick steel sheet door leaf primed with zinc phosphate primer and painted with semi-gloss oil paint hammer finish, 1.4 mm thick hot dipped galvanized steel sheet door frame, including welding, fixing, fittings, accessories, hardware sets and all required as per drawings and specifications.
a. | SD06, 0.7x1.3m, Fire-rated 45 minutes | No. | 1 |  | 0
|  | Carried forward |  |  | 0
Division 08: Openings
Item No. | Description | Unit | Quantity | Rate (USD) | Amount (USD)
| Brought forward from previous page |  |  |  | 0
2 | SECTION 08210- Wood Doors
2.1 | Supply and install solid core flush wood doors with high pressure laminated veneer ( fire rated wherever required), approved finish as per schedules, details and specifications including powder coated steel frames, welding, painting system, fixing, workmanship, accessories, 1mm stainless steel kick plate, 1mm stainless steel push plate , louver , vision panels ( fully tempered 8mm clear glass)wherever needed, complete as shown on drawings and door schedules. (including Hardware sets). the contractor shall provide sample and workshop drawings from specialist manfacturer for the site engineer approval.
a. | LD01, 1.0x2.2m, Fire-rated 45 minutes | No. | 2 |  | 0 | a
b. | LD03, 0.9x2.2m, with vision panel | No. | 3 |  | 0
c. | LD05, 1.2x2.2m, Fire-rated 45 minutes | No. | 21 |  | 0 | a
d. | LD08, 1.8x2.2m, Fire-rated 60 minutes, with vision panel | No. | 3 |  | 0 | a
e. | LD11, 1.0x2.2m, Fire-rated 45 minutes | No. | 1 |  | 0 | a
f. | LD16, 0.8x2.2m, Fire-rated 45 minutes | No. | 2 |  | 0 | a
g. | LD18, 1.4x2.2m, Fire-rated 60 minutes, with vision panel | No. | 1 |  | 0 | a
|  | Carried forward |  |  | 0
Division 08: Openings
Item No. | Description | Unit | Quantity | Rate (USD) | Amount (USD)
| Brought forward from previous page |  |  |  | 0
Notes:
Aluminum Doors and Windows
All aluminum profile, sections, ironmongeries and accessories of best quality and free from manufacturing defects to be completed and fixed in proper manner and according to the specifications and manufacturer instructions. Fabrication and fixing of all Aluminum components shall be carried out by experienced tradesman. All aluminum is to comply with the relevant European or equivalent Standard and is to have thermosetting polyester or acrylic urethane powder coating with cured film thickness not less than 0.04 mm. Aluminum profile and sections thickness shall not be less than 1.8mm. Joints shall be carried out by mechanical means and are to be properly riveted, halved and sealed and are to show no distortion and be waterproof. Shop drawings for Aluminum fabrication should be submitted to the Engineers for approval before the fabrication.
Rates shall include for: (1) Verify that wall surfaces and openings are ready to receive frames and are within tolerances. (2) All accessories, wheels, rails, hinges, handles, locks, brushes, rubber EPDM, and angles of windows must be the original and of high quality. (3) Rubber beadings, rollers, casement stays, barrel bolts, rings, casement fasteners and any other necessary to complete the work and as specified in detailed drawings. (4) Necessary silicon to fill gaps of approved color. (5) (60 - 80) microns powder coated Aluminum extrusions to be used in all Doors, windows and fanlights. (6) Scaffolding where needed. (7) Color of aluminum as per Engineer approval and matching the existing. (8) Windows dimensions more than 1m square must include internal aluminum profiles as dividers. (9) Glass and Glazing . (10) 4mm thick Aluminum composite sheet of approved color for paneling.(11) tempered glass to be used for Door, window glass panels (12) Door closer and stoper. (13) All samples to be approved by the Engineer. (14) All screws to be used for fabrication and fixing of Aluminum work shall be of approved quality stainless steel. (15) All Doors, windows and fanlight shall be fixed complete as per detail drawings. (16) Outside aluminum frames should be embedded with a mastic compound so as to make it impervious. (17) All windows and doors to be fully surrounded and bonded to adjacent structure with EPDM membranes to agreed details and should have double mastic seals / caulking to front and rear behind frames. (18) Should any defects appear in the works this is to be taken down and renewed to the Engineer satisfaction and any works disturbed in consequence must be made good at the Contractor's expense.
3 | SECTION 08100- Metal Doors and Frames
Aluminum Doors and Frames
3.1 | Supply, installation, and finishing of powder-coated aluminum leaf doors of approved color, comprising of 60 mm X 40 mm aluminum frames, with thickness not less than 1.5 mm, the leaf comprising of 4mm aluminum composite panel, durable high quality provided by first grade specialized local manufacturers, work includes all required stainless steel hardware, supplies, and accessories (frames, aluminum body profile, hinges, locks, handles, rubber, and etc), ventilation louvers where required, fixing doors accurately with anti-rust screws, sealing with silicone properly including all necessary related works, complete as shown on drawings, specifications and as per Engineers' instructions, and manufacturer recommendations.
a. | LD06, 0.8x2.2m | No. | 4 |  | 0
b. | LD07, 1.0x2.2m | No. | 18 |  | 0
a
a
|  | Carried forward |  |  | 0
Division 08: Openings
Item No. | Description | Unit | Quantity | Rate (USD) | Amount (USD)
| Brought forward from previous page |  |  |  | 0
4 | SECTION 08520- Aluminum Windows
4.1 | Supply and install sliding/fixed/hinged double-glazed aluminum windows (6 mm clear tempered glass, 12 mm spacer, 6 mm clear tempered glass), comprising powder-coated aluminum sections, including all necessary frames and fixation of the glass, sub frames, trims, mastic silicon sealant, locks, ironmongery, flashing, automatic shutters caulking, aluminum fly screens & insect screens, weather stripping, hardware and all accessories complete as per drawings, specifications, and Engineers' instructions.
* | Extruded aluminum system, non-thermally broken pre-tested and pre-engineered international system
* | the overall U-Value including the glass shall not exceed 2.9 W/m2/°K
a. | External windows, Sliding panels, double glazing | m2 | 82 |  | 0 | a
b. | External windows, Fixed panels, double glazing | m2 | 5 |  | 0 | a
c. | External windows, Sliding with fixed panel, double glazing | m2 | 30 |  | 0 | a
d. | External windows, Hinged with fixed panel, double glazing | m2 | 2 |  | 0 | a
a
|  | Carried to Summary |  |  | 0 | 0

## Div09
Division 9: Finishing | [6 empty] | d | Demolish | 0
Item No. | Description | Unit | Quantity | Rate (USD) | Amount (USD) |  | a | ARCH | 0
[7 empty] | s | STR | 0
| ** Quantities in this bill include Main Building and Service Building | [5 empty] | f | Façade | 0
[7 empty] | r | ROOF | 0
1 | SECTION 09220- Portland Cement Plaster | [5 empty] | sb | Service B. | 0
| Height of metal lath and metal angles used in plastering should be equal to the complete height of the wall or complete width in case of meeting of block walls with concrete. In case of meeting with lintels, metal lath should be on the complete length of lintels. | [5 empty] | st | Site | 0
1.1 | Internal plaster Supply and apply three coats cement and sand plastering wherever required, including metal lath,corner mesh, strip mesh, corner bead, metal lath sheet and plaster stop bead, all as per drawings and specifications.
a. | Plastering and to internal walls, ceilings for hospital building | m2 | 670 |  | 0 | a
1.2 | Repair plastering for internal walls and ceiling
a. | for main building | m2 | 1395 |  | 0 | a
st
|  | Carried forward |  |  | 0
Division 9: Finishing
Item No. | Description | Unit | Quantity | Rate (USD) | Amount (USD)
| Brought forward from previous page |  |  |  | 0
3 | SECTION 09300 - Tiles
All works must be according to drawings, specification and Engineers' instructions. Rates shall include: (1) Samples for approval and all the required tests. (2) Cleaning, mechanical polishing and pointing using grout. (3) Local marble must be Grade (A) free cracks and clay flaws. (4) Measuring the stockpiled quantities of tiles and obtaining the Engineer approval prior to shipment to the site. (5) Transporting and carefully handling the stored quantities to the site. (6) White cement to be used for porcelain tiles. (7) Plastic angle beads for ceramic wall tiles at the corners and top and sides of ceramic edges. (8) leveling layer wherever required as per site condition, cutting, fixing with polymer-based tile adhesive and grooves to be filled with anti-bacterial and anti-fungal type tile grout to match with existing color, all complete as per Engineers' instructions. (9) Tile bed using 1:3 cement sand mortar including surface preparation.
3.1 | Floor tiles
3.1.1 | Porcelain tiles Providing, laying, and finishing porcelain floor tiles of high-grade glaze porcelain floor tiles, the porcelain tiles, (conformed to European specification or equivalent) by using a mortar cement or special adhesive and to be approved by the Engineer, and tiles water absorption rate shall be less than 0.5 according to ASTM C373 and PTCA. The work includes, supplying and laying sand bed, installing tiles in proper technical way on a leveled layer of cement mortar (1cement: 3sand) not less than 2cm thick and special adhesive, grouting and finishing breaks properly, curing with water properly for not less than seven days. And all necessary related works to finish the work according to the specifications, technical rules, and the Engineers' instructions.
a. | size (400x400)mm , thickness not less than 9mm | m2 | 85 |  | 0 | a |  |  |  | 5
b. | size (600x600)mm , thickness not less than 9mm | m2 | 330 |  | 0 | a
3.1.2 | Full comprehensive repairs to the existing flooring, skirting including but not limited to replacing broken tiles, adding missing tiles of size and shape to match the existing, crystallization, polishing, grouting and cleaning and all necessary works complete as per specifications, drawings and engineer's instructions and approval
For replacing broken parts and adding missing parts, the quantity is assumed not to exceed 15%, if the quantity exceeds 15%, the price of the item shall be as the price of the same new tile
a. | Existing staircase marble treads and risers | lm | 115 |  | 0
b. | Existing staircase marble landing | m2 | 20 |  | 0
c. | Existing marble skirting | lm | 115 |  | 0
|  | Carried forward |  |  | 0
Division 9: Finishing
Item No. | Description | Unit | Quantity | Rate (USD) | Amount (USD)
| Brought forward from previous page |  |  |  | 0
3.2 | Walls Tiles
Note: All works of plastering under any kind of walls tiles are included within the price of the tiles items.
3.2.1 | Ceramic wall tiles Supply, installation, and finishing of high-grade glaze Ceramic wall tiles, the tiles material to (conformed European standard or equivalent and of approved make) in all colors, shades except burgundy, bottle green, black of any size as approved by Engineer-in-Charge, in skirting, risers of steps and dados, over 12 mm thick bed of cement mortar 1:3 (1 cement: 3 coarse sand) and jointing with grey cement slurry @ 3.3kg per sqm, including pointing in white cement mixed with pigment of matching shade complete. The work includes all related works to finish the work according to the specifications, technical rules and the Engineers' instructions
a. | Size (400x400)mm, thickness not less than 8mm | m2 | 525 |  | 0 | a
a
|  | Carried forward |  |  | 0
Division 9: Finishing
Item No. | Description | Unit | Quantity | Rate (USD) | Amount (USD)
| Brought forward from previous page |  |  |  | 0
3.3 | SKIRTING:
Item includes all surface preparation work such as cleaning and scrubbing, patching defective areas, ..etc. as per the specifications. Item also include supply and install of mortar layer with thickness needed for leveling skirting with required projection over walls. All as per related specifications.
3.3.1 | Porcelain Skirting Supply, installation, and finishing of 80 mm height, (conformed to European standard or equivalent) and to be approved by the Engineer, glaze porcelain skirts to match the selected porcelain tiles. The work includes preparing surfaces , installing tiles accurately on a layer of cement-based glue adhesive, grouting and finishing joints properly using cement based proprietary grout, and all necessary related works to finish the work according to the specifications, technical rules, and the Engineers' instructions
a. | for hospital building | L.m | 265 |  | 0 | a
4 | SECTION 09500 - Acoustical Suspended Ceilings
4.1 | Mineral fiber suspended ceilings Providing fabricating and fixing of modular grid type false ceiling at all height as directed of 600 mm x 600 mm x 15 mm thick, mineral fiber acoustical tegular ceiling tiles of approved texture, design and pattern and of type classic lite RH- 99 laid on prelude XL exposed grid system with 9 mm wide T section flanges color white. The tiles should have Humidity Resistance (RH) of 99%, Light Reflectance > 85%, Thermal Conductivity k = 0.052 - 0.057 w/m K, Fire Performance as per (BS 476 pt. - 6 and7) in true horizontal level suspended on interlocking T-Grid of hot dipped all round galvanized iron sections of 0.33 mm thick (galvanized @120 gsm). The framework comprises of main runner of size 15 x 42 x 3000 mm spaced at 600 mm centers securely fixed to the structural soffit by approved hangers at 1200 mm maximum centers. Hanger (GI wire) to be fixed by approved roof plug, level adjusters and screws etc. The last hanger at the end of each main runner should not be greater than 450 from the adjacent wall. Flush fitting 600 mm long cross tees (with double stitching) to be interlocked between main runner at 600mm center from 600x600mm modules. Cut cross tees longer than 600mm to be supported independently 600mm x 600 mm modules to be formed by fitting 600 mm long flush fitting cross tees of size 15 x 42 x 600mm centrally between the 600 mm cross tees. Perimeter trim to be wall angle of size 19 x 19 x 3000mm secured to walls at 450 mm maximum centers. The work shall be carried out as per specifications, drawings and as per directions of the engineer-in-charge. The price includes all necessary related works to get the work completely finished according to the technical rules, drawings, and as instructed by the engineer. | m2 | 445 |  | 0 | a
|  | Carried forward |  |  | 0
Division 9: Finishing
Item No. | Description | Unit | Quantity | Rate (USD) | Amount (USD)
| Brought forward from previous page |  |  |  | 0
4.2 | Gypsum board ceiling with emulsion paint Supply and install 12.5 mm thick suspended ceiling gypsum board painted with emulsion paint, price to include channel, steel anchor, fixing, painting system , accessories and all required as per drawings, specifications and approval of the Engineer. | m2 | 215 |  | 0 | a
4.3 | Aluminum ceiling tiles Supply and install aluminum ceiling tiles 600mmx600mmx1mm thickness,at wet area including metal subframes and furring, accessories, flashing and trims, fasteners and sealant, workmanship, fabrication and fixation to Engineer's instructions. | m2 | 88 |  | 0 | a
5 | SECTION 09650 -Resilient flooring
* | Notes:
All resilient flooring sheets shall be anti bacterial type.
The Contractor shall provide the manufacturer's catlouges for the Engineer's Approval, catalouges shall include cutting and insatallation methods and all required details
Cleaning of existing flooring to be ready to recieve the new flooring sheets
The installer to maintain the zero level during and after installation using Self Leveling.
5.1 | Vinyl sheets Supply and install vinyl sheets of 2mm thickness,fixed over existing tiles, heavy duty anti slip,with 100 mm full cove former skirting, moisture and fire resistant,works include maintinance of the exisiting tiles or replacement of tiles in limited areas where required to accomodate the MEP installation, complete as per drawings, specifications and manufacturer's recommendations.
a
a. | Vinyl sheets as per drawings | m2 | 360 |  | 0 | a
a
|  | Carried forward |  |  | 0
Division 9: Finishing
Item No. | Description | Unit | Quantity | Rate (USD) | Amount (USD)
| Brought forward from previous page |  |  |  | 0
6 | SECTION 09900 - Painting
Note:
Unit rates shall include: (1) All the painting materials used should be approved and tested by approved local laboratory and have the final approved from the Engineer. (2) Supplying of all materials, scaffolding, workmanship and tools and whatever else needed. (3) clean surface to receive the painting (4) Any taping and covering to protect horizontal and vertical items and surfaces. (5) Applying wall skim coat to smooth the surface. (6) Cleaning and polish floors, doors, fittings, furniture and windows, etc. Upon completion. (7) Painting door and window's reveals and shall not measure separately. (8) Costs of sampling and testing as required and according to technical specifications and work requirement. (9) Painting should not start until all tiling, skirting, sanitary, valves, electric wiring, anchoring, patching and making good of all works are completed and approved.
6.1 | Emulsion paint Supply and apply emulsion paint, Price shall include surface preparation of existing surface to receive the new paint, priming, and two coats of putty, color to be approved by the Engineer and all according to drawings and specifications.
a. | for hospital building ceiling | m2 | 20 |  | 0 | a
6.2 | Acrylic paint Supply and apply internal high acrylic semi matt paint , Price shall include surface preparation of existing surface to receive new paint, priming, and two coats of putty, complete as shown on drawings and as per specifications and the engineer's instructions.
a. | for hospital building walls | m2 | 2065 |  | 0 | a
|  | Carried to Summary |  |  | 0 | 0

## Div10
Division 10: Specialties | [6 empty] | d | Demolish | 0
Item No. | Description | Unit | Quantity | Rate (USD) | Amount (USD) |  | a | ARCH | 0
[7 empty] | s | STR | 0
1 | SECTION 10260 - Wall and Corner Guard | [5 empty] | f | Façade | 0
1.1 | Supply and install surface mounted crash rail of aluminum clips covered by Acrovyn high impact acrylic vinyl at 90cm height, size 150 x 35.4mm with continuous Alum retainer with cushion for added shock absorption, including fixing, fittings , accessories and all required to complete the job as per drawings and the manufacturer's recommendations. | L.M | 115 |  | 0 | a | r | ROOF | 0
[7 empty] | sb | Service B. | 0
2 | SECTION 10440 - Signage
2.1 | Supply and install signage system, comprising of lazer printed text in both Arabic and English languages on high quality plastic of 3mm thick, complete with all required mounting decvices, all as specified and indicated. Contractor to provide sample and workshop drawings claryfing , fixing method , location , sizes ...etc , to be approved by the Engineer.
2.1.1 | Signs fixed on walls and doors
a. | SI-01 75mmx150mm | No. | 7 |  | 0 | a
b. | SI-03, 150mmx150mm | No. | 23 |  | 0 | a
c. | SI05, 450mmx600mm | No. | 2 |  | 0 | a
2.1.2 | Ceiling mounted signs
a. | SI-02 75mmx150mm | No. | 32 |  | 0 | a
b. | SI-04, 150mmx450mm | No. | 3 |  | 0 | a
|  | Carried forward |  |  | 0
Division 10: Specialties
Item No. | Description | Unit | Quantity | Rate (USD) | Amount (USD)
| Brought forward from previous page |  |  |  | 0
3 | SECTION 10800- Toilet, Bath and Laundry Specialties
3.1 | Supply, install, & fix the following toilet accessories of stainless steel Grade 304, satin finish & mirrors, all according to drawings, specification and Engineer's instructions. Contractor to provide samples to be approved by the Engineer for quality, finish and size:
a. | Horizontal grab bar, AX01 | No. | 36 |  | 0 | a
b. | Vertical grab bar, AX02 | No. | 18 |  | 0 | a
c. | Sanitary napkin disposal, AX03 | No. | 20 |  | 0 | a
d. | Toilet paper disposal, AX04 | No. | 20 |  | 0 | a
e. | Soap Dispenser, AX05 | No. | 22 |  | 0 | a
f. | Paper towel dispenser, AX06 | No. | 22 |  | 0 | a
g. | Robe hook, AX08 | No. | 20 |  | 0 | a
h. | Waste bin, AX09 | No. | 42 |  | 0 | a
i. | Shower seat, AX10 | No. | 18 |  | 0 | a
3.2 | Mirrors 6mm thick Mirrors, on and including 18mm Lamiwood edge with 2mm solid colour pvc, 3mm x 3mm bevelled edges and P.V.C back bonded safety film, including all necessary fixings, fittings and accessories, complete as shown on drawing and specifications
a. | Mirror 900mmx600mm, AX07 | No. | 20 |  | 0 | a
|  | Carried to Summary |  |  | 0 | 0

## Div15
Division 15: Mechanical Works
Item No. | Description | Unit | Quantity | Rate (USD) | Amount (USD)
Supply. Install, Test and Commission the following items in accordance with the Specifications, Drawings, Preambles and Engineer's approval
1 | Section (1) - HVAC System
Ventilation and Air Conditioning
1.1 | Section 15810
1.1.1 | Supply, install, test and commission galvanized sheet steel duct with 22-gauge thickness and G90, flange method connection for all ducts connections, including all supports and hangers, brackets, sealant, volume dampers, and all necessary accessories to complete the job in perfect running order, in accordance with drawings, specifications, and the approval of the engineer. | m2 | 470 |  | 0
1.1.2 | Supply, install, test and commission thermal insulation for duct work of rigid glass fiber, with a thickness of 24 mm and density of 24 Kg/m3, including aluminium vapor barrier thickness and all necessary accessories to complete the job in perfect running order, in accordance with drawings, specifications, and the approval of the engineer. | m2 | 200 |  | 0
1.2 | Section 15850
1.2.1 | Supply, install, test and commission air distribution terminals, made of extruded aluminum complete with frame, fixing trim, air directional vanes, dampers, the plenum box and insulated flexible ducts etc.… as specified and shown on drawings
1.2.1.1 | 4-Way Square Ceiling Diffusers (Supply)
a | SD-1, (150x150)mm | No. | 24 |  | 0
b | SD-2, (230x230)mm | No. | 4 |  | 0
|  | Carried forward |  |  | 0
Division 15: Mechanical Works
Item No. | Description | Unit | Quantity | Rate (USD) | Amount (USD)
| Brought forward from previous page | . |  |  | 0
0
1.2.1.2 | Exhaust Air Grill |  |  |  | 0
a | EG-1, (150x150)mm | No. | 23 |  | 0
b | EG-2, (200x200)mm | No. | 1 |  | 0
c | EG-3, (250x250)mm | No. | 1 |  | 0
1.2.1.3 | Door Grill |  |  |  | 0
a | DG, (300x250)mm | No. | 2 |  | 0
1.3 | Section 15837 |  |  |  | 0
1.3.1 | Supply, install, test and commission ventilation exhaust and fresh fan complete with flexible connections, wire mesh, counter flanges, anti vibration mountings, control panel, supports, back draft damper, electrical connections (MCC), wiring off-on nearby isolating weather proof switches, as shown on drawings and as specified. |  |  |  | 0
a | EXF-13, Centerfugal Inline Direct Drive, Air flow 350 L/ s, 120 Pa | No. | 1 |  | 0
b | EXF-17, Centerfugal Inline Direct Drive, Air flow 605 L/ s, 140 Pa | No. | 1 |  | 0
|  | Carried forward |  |  | 0
Division 15: Mechanical Works
Item No. | Description | Unit | Quantity | Rate (USD) | Amount (USD)
| Brought forward from previous page | . |  |  | 0
15.14 | Section 15100
15.14.1 | Supply, install, test, commission and maintain Heating water pipes, seamless black steel to ASTM A53 Sch. 40, for pipes running above false ceiling, in shafts, on roof, including flexible connections, automatic air vents, isolation valve, regulating valve, brackets, hangers, aluminium cladding 0.7mm to external pipes and all necessary accessories, including pipe protection and thermal insulation type (sectional) with thickness 5 cm and density at least 40 kg/m3, to complete the job in perfect condition, as specified and shown on drawings.
a | Ø 20 mm dia. | L.M | 572 |  | 0
b | Ø 25 mm dia. | L.M | 85 |  | 0
c | Ø 32 mm dia. | L.M | 25 |  | 0
|  | Carried forward |  |  | 0
Division 15: Mechanical Works
Item No. | Description | Unit | Quantity | Rate (USD) | Amount (USD)
| Brought forward from previous page | . |  |  | 0
15.26 | Section 15670
15.26.1 | Supply, install, test, and commission heating radiator, steel type, with all the necessary pieces, trims, tees, bolts, back-and-forth switches, vents, isolation valve, regulating valve, plugs, rails, fixation, and heat-resistant. The price includes the provision and installation of (Thermostatic Head), each radiator must control the room temperature, and the contractor must obtain the approval of the supervising engineer before installing it, the standard specifications according to which the manufacturer is manufactured must also be prominently engraved on the radiator section.
a | R1.0 | No. | 6 |  | 0
b | R0.6 | No. | 3 |  | 0
c | R0.7 | No. | 13 |  | 0
d | R0.8 | No. | 1 |  | 0
e | R1.1 | No. | 1 |  | 0
f | R1.2 | No. | 2 |  | 0
f | R1.3 | No. | 2 |  | 0
|  | Carried forward |  |  | 0
Division 15: Mechanical Works
Item No. | Description | Unit | Quantity | Rate (USD) | Amount (USD)
| Brought forward from previous page | . |  |  | 0
Section (2) - Plumbing System
2 | Domestic Water System
2.1 | Section 15020
2.1.1 | Supply, install, test and commission PPR-CT pipes class 2 (S-3.2) complying with (EN ISO 15874) or SDR 7.4 complying with DIN 8077, DIN 8078 for cold water supply for pipes runs in ceiling voids, shafts, Internally exposed and exposed outside, for exposed pipes to the sun, shall be insulated by closed cell rubber insulation 6 mm thickness insulation and protected by smooth aluminum cladding of 1 mm thickness, the work includes providing and installing saddles, screws, nails, hardware fixing, jointing, materials cutting holes, chasing in brickwork, all fittings, Isolating valves, sleeves, supports, clips etc., accessories (Pipes, couplings, elbows, valves, stopcocks, clips, .etc.) of high quality and heavy-duty. In addition to fixing pipes on walls and roofs properly with clips, repairing any damage caused during the installation process, and all necessary to complete works specified and shown on drawings:
a | Diam. 20 mm | Lm | 79 |  | 0
b | Diam. 25 mm | Lm | 68 |  | 0
c | Diam. 32 mm | Lm | 210 |  | 0
d | Diam. 40 mm | Lm | 44 |  | 0
e | Diam. 50 mm | Lm | 31 |  | 0
f | Diam. 63 mm | Lm | 6 |  | 0
2.1.2 | Supply, install, test and commission PPR-CT pipes class 2 (S-3.2) complying with (EN ISO 15874) or SDR 7.4 complying with DIN 8077, DIN 8078) for hot water supply/return with insulation for pipes runs in ceiling voids, shafts, Internally exposed and exposed outside, for exposed pipes to the sun, shall be insulated by closed cell rubber insulation 6 mm thickness insulation and protected by smooth aluminum cladding of 1 mm thickness, the work includes providing and installing saddles, screws, nails, hardware fixing, jointing, materials cutting holes, chasing in brickwork, all fittings, Isolating valves, sleeves, supports, clips etc., accessories (Pipes, couplings, elbows, valves, stopcocks, clips, .etc.) of high quality and heavy-duty. In addition to fixing pipes on walls and roofs properly with clips, repairing any damage caused during the installation process, and all necessary to complete works specified and shown on drawings:
a | Diam. 20 mm | Lm | 40 |  | 0
b | Diam. 25 mm | Lm | 110 |  | 0
c | Diam. 32 mm | Lm | 205 |  | 0
d | Diam. 40 mm | Lm | 48 |  | 0
e | Diam. 50 mm | Lm | 28 |  | 0
f | Diam. 63 mm | Lm | 6 |  | 0
|  | Carried forward |  |  | 0
Division 15: Mechanical Works
Item No. | Description | Unit | Quantity | Rate (USD) | Amount (USD)
| Brought forward from previous page | . |  |  | 0
2.2 | Section 15430
2.2.1 | Supply, install, test and commission plumbing fixtures and related mixers, the price shall include all accessories (angle valves, wall washers, gaskets, screws and inserts, angles, supports, wall connectors, smell preventers, sealant and consumables), flexible pipes for drain, satinless steel flexible at all counter sinks, execution of related civil works including material, the installation of saving devices, hand over the installations in an operational and clean manner to the satisfaction of the Engineer and as per schedules and specifications. Plumbing fixtures types, colors and models to be coordinated with the Architectural team.
a | Wall mounted wash basin & related Mixer, and waste drain | No | 20 |  | 0
c | Shower mixer, Shower uncia & drain | No | 20 |  | 0
d | Wall mounted suspended toilet seat , seat cover with arm, Embedded flush tank with required brackets, & Stainless steel push button of flush cover | No | 20 |  | 0
f | Stainless steel trigger Hand spray with wall mounted hook | No | 20 |  | 0
|  | Carried forward |  |  | 0
Division 15: Mechanical Works
Item No. | Description | Unit | Quantity | Rate (USD) | Amount (USD)
| Brought forward from previous page | . |  |  | 0
3 | Drainage System
3.1 | Section 15150
Above Ground Drainage
3.1.1 | Supply, install, test and commission above ground soil, waste overflow, and venting, solvent weld UPVC pipe class 4, for all floors, vent pipe and rain water pipes, complete with fittings, supports, brackets, hangers, clips, sleeves, and all necessary accessories to complete the installations as specified and shown on drawings:
a | Diam.50 mm | Lm | 120 |  | 0
b | Diam. 80 mm | Lm | 81 |  | 0
c | Diam. 110 mm | Lm | 95 |  | 0
d | Diam. 160 mm | Lm | 8 |  | 0
3.2 | Section 15155
3.2.1 | Supply, install, test and commission Stainless steel floor drains complete with Stainless steel covers (cover to be coordinated with tiling), strainers, trap and all necessary accessories in accordance with specifications and drawings.
a | Ref. Floor Drain (FD) 80mm dia. | No. | 29 |  | 0
3.3 | Section 15155
3.2.1 | Supply, install, test and commission Stainless steel shower drains complete with Stainless steel covers (cover to be coordinated with tiling), strainers, trap and all necessary accessories in accordance with specifications and drawings.
a | Ref. Shower Drain (SD) 80mm dia. | No. | 2 |  | 0
|  | Carried forward |  |  | 0
Division 15: Mechanical Works
Item No. | Description | Unit | Quantity | Rate (USD) | Amount (USD)
| Brought forward from previous page | . |  |  | 0
4 | Section (3) - Fire Fighting System
4.1 | Section 15520
4.1.1 | Supply, install, test, commission of portable fire extinguisher, include all necessary accessories as specified and shown on drawings.
a | Type (CO2) 4.5kg | No. | 3 |  | 0
b | Type (POWDER) 6kg | No. | 1 |  | 0
4.1.2 | Supply, install, test and commission fire hose cabinets (Stainless steel Doors) recessed in the wall, complete with swivel bracket, manual hose nozzle, pipe connection, 30 meters long Ø25mm, hose in rubber non kickable type with fire extinguisher ABC powder 6kg and all necessary accessories as specified and shown on drawings.
a | HRC-01 | No. | 2 |  | 0
4.1.3 | Supply, install, test and commission black seamless steel pipes schedule 40, as specified including protection for pipes which run under ground and above ground inside the building, Jointing between pipes and fittings shall be by grooving, including flexible connections, end caps, hangers, brackets and automatic air vents all as specified. Price shall include all civil works as specified and as shown on drawings.
a | Dia. 40 mm | Lm | 44 |  | 0
b | Dia. 50 mm | Lm | 3 |  | 0
|  | Carried forward |  |  | 0
Division 15: Mechanical Works
Item No. | Description | Unit | Quantity | Rate (USD) | Amount (USD)
| Brought forward from previous page | . |  |  | 0
6 | Section (5) - Medical Gases
6.1 | Section 15480
6.1.1 | Supply, install, test & commission Copper pipe degreased, light gauge, solid drawn, phosphorous de-oxidized, non-arsenical tube conforming to BS-EN 1057:1996 (formerly BS 2871, Part 1, Table 'X'). Suitable for use with BS 864 Part 2 fittings, installed, connected, and tested complete with allowance for HKD type concrete inserts with drop rod and munsen ring brackets, spaced to HTM 02-01 recommendations, isolating valve, In-line valve lockable quarter-turn Shut off valve, assorted fittings, solder and identification tape as specified and shown on drawings.
d | Dia. 28mm | Lm | 80 |  | 0
e | Dia. 22 mm | Lm | 240 |  | 0
f | Dia. 15 mm | Lm | 550 |  | 0
g | Dia. 12 mm | Lm | 100 |  | 0
|  | Carried forward |  |  | 0
Division 15: Mechanical Works
Item No. | Description | Unit | Quantity | Rate (USD) | Amount (USD)
| Brought forward from previous page | . |  |  | 0
6.1.2 | Supply, install, test and commission Emergency isolation valve complying to HTM 0201 and C11, housed within a Lockable box with “break glass” safety Feature emergency access, including NIST Connection ports, secondary alarm and all required accessories, as specified and shown on drawings.
a | AVSU-1st-01(3 Outlet) | No. | 1 |  | 0
b | AVSU-1st-02(3 Outlet) | No. | 1 |  | 0
6.1.7 | Supply, install, test & commission medical gas terminal units installed, connected, and tested complete with plastic fascia plate, 150mm stub pipe and all required accessories, for all types of the bed head unit referring to the medical BOQ, as specified and shown on drawings.
a | Oxygen (O2) Outlet | No. | 34 |  | 0
b | Vacuum (V) Outlet | No. | 34 |  | 0
c | Medical Air (MA4) Outlet | No. | 34 |  | 0
|  | Carried to Summary |  |  | 0

## Div16
Division 16: Electrical Works
Item No. | Description | Unit | Quantity | Rate (USD) | Amount (USD)
1 | Section 16445-Distribution Boards
Supply, install, connect and commission distribution boards including enclosure, main isolator or main incoming circuit nreaker, miniature outgoing circuit breakers, contactors, busbars and other needed accessories, as per specifications and shown on the drawings.
a. | DB.FL | No. | 1 |  | 0
b. | EDB.FL | No. | 1 |  | 0
c. | UDB.F | No. | 1 |  | 0
d. | EDBL.FL | No. | 1 |  | 0
e. | DB.FR | No. | 1 |  | 0
f. | EDBL.FR | No. | 1 |  | 0
g. | EDB.FR | No. | 1 |  | 0
h. | DBM.FR | No. | 1 |  | 0
|  | Carried forward |  |  | 0
Division 16: Electrical Works
Item No. | Description | Unit | Quantity | Rate (USD) | Amount (USD)
| Brought forward from previous page |  |  |  | 0
2 | Section 16122-Feeding Power Cables
Supply, install, test and commission the following power cables as specified and shown on the drawings. The cables shall be installed on cable trays, cable ladders, trenches or in UPVC conduits. The works include the conduits, Manholes ,galvanized cable trays mounted horizontally or vertically, cable ladders mounted in electrical shafts , electrical trench and UPVC conduits as shown on the electrical drawings with concrete encasement at road crossing areas.including all required equipment and all civil works related to the installation and as per specifications and shown on the drawings.
a. | (5x16 mm2 CU/PVC/LS0H/PVC) | L.M | 30 |  | 0
b. | (4x25 mm2 CU/PVC/LS0H + 1X16 mm2 PVC/ECC) | L.M | 75 |  | 0
c. | (5x10 mm2 CU/PVC/LS0H/PVC) | L.M | 70 |  | 0
d. | (3x10 mm2 CU/PVC/LS0H/PVC) | L.M | 75 |  | 0
3 | Section 16140 - Wiring Devices
3.1 | Socket Outlets
Supply, install, test and connect the following socket outlets including wires, cables, PVC or galvanized conduits and all accessories up to distribution board as per drawings and specifications.Price shall include any opening in the wall or in the tiles and reinstate the wall and floor as per the existing condition and as per specifications and shown on the drawings.
a. | 13A, 230V single phase, 3-PIN socket outlet with switch. | No. | 124 |  | 0
b. | 13A, 230V single phase, 3-PIN single socket outlet with switch, Weather proof. | No. | 2 |  | 0
c. | 13A, 230V single phase, 3-PIN double socket outlet with switch. | No. | 5 |  | 0
d. | 13A, 230V single phase, 3-PIN double socket outlet with switch, Weather proof. | No. | 5 |  | 0
e. | 13A, 230V single phase, 3-PIN double socket outlet with switch, desk mounted. | No. | 4 |  | 0
f. | 32A, 230V single phase, 3-PIN industrial socket outlet. | No. | 1 |  | 0
g. | Connection unit with flex outlet wall mounted for medical equipment | No. | 1 |  | 0
|  | Carried forward |  |  | 0
Division 16: Electrical Works
Item No. | Description | Unit | Quantity | Rate (USD) | Amount (USD)
| Brought forward from previous page |  |  |  | 0
3.2 | Power Point for Medical Equipment's
Supply, install, test and connect the following power points for medical equipment's & BHU's , including wires, cables, PVC or galvanized conduits and all accessories up to equipment's from electrical panel to the unit as shown as per drawings and specifications. Price shall include any opening in the wall or in the tiles and reinstate the wall and floor as per the existing condition.
a. | Power point for W-BHU. Fed from Normal | No. | 34 |  | 0
b. | Power point for W-BHU. Fed from Emergency | No. | 34 |  | 0
c. | Power point for EX-BHU. Fed from Normal | No. | 1 |  | 0
d. | Power point for EX-BHU. Fed from Emergency | No. | 1 |  | 0
3.3 | Disconnect Switch Isolator
Supply, install, test and commission the following heavy duty disconnect switch isolators as specified and shown on the drawings. The disconnect switch should suit the equipment rating, single phase for single phase equipment, and 3 phase for 3 phase equipment. The outdoor isolators and inside mechanical rooms shall have waterproof enclosure with IP=65 with all needed conduits. Price shall include wires / cables up to 4mm2 and accessories and all needed cable trays and ladders, any opening in the wall or in the tiles and reinstate the wall and floor as per the existing condition.
a. | Disconnect switch isolator,1 phase rating 20A, IP-65 | No. | 2 |  | 0
b. | Disconnect switch isolator,1 phase rating 25A, IP-65 | No. | 1 |  | 0
4 | Section 16510 - Lighting Points
Supply, install, test and connect and commission lighting points including wires, cables, conduits, lighting switches, ceiling rose and all needed to complete the job as per specifications ,drawings & engineer's instructions.
a. | Internal lighting point. | No. | 138 |  | 0
b. | Internal lighting point exit signs | No. | 8 |  | 0
c. | Internal lighting point in Bedhead unit | No. | 34 |  | 0
5 | Section 16510 - Lighting Fixtures
5.1 | Internal Lighting Fixtures
Supply, install, test, connect and commission the following internal lighting fixtures as per drawings and specifications.
a. | TYPE (L2) | No. | 54 |  | 0
b. | TYPE (L2EM) | No. | 27 |  | 0
c. | TYPE (L3) | No. | 6 |  | 0
d. | TYPE (L3EM) | No. | 4 |  | 0
e. | TYPE (L4) | No. | 2 |  | 0
f. | TYPE (L4EM) | No. | 1 |  | 0
g. | TYPE (L5). | No. | 3 |  | 0
|  | Carried forward |  |  | 0
Division 16: Electrical Works
Item No. | Description | Unit | Quantity | Rate (USD) | Amount (USD)
| Brought forward from previous page |  |  |  | 0
h. | TYPE (L5EM) | No. | 21 |  | 0
i. | TYPE (L6) | No. | 5 |  | 0
j. | TYPE (L6EM) | No. | 2 |  | 0
k. | TYPE (L7). | No. | 4 |  | 0
l. | TYPE (L7EM) | No. | 2 |  | 0
m. | TYPE (L9). | No. | 3 |  | 0
n. | TYPE (L9EM) | No. | 3 |  | 0
o. | TYPE (L14) | No. | 1 |  | 0
5.2 | Exit Signs & Emergency kit Fixtures
Supply, install, test, connect and commission the following exit signs & emergency kit fixtures as per drawings and specifications. Wires shall be fire rated.
a. | TYPE (E1). | No. | 4 |  | 0
b. | TYPE (E2). | No. | 4 |  | 0
6 | Section 16710- Fire Alarm System
Supply, install, test and commission addressable type fire alarm equipment in accordance with NFPA 72/BS5839 and NFPA 70/BS7671 inclusive of all equipment and accessories, batteries, charger, internal conductors and/or cables, switches, power supply, Automatic telephone dialer, the job shall include but not limited to installation, termination, commissioning and testing and any job required to complete the job according to civil defence requirements, drawings, Section 16710 and other related sections of specification and engineer's instructions, the price shall include fire alarm system points with all needed fire rated cables 950 C` withstand for minimum two hours, in addition to PVC conduits and all needed accessories from FACP till all devices and detectors and as per specifications and drawings.
a. | Addressable Photoelectric Smoke detector. | No. | 42 |  | 0
b. | Addressable Photoelectric Smoke detector, wall mounted. | No. | 1 |  | 0
c. | Addressable Photoelectric Smoke detector, to be installed above false ceiling. | No. | 60 |  | 0
d. | 24V DC Conventional Indoor Flasher. | No. | 6 |  | 0
e. | Addressable Zone Module. | No. | 4 |  | 0
f. | Manual call/ Break Glass point at 1200mm FFL. | No. | 5 |  | 0
g. | Short circuit isolator. | No. | 8 |  | 0
|  | Carried forward |  |  | 0
Division 16: Electrical Works
Item No. | Description | Unit | Quantity | Rate (USD) | Amount (USD)
| Brought forward from previous page |  |  |  | 0
7 | Section 16690 - Structure Cabling System
The item unit rate shall include all PVC and/or galvanized steel conduits/ trunking, telephone and/or data RJ-45 socket outlet and/or socket outlet RJ-45 for CCTV camera point on wall, ceiling, or counter mounted as indicated, galvanized steel wall and/or floor mounting box, UTP CAT6 cable through 25mm PVC conduit with pull boxes from the appropriate patch panel (s) to the served data points , price shall include telecome manholes and all other accessories needed as shown on the drawings and as called for in the specifications and in accordance with relevant codes of practice and highest prevailing engineering standard.Price shall include any opening in the wall or in the tiles and reinstate the wall and floor as per the existing condition
Note; Outlets face plate color, material shape and type of finishes shall be as per the Engineer approval, back boxes of the outlets shall be coordinated with the approved type /model of the outlets intended to be used on this project, and must be included in the price of the point.
Telephone and/or Data Outlets shall be measured in Number (No.).
Note; where telephone or data socket outlets installed in a multi-compartments trunks or in floor box; the outlets, conduits and cabling to the nearest distribution floor patch panel shall be included in this item, multi-comportments trunks and floor box shall be priced under separate item
Note; The rack size include the patch panels & switches needed for all IP systems
a. | 1 x RJ45 wall mounted Data outlet complete with 1x4P UTP CAT6 cables and conduits from outlet to related patching connectivity. | No. | 56 |  | 0
b. | Ditto but Disk Mounted | No. | 4 |  | 0
c. | Single RJ45 for CCTV camera and door control panel ceiling/wall mounted (outlet, cabling and patching are include in the structure cable system Job). | No. | 7 |  | 0
d. | Data Points for BHU's, PNDT's, WAC's & S.C.Ps with 1x4P UTP CAT6 cable | No. | 70 |  | 0
e. | 1.0m UTP Cat6 Patch cord | No. | 137 |  | 0
f. | 4X4 UTP CAT6 cable Backbone cable between cabinets | MR | 60 |  | 0
g. | 48 port UTP CAT6 patch panel | No. | 2 |  | 0
h. | 24 port UTP CAT6 patch panel | No. | 1 |  | 0
i. | 30U free stand data cabinet with accessories | No. | 1 |  | 0
j. | 48 port UTP CAT6 switch panel | No. | 2 |  | 0
k. | 24 port UTP CAT6 POE switch panel | No. | 1 |  | 0
|  | Carried Forward |  |  | 0
Division 16: Electrical Works
Item No. | Description | Unit | Quantity | Rate (USD) | Amount (USD)
| Brought forward from previous page |  |  |  | 0
8 | Section 16729 - IP based CCTV System
Supply, install, terminate, test and commission IP based CCTV system, the job shall include empty PVC conduits, pulling rope, pull boxes, fittings, civil works and any required job needed to complete the job needed to complete the job according to section 16729 and other related sections of specifications, drawings and Engineer's instructions. Note the wiring from cameras , connection to patch panel and patch panel as well as all switches shall be carried by Structure Cable System.
a. | Fixed in ceiling recessed/Surface mounted dome networkable camera day night varifocal 3.8-13mm , 1/2.7" CMOS image sensor as specified in Section 16729. | No. | 7 |  | 0
9 | Section 16735 - Voice Evacuation System
The item unit rate shall include all PVC conduits, fire rated wires from the panels to the served speaker, galvanized steel trunking, complete with all in and out cables up to the served speaker as per the manufacturer’s recommendations, Interface to fire alarm system and all other accessories needed in accordance to the relevant codes of practice and highest prevailing engineering standards.
a. | 6W loudspeaker with tap changer transformer, Recessed in false ceiling, IP20 | No. | 13 |  | 0
b. | 6W loudspeaker with tap-changing transformer, Recessed in false ceiling, IP-44 | No. | 2 |  | 0
c. | 6W loudspeaker with tap-changing transformer, surface mounted. IP-40 | No. | 2 |  | 0
10 | Section 16790 - Nurse Call System
Supply, installation, Testing & Commissioning of following Nurse Call system Components including connection wires, cables, conduits, power source where needed, galvanized trunks, complete in all respects with all necessary accessories as required for completion & successful operation of the system as per drawings, medical specialist requirements, relevant standard & technical specifications of the tender.Price shall include any opening in the wall or in the tiles and reinstate the wall and floor as per the existing condition
a. | Over Door Light | No. | 36 |  | 0
b. | Toilet Set Points (Including Emergency Ceiling Suspended Pull Cord, Toilet Emergency Push Button - bath station, Toilet reset unit with emergency pull button) | No. | 18 |  | 0
c. | Staff to staff emergency call | No. | 1 |  | 0
d. | Connection to BHU&MED including staff to staff , nurse call & nurse emergency as per drawings and needed connections per medical specialist | No. | 35 |  | 0
e. | Pull cord Patient Station | No. | 34 |  | 0
f. | Reset button for the room | No. | 18 |  | 0
g. | Annunciator panel | No. | 1 |  | 0
h. | Nurse call station | No. | 1 |  | 0
|  | Carried Forward |  |  | 0
Division 16: Electrical Works
Item No. | Description | Unit | Quantity | Rate (USD) | Amount (USD)
| Brought forward from previous page |  |  |  | 0
11 | Section 16740: PABX System
a. | Telephone box 60 pair | No. | 1 |  | 0
b. | 1 x RJ11 wall mounted telephone outlet complete with 1x4P UTP CAT3 cables and conduits from outlet to related patching connectivity. | No. | 41 |  | 0
c. | Ditto as above but counter mounted. | No. | 2 |  | 0
|  | Carried to Summary |  |  | 0

## Summary
Summary
Bill No. | Description | Page | Amount (USD)
1 | Division 01: General Requirements | 1
2 | Division 02: Site Construction | 3 | 0
3 | Division 04: Masonry Works | 5 | 0
4 | Division 05: Metal Works | 6 | 0
5 | Division 06: Wood and Plastic | 7 | 0
6 | Division 07: Thermal and Moisture Protection | 8 | 0
7 | Division 08: Openings | 12 | 0
8 | Division 9: Finishing | 18 | 0
9 | Division 10: Specialties | 20 | 0
10 | Division 15: Mechanical Works | 30 | 0
11 | Division 16: Electrical Works | 37 | 0
a. | Total of Bills |  | 0
b. | Percent Addition/Reduction (%) |  | 0%
c. | Addition/Reduction Amount (USD)= (axb) |  | 0
d. | Total of Bills including (Addition/Reduction) (USD)=(a+c) |  | 0
e | Total Amount (USD), Numbers and Words |  | 0