# Suspended ceilings

There is a Product Partner for this worksection. Click the logo to be redirected to their page.

Worksection application

This worksection is applicable to proprietary suspended internal ceilings and external soffits of dry construction with suspension systems attached to a supporting structure.

Related material located elsewhere in NATSPEC

Related material may be found in other worksections. See for example:

- Acoustic insulation for acoustic insulation to walls and bulk acoustic insulation laid over ceiling systems.

- Partitions – systems or Partitions – framed and lined for plenum barriers.

Worksection(s) on which this worksection relies

The following worksections must be included, with this worksection, to provide a complete specification:

- General requirements.

- Light steel framing.

- Light timber framing.

- Lining.

Material not included in NATSPEC

Some projects may include items not covered by NATSPEC. For these you may need to create new text, modify this text or use an applicable worksection.

Worksection cross-referencing

Other worksections that cross reference this worksection are:

- None.

Documenting this and related work

You may document this and related work as follows:

- Show ceiling types and coordination of combined services on reflected ceiling plans.

- Show particular requirements for the sheet linings can be on the drawings or scheduled either in this worksection or in Lining. Do not duplicate.

## General

AS/NZS 2785 definitions do not include timber systems that form part of AS/NZS 2589.1.

### Inspection

#### Notice

Give sufficient notice so that inspection may be made of the framing preparation and setout of suspended ceilings before installation of panels.

Hold points, if required, should be inserted here.

### Submissions

#### Samples

Submit samples as follows:

- Ceiling material: Sheet, panel, tile, with insulation

- Methods: Methods of jointing, fixing, height adjustment.

- Suspension: Sections proposed for suspension system, including wall angles and trim.

If prototypes are specified, separate samples of visible components may not be necessary.

## Products

### Linings

#### Fibrous plaster tiles

All imported fibrous plaster tiles with hard cast plaster face for decorative ceiling sections.

Now made obsolescent, but still available.

#### Plasterboard panels

All imported glass fibre reinforced gypsum plasterboard panels or tiles to approval of the Employers representative. Refer to the Suspended ceiling schedule.

#### Suspension system

Refer to the Suspended ceiling schedule.

## Execution

### Installation

Show on the drawings the location and extent of the suspended ceiling and where appropriate the basic grid layout. See also AS/NZS 2785 Section 4 on installation. Delete the installation clauses for materials not required for the project. Consult manufacturers for particular installation requirements for other materials.

#### Ceiling grid

Set out the ceiling grid so that panel joints and centrelines of visible suspension members coincide with grid lines shown on the drawings. If not otherwise shown, set out so that opposite margins are equal.

Pattern and texture: Set out patterned or heavily textured materials to give consistency in direction of pattern or texture.

Special sized panels: Provide special sized purpose-made panels to fill non-standard margins, openings and penetrations.

#### Cut tile edges

General: Conceal, or finish to match prefinished edges.

Generally only plain units or units within a random pattern will be considered for approval to cut.

#### Lighting

Fit lights within the ceiling grid system to ensure that distortion, overloading or excessive vertical deflection is prevented. Support lights on the ceiling primary grid members.

#### Proprietary systems

Provide suspended ceilings as complete proprietary systems, each fabricated by one manufacturer and installed by a specialist installer of demonstrated capacity.

#### Protection

Protect existing work from damage during the installation.

#### Stability

Install the ceilings level; and fix so that under normal conditions there is no looseness or rattling of ceiling components.

### Supports

The suspension system may comprise hangers or struts depending on which direction the load is applied. External ceilings will be subjected to upward wind loads and will therefore require strutting members, see AS/NZS 2785 Appendix A.

#### Bracing

General: Provide bracing to prevent lateral movement and to resist any imposed horizontal seismic force.

The ceiling where it abuts glazing should be braced at the perimeter, to prevent the ceiling from transferring horizontal load to the glazing under seismic activity.

#### External suspended ceilings

Support external suspended ceilings on rigid members capable of carrying the imposed loads. Install members to minimise any eccentricity, and ensure that the upward and downward wind loads are carried through to the supporting structure.

#### Movement joints

Exterior ceiling systems are subjected to additional thermal movement, due to the uncontrolled nature of the environment. The spacing of control joints should take account of these additional thermal effects.

Install the ceiling with control joints to correspond in location and direction to those in the structural frame.

#### Finishes

Repair damaged finishes by replacement or refinishing of the item. All repairs are to be completed so no sign of the damage is visible in the completed work.

#### Support members

Grid members: If required, notch grid members at the junction with the perimeter trim to ensure the panels lie flat on the perimeter trim.

Services: Do not suspend from services (e.g. pipework or ductwork) unless the service has been designed to accept the ceiling load. In locations where services obstruct the ceiling supports, provide bridging and suspension on each side of the services.

Spacing: Space the support members as required by the loads on the system and the type of ceiling, and allow for the installation of services and accessories, including ductwork, light fittings and diffusers. Provide additional support or suspension members for the fixing of such items.

#### Suspension system

Height adjustment: Provide height adjustment by means of a length adjustment device at each suspension point, permitting length variation of at least 50 mm.

If particular height adjustment devices are not permitted, say so here. The use of threaded rod systems does not necessarily constitute a stronger ceiling grid system.

### Panels

#### General

Fitting: Fit panels accurately and neatly, free from air leakage and staining.

Panel lock clips: If panels are exposed to wind loads or if required for security, insert locking clips at the junction of rails and panels.

#### Accessories and trim

Provide accessories and trim necessary to complete the installation.

Plasterboard trim: Provide purpose-made corner beads, casing beads and stop beads.

Metal Trim: Provide trims at junctions with other building elements and surfaces, such as walls, beams and penetrations, consistent with the style, materials and finishes of the ceiling system generally.

Insert type and proprietary name, or delete if the prescriptive specification in the template is sufficient.

Installation: e.g. “In accordance with the manufacturer’s recommendations”.

Finish: e.g. “Painted”.

Type: e.g. “Standard 90 mm scotia cornice”, “Moulded plaster sprinkler cornice”.

Show on drawings and refer to the detail.

For package (multiple-prime) contracting, note that curtain tracks may not be installed by the suspended ceiling contractor.

#### Service penetrations

Provide openings for, and fit the ceiling system up to, all services elements such as light fittings, ventilation outlets, detectors, sprinklers and loudspeakers.

Provide for ceiling access panels where necessary to light fittings, sprinkler control valves, and the like.

### Access panels

#### Finish

Match the ceiling panels in appearance and performance and mark the panel for easy identification.

### Completion

#### Spares

Applies mainly to demountable systems where the tiles, etc., are liable to suffer from handling. Suspension system members should need less replacement. Vary the quantities stated, as required.

Supply spare matching tiles and accessories of each type for future replacement purposes. Store the spare materials on site where directed.

If the names of firms and proprietary types are quoted here, much of the data required by this schedule may be unnecessary.

Suspended ceiling system type: Nominate for flush set ceilings, tiles or panels.

Demountability: Required or not.

Trim: Plain angle, shadow angle. Use manufacturer’s descriptions.

If using perimeter trim and exposed support grid it is necessary to notch the grid members at the junction with the perimeter trim to ensure the panels lie flat on the trim. The extra cost may not be warranted in all cases. Specify if required.