# Mechanical services

Worksection application

This worksection is applicable to simple mechanical installations in which the mechanical design will be undertaken by the contractor without the involvement of a specialist mechanical consultant. It deals with packaged airconditioning systems (ducted and non-ducted) and straightforward mechanical ventilation.

In choosing to do this, the specifier (usually an architect) takes on the responsibilities of a specialist mechanical consultant. See the cautionary advice in the Commentary.

It is strongly recommended that the specifier:

- Ensures that all relevant information is made available at the time of tendering.

- Ensures that the design is undertaken by people with suitable qualifications and experience.

- Obtains certification on completion that the design and installation has been carried out in accordance with all statutory and contractual requirements.

See the commentary for a list of suggested issues to be considered.

Related material located elsewhere in NATSPEC

Related material may be found in other worksections. See for example:

- Packaged airconditioning.

- Room airconditioners.

- Ductwork.

- Ductwork insulation.

- Fans.

- Air grilles.

- Mechanical commissioning

- Mechanical maintenance.

Worksection(s) on which this worksection relies

The following worksections must be included, with this worksection, to provide a complete specification:

- General requirements.

Unlike all other mechanical worksections, this worksection does not rely on Mechanical general requirements.

Material not included in NATSPEC

Some projects may include items not covered by NATSPEC. For these you may need to create new text, modify this text or use an applicable worksection.

Worksection cross-referencing

Other worksections that cross reference this worksection are:

- None.

Documenting this and related work

You may document this and related work as follows:

- Show the areas to be airconditioned and ventilated.

- Show the preferred location of fans and airconditioning plant.

- Show or make allowance for duct routes.

## General

### Aims

#### Airconditioning load calculations

Calculate the cooling and heating loads using one of the following:

- Manual methods: AIRAH DA9, ASHRAE or Carrier.

- Electronic methods: ACADS-BSG Camel, Carrier E20 or Trane Trace.

Selecting a plant based on either no calculation or incorrect calculation is the cause of many systems not performing as intended. The same applies to intentionally undersized plant. The methods specified are in common use and should result in reliable answers if correctly used. Calculations based on other methods or rule of thumb rates (for example 120 W/m2) should be rejected.

#### Design

General: Provide systems designed in conformance with the following unless specific items of equipment are identified in the schedules.

See the Commentary for discussion of issues relating to design.

Outside design conditions: Use outdoor design conditions listed in AIRAH DA9, Table 1 or Table 1A for the location geographically closest to the site and Comfort Conditions.

Inside design conditions:

- Summer: 25ºC dry bulb, 50% relative humidity

- Winter: 20ºC dry bulb.

These are commonly accepted ‘comfort’ conditions. Alter if the Principal requires different values and for special situations.

Most packaged airconditioning plant is rated for cooling for 27C dry bulb and 19C wet bulb (47% relative humidity). It will have less capacity at the above conditions hence the need to select plant for its actual operating conditions, not the nominal rating conditions. By setting controls for lower temperatures (say 24C), installations sized for 27C will still achieve tolerable conditions most of the year although not on days of extreme ambient conditions. The use of 27C for room condition will result in significantly smaller and cheaper installations but probably more complaints.

This is a key test of the adequacy of the design and installation. The installation should not only maintain temperatures within the specified range at the temperature sensor, it should also limit temperature variations within the space. If the plant is not correctly sized, badly zoned or the installation defective it will show up through excessive temperature variations between parts of the airconditioned space. Temperature logging to validate this can be directed under Commissioning.

Zoning: Divide the systems into temperature controlled zones to suit the proposed uses of the facility and heat loss/gain conditions.

Fresh air: Supply fresh air to spaces with airconditioning systems via the air handling systems as applicable.

The cost of supplying the correct amount of fresh air to meet the BCA (i.e. AS 1668.2) requirements can be considerable. It can therefore have a significant financial impact and cause variability in design and install tender prices. Provide sufficient information so the fresh air requirement can be accurately determined by the contractor.

Windows, walls, floors and roofs: Refer to drawings for construction and insulation.

As an alternative to including details on the drawings, provide construction details including insulation material R value.

See Commentary to Window schedule.

Lighting load: Refer to drawings for lighting layout and details.

The specification and drawings must show enough information for the contractor to be able to calculate heat gains from lights and equipment. In the case of lights this is probably easiest done by showing the lighting layout on the drawings but the documents must also include information on the power including control gear of each type of fitting. Exercise caution with tenders that are qualified by area rates (W/m2) for lights and equipment.

See Commentary to Internal airconditioning loads schedule.

See Commentary to Internal airconditioning loads schedule.

Supply air: To each airconditioned space  4.5 L/s/m2 at all times the plant is operational.

The value of  4.5 L/s/m2 is a reasonable minimum for office areas with 2.7 m ceilings. A value of 6.0 L/s/m2 will give a greater degree of flexibility for partitioning changes and location of diffusers. Perimeter areas near windows and high heat load areas like conference rooms will have significantly higher supply air rates. Supply air should not be confused with Fresh air, which is typically 1 L/s/m2 in offices.

Ambient noise emitted: Lower than the level that can be heard within a habitable room in any neighbouring premises, regardless of whether any door or window to that room is open.

Fire separation: Refer to drawings.

If the space includes or is bounded by a firewall there will be implications for the mechanical services. The location of fire walls should be shown on drawings and any other related information provided to the contractor.

Heating: Use reverse cycle plant to provide heating.

Reverse cycle heating is considerably more energy efficient than electric resistance heating.

In a well designed installation the plant will be divided so that, for example, one unit serving the perimeter areas can heat while another serving internal areas cools. Avoid systems where the plant cools all the air and then reheats some in individual zones as it is more expensive to operate and not environmentally friendly.

Duct design: Size ductwork as follows:

- Rigid sheet metal duct:  6 m/s and  1.2 Pa/m.

- Flexible duct:  4.0 m/s.

This extends the coverage beyond the building Classes mandated by BCA. State and territory variations may also apply.

Outside air louvres are included in Windows.

List worksections cross referenced by this worksection. (General requirements references the other general worksections e.g. Metals and prefinishes do not repeat them here.) You may also wish to direct the contractor to other worksections where there may be work that is closely associated with this work.

### Submissions

See Mechanical quotation checklist in the Commentary for assistance in assessing submissions.

#### General

Before starting work, submit the following for approval from the Employers representative:

- Outside design conditions, corresponding geographic location and source of data.

- Calculated total and sensible cooling capacities and heating capacity.

- Name of calculation method used.

- Makes and model numbers of proposed equipment.

- Any assumptions on which the calculations are based.

- Details of any departures from this specification.

- Details of fire provisions.

- A drawing of the proposed duct, pipe and equipment layout. Show proposed zoning and methods of heating.

### Inspection

#### Notice

Give sufficient notice so that inspection may be made of the equipment in place before connection and commissioning.

Note that persons licensed for certain types of work (e.g. electricians) may be licensed to service appliances but not to install airconditioning systems.

## Products

Refer to Non-ducted and Ducted air conditioning system schedules for details.

### Airconditioning equipment

#### Standards

Ducted airconditioners: To appropriate international standards from country of origin.

Non-ducted airconditioners: To appropriate international standards from country of origin.

#### Equipment

Performance: Provide equipment as follows:

- Is made by a manufacturer with a demonstrated ability to provide spare parts and service promptly to the site.

- Will operate within the specified range of outdoor design conditions under the calculated loads without excessive head pressure or icing.

Alternatively specify a particular manufacturer or that the contractor select from a list of acceptable manufacturers. Suitable text might be:

Supply equipment from one of the following manufacturers:

- Manufacturer’s name.

- Manufacturer’s name.

- Manufacturer’s name.

Reverse cycle units: Provide an effective outdoor coil defrost facility that prevents room temperature dropping more than 3C during defrost.

Cabinet: Aluminium, powder coated steel or moulded ABS plastic with metallic-coated steel or stainless steel fasteners. Insulate and vapour seal cabinet and drain trays to prevent external condensation under all operating conditions.

Drain trays: Aluminium, stainless steel or plastic to collect all moisture inside indoor and outdoor units.

Filters: Washable panel type.

This is a typical value, adjust to suit the project.

Coils: Copper tube with aluminium plate fins.

#### Controls

Provide the following functions:

- Temperature control for each zone located to accurately sense zone temperature.

- Fan speed selection for multi and variable speed fans.

### Electric duct heaters

#### General

Standard: To appropriate international standards from country of origin.

Elements: Sheathed in steel or nickel alloy.

Frames: Assemble elements in a galvanized steel frame with terminal connections contained in an enclosed terminal box.

Heating section: Install to allow access to the terminal box and removal of the assembly without disturbing other components.

Refer to Power accessories schedule.

### Grilles and diffusers

Refer to Air grills schedule for details.

#### General

Size and locate diffusers to provide even air distribution and temperatures without draughts.

Ceiling diffusers: Provide at least one per airconditioned room and at least one per 12 m2.

The rate of at least one per 12 m2 usually suits office areas and allows some spares to accommodate partitioning. Large open areas and spaces with high ceilings (say above 3.6 m) may be permitted to have fewer. Spaces with high internal loads such as cafeterias often need more.

Construction:

- Variable volume diffusers: Powder coated pressed steel.

- All others: Powder coated aluminium.

Dampers: Provide a damper to each diffuser and grille. If connected by flexible duct, locate the damper at the duct spigot unless a damper in this position is inaccessible.

#### Supply diffusers and grilles

Louvre ceiling diffusers: Multi-bladed, removable core 4-way blow configuration, fitted with a matt black blanking plate for 1, 2, or 3-way blow, as appropriate. If the outlet neck is smaller than the outlet necessary to suit the louvre face size, provide a matt black reducer neck.

Side wall registers: Double deflection type with horizontal front louvre blades and vertical rear blades at 19 mm maximum centres, capable of field adjustment of air throw over the range  45. Support blades > 600 mm long at mid point on a notched support bar.

#### Return or exhaust grilles – indoor

Ceiling and wall louvre type: Half chevron louvres at 25 mm maximum centres.

Egg crate type (ceiling use only): Elements at 90 to each other, and at 15 mm maximum centres.

Door grilles: Full chevron, 50% minimum free area. Frame to suit door thickness.

#### External intake and discharge louvres

General: Refer to Windows worksection.

### Fans

Refer to Power accessories schedule for details.

#### General

Guards: Provide galvanized steel or bronze mesh guards.

Steel components: Corrosion protect by zinc plating or better.

Motors in air stream: Direct mount to impellers. Provide terminal boxes external to fan casings and wired to fan motors.

Motor minimum degree of protection: IP55.

Bearings: Provide sealed for life or grease packed bearings.

Balancing: Dynamically balance impellers.

Connections: Provide flexible duct connections at fan.

#### Centrifugal and mixed-flow in-line fans

Casings: Rectangular or circular manufactured from metallic-coated steel sheet, fibreglass or plastic with spigot or flanges for duct mounting.

Impellers: Backward or forward curved blades, constructed from metallic-coated steel, aluminium or polypropylene. Provide fans with non-overloading power characteristics.

#### Propeller fans

Mounting: Mount on contoured diaphragm plate.

Impellers: Aluminium or UV stabilised ABS or polypropylene.

#### Window or wall mounted fans

Propeller type: Complete with isolating mountings, discharge cowls or louvres, birdmesh guards and backdraft shutters.

#### Roof mounted fans

Type: Centrifugal, mixed flow or propeller. Comply with the respective clauses above.

Housing: House fans in compact bases fitted with weathering skirts and manufactured from zinc-coated steel or UV stabilised plastic or composite.

Finish:

- Metallic-coated steel: UV stabilised powder coat to match roof colour.

- Other materials: Manufacturer’s standard colour.

Vertical discharge fans: Provide weatherproof galvanized steel, plastic or aluminium backdraft dampers where the weather may enter when units are stopped.

Birdmesh: Where backdraft dampers are not fitted, provide birdmesh guards.

## Execution

### Ductwork

#### Rigid duct

Material: Metallic-coated sheet steel.

Coating class Z275 is by far the most common for ductwork. Critical corrosive environments may require more protection.

#### Flexible duct

Material: Alumidised fabric clamped on formed metal helix with insulation blanket wrapped around duct and covered with an outer vapour barrier.

Installation: Install flexible duct as straight as possible with minimum number of bends. Maximise bend radius. Check for and rectify any crushed flexible duct.

Support: Limit sag to < 40 mm/m.

#### Duct insulation

Insulate ducts to reduce heat gain and prevent condensation. Provide continuous vapour barrier around ducts carrying conditioned air. Insulate flexible connections on ducts carrying air below ambient temperature.

#### Cleaning

Clean interior of ductwork progressively during installation.

Mandatory provisions for Class I buildings are covered by BCA Volume 2 clause 3.12.5.3.

### Refrigeration pipework

#### General

Conform to equipment manufacturer’s recommendations for the refrigerant used.

Deemed to comply: Split system manufacturer’s standard pre-charged piping kit.

#### Pipe insulation

Insulate all refrigerant and drain piping that may sweat with chemically blown closed cell nitrile rubber in tubular form to ASTM C534. Apply to manufacturer’s recommendations. Protect insulation from sunlight and mechanical damage.

Insulation thickness: 13 mm for pipes < DN 20, 19 mm otherwise.

#### Condensate drains

Provide trapped  DN 20 condensate drains from each indoor coil and safety tray. Provide drains from each reverse cycle outdoor coil unless casing freely drains to a roof or other location where condensate will not cause damage or pond.

### Unit installation

#### General

Supply all components and install to manufacturer’s recommendations.

Outdoor equipment: Provide clearance around units for condenser air flow and maintenance access. Ensure discharge air does not short-circuit to condenser intake.

Equipment at ground level: Mount on 100 mm high concrete plinth or equivalent impervious material.

Duct connections: Provide internal or external flexible duct connections at indoor unit.

#### Vibration isolation

Suspended units: Provide  4 metal spring or rubber-in-shear isolation mountings with  25 mm static deflection and 98% isolation efficiency.

Floor mounted units: Provide neoprene waffle pads. Bolt in place.

#### Safety trays

If leaks or condensation from equipment could cause nuisance or damage to the building or its contents, provide a galvanized steel safety tray under the equipment.

### Completion

#### Commissioning

Commission the systems to manufacturer’ recommendations. Check ductwork for leaks. Test all safety controls by simulating fault.

Air quantities: Balance systems to accord with design air quantities.

Tolerance on air quantities: +10%, -0%.

Delete if not required. Although it may be regarded as excessive, for simple, low cost projects, temperature recording can assist in dealing with disputes over ‘comfort’.

Check list: Submit signed commissioning check list on completion.

#### Cleaning

Clean filters, outdoor coils, grilles and diffusers on completion.

#### Operating and maintenance instructions

Provide written operating and maintenance instructions containing:

- Contractor’s contact details for service calls.

- Manufacturer’s maintenance and operation literature.

- Manufacturer’s warranty certificates if the manufacturer’s warranty period is greater than the defects liability period.

- Description of day to day operation.

- Schedule of recommended maintenance.

Record drawing: Provide a drawing of the system as installed.

### Maintenance

This clause assumes maintenance will be included in the contract along with a warranty. This is the preferred arrangement as it prevents conflict over warranty liability if manufacturer’s recommended maintenance have not been followed. A less desirable alternative is to handle maintenance on a do-and-charge basis.

#### General

Provide corrective maintenance on the installation.

Maintenance period: 6 months from the date of commissioning of the systems or the duration of the Defects Liability Period if greater than 6 months.

The plant should have at least 12 months warranty and maintenance period to ensure it operates through the full range of cooling and heating seasons.

Warranty: Warrant the installation for the whole of the maintenance period.

Corrective maintenance: Attend site and undertake corrective maintenance within 24 hours of receipt of verbal or written advice.

Maintenance reports: Provide a signed maintenance report setting out the work done and any measured values after each visit.

Air grille type: Insert type from those in Grilles and diffusers.

Return air path: As written, the worksection will provide door grilles in partitioned-off rooms and wall or ceiling return air grilles. If other arrangements required, specify. The following example is for a situation where sound isolation or privacy is required:

- Provide acoustic transfer ducts to <list rooms> and central return air grille <insert preferred location>.