# ELECTRICAL SERVICES

Worksection application

This worksection is applicable to simple electrical installations in which the electrical design will be undertaken by the contractor without the involvement of a specialist electrical consultant.

Related material located elsewhere in NATSPEC

There are no directly related NATSPEC worksections.

Worksection(s) on which this worksection relies

The following worksections must be included, with this worksection, to provide a complete specification:

- General requirements.

Material not included in NATSPEC

- Some projects may include items not covered by NATSPEC. For these you may need to create new text, modify this text or use an applicable worksection.

Worksection cross-referencing

Other worksections that cross reference this worksection are:

- None.

Documenting this and related work

This worksection provides a brief specification for a design and installation package of work and is intended for use when there is an extensive package of work to be designed by the contractor.

In choosing to do this, the specifier (usually an architect) takes on the responsibilities of a specialist electrical consultant. A worksection Template such as this cannot cover all possible projects or situations so the specifier using it needs to be aware of the limitations of the approach and their own limitations and responsibilities, particularly in relation to professional and public liability. It is strongly recommended that the specifier:

- Ensures that all relevant information is made available at the time of tendering.

- Ensures that the design is undertaken by people with suitable qualifications and experience.

- Obtains certification on completion that the design and installation has been carried out in accordance with all statutory and contractual requirements.

Specifiers should consider the professional and public liability implications of undertaking responsibility for design without the involvement of an electrical consultant. Do you have the necessary expertise? Does your professional liability insurance cover you for this? If transferring responsibility to the contractor you should be sure that the contractor has all relevant design and safety information.

## GENERAL

### AIMS

#### Responsibilities

Provide electrical systems in conformance with the Electrical systems schedule.

Schedule a summary of the principle electrical systems to suit the project.

For contractual reasons this summary should not attempt to be a ‘Scope of Work’ or to imply that it includes ALL work although the content may appear to be very similar to what has traditionally been included in ‘Scope of Work’ clauses. Do not use vague phrases like ‘to the complete satisfaction of the superintendent’ or blanket phrases like ‘and all other work necessary to compete the contract’. If the services are part of a single prime contract do not include subcontractors (as opposed to contractor’s) responsibilities here. For example the contractor is responsible for all cranage so do not imply that it is the responsibility of a subcontractor.

Statutory authorities and other bodies may levy  fees, payment of which are normally the responsibility of the contractor. Preliminaries defines the responsibilities, within the terms of the general conditions of contract, for the payment of fees by the contractor and principal.

- Do not include statements about payment of fees in this worksection.

- Ensure that fee payment responsibilities of contractor and principal are adequately covered in Preliminaries.

- If the principal has already paid some fees include details in Preliminaries  so that allowance is not duplicated.

#### Qualification

Use only persons appropriately experienced and qualified to undertake the electrical design and construction work on the systems documented.

#### Performance

Carry out verification tests and measurements to show compliance with the specification.

#### Rates for installation work

Rates for installation of cabling, light fittings, sockets, switches and all other electrical components are to include allowance for fixings, connection, chasing of wiring and any other works required for the installation of the electrical system to a fully operational and safe working condition.

### Inspection

#### Notice

Give sufficient notice so that inspection may be made of the following:

- Underground electrical services conduits prior to concealment.

- Above ground electrical services conduits in walls prior to concealment.

- Switchboards prior to installation.

#### Inspection and testing on completion

- To verify that the requirements of this specification have been met, all electrical installations and any alterations, additions or repairs to an existing electrical installation, after completion and before being energised shall be:

- Inspected as far as is practicable

- Tested

- Precautions shall be taken to insure the safety of persons and to avoid damage to property and the electrical installation equipment during inspection and testing.

- NOTE: if requires, the contractor is responsible to provide temporary power generator in order to undertake all needed testing.

- A visual inspection shall be made when work on an electrical installation has been completed in order to verify that the work complies with the requirements of this specification. The visual inspection shall be carried out before, or in association with testing and shall where practicable be made before the relevant part of the electrical installation is placed in service. Visual inspections shall be carried out prior to the completion of the installation where that part of the electrical installation will be covered by following works.

- The following items provide a guide to the matters to be checked during the visual inspection to assess that the relevant requirements of this specification have been met.

- General:

- Protection against direct contact with live parts e.g. Insulation and enclosure.

- Protection against indirect contact with exposed conductive parts, e.g. Double insulation or isolating transformers.

- Protection against hazardous part, e.g. Enclosure, guarding or screening of flammable materials, hot surfaces and parts that may cause physical injury.

- Protection against spread of fire, e.g. Penetration of fire barriers.

- General condition of the electrical equipment, e.g. Signs of damage that could impair safe operation, disconnection of unused electrical equipment.

- Consumers Mains:

- Current carrying capacity.

- Voltage drop.

- Underground installation conditions, e.g. Enclosure, depth of burial and mechanical protection.

- Aerial installation conditions.

- Connection of wiring.

- Protection against external influences.

- Switchboards:

- Location, e.g. Access and egress.

- Protective devices, e.g. Overload and residual current rating, fault current rating.

- Isolating devices, e.g. Main switches.

- Connecting devices, e.g. Neutral bars, earth bars and live links.

- Connection and fixing of wiring and switchgear.

- Identification and labelling of electrical equipment.

- Protection against external influences.

- Wiring systems:

- Conductor size, e.g. Current-carrying capacity and voltage drop.

- Identification of cable cores.

- Adequate support and fixing.

- Connections and enclosures.

- Particular installation conditions, e.g. Underground, aerial and emergency systems.

- Segregation from other services and electrical installations.

- Protection against external influences, e.g. Enclosure.

- Electrical equipment:

- Isolation and switching devices for protection against injury from mechanical movement devices and motors.

- Isolation and switching devices for protection against thermal effects, e.g. Motors, room heaters and water heaters.

- Switching devices for particular electrical equipment, e.g. Socket outlets and cooking appliances.

- Particular installation conditions, e.g. Locations affected by water, explosive atmospheres, extra low voltage and high voltage.

- Compliance with required standard.

- Connection, support and fixing.

- Protection against external influences.

- Earthing:

- Multiple earth neutral (MEN) connection.

- Earth electrode.

- Earthing conductors, e.g. Size and identification.

- Equipotential bonding conductors, e.g. Size and identification.

- Connections, joints and terminations.

- Protection against external influences.

- Connection to earthing arrangements for tother systems.

- Creation of earthed situation that may require earthing of additional electrical equipment.

- Testing:

- After completion of, or in association with the visual inspection tests, testing shall be carried out on the electrical installation to verify that it complies with ther requirements of this specification and that it is suitable for the use intended.

- Sequence of tests as noted:

- Consumers mains test - polarity

- Sub-mains tests - polarity

- Earth resistance test – continuity of main earthing conductor

- Insulation resistance test of installation

- Earth resistance test for other earthed & equipotential bonded parts

- Final sub-circuit test –

- polarity

- connections

- Verification of operation of residual current devices

- Fault loop impedance test

The system design may be described in terms of the performance required. On completion the installed systems should be verified according to the performance parameters established.

## EXECUTION

### GENERAL

#### General

Arrangement: Arrange services so that services running together are parallel with each other and with adjacent building elements.

Installation: Install equipment and services plumb, fix securely and organise reticulated services neatly. Allow for movement in both structure and services.

Lifting: Provide heavy items of equipment with permanent fixtures for lifting as recommended by the manufacturer.

Suspended ground floors: Keep all parts of services under suspended ground floors > 150 mm clear of the ground surface. Make sure services do not impede access.

#### Samples

Samples: Provide samples of all accessories and light fittings for the approval of the Employers representative prior to use in the project.

#### Installation of accessories

General: Install accessories in conformance with the Installation of accessories table.

Flush mounting: Provide flush mounted accessories except in plant rooms.

Mounting heights: To on-site direction

Restricted location: Do not install wall boxes across junctions of wall finishes.

Surface mounting: Proprietary mounting blocks.

Specify areas where accessories may be mounted direct to the building service.

#### Installation Of Accessories Table

| Wall construction | Installation and concealed cabling facilities |
| --- | --- |
| Rendered brickwork partition | Flush wall box with conduit chased into wall |
| Double sided face brick partition | Vertically mounted flush wall box with conduit concealed in cut bricks |
| Concrete wall or slab | Flush wall box or flush mounted outlet with thermoplastic insulated cables in conduit integral with slab. Do not chase into concrete walls without obtaining approval from the Employers representative. |

#### Installation of ceiling mounted appliances

Connections: Provide flush mounted outlets on the ceiling next to support brackets.

Fixing: Provide support brackets fixed through ceiling to the building structure. Brace appliances that have excessive bending moments, are heavy or vibrate, to prevent horizontal movement.

#### Electrical installations

- All cabling and wiring is to be installed in approved PVC conduit or within a metal cable tray for horizontal runs within the ceiling. there will be no exceptions. Any cabling installed otherwise will be removed and replaced correctly at the contractor’s expense. All below ceiling level electrical circuits are to be installed in surface mounted conduits.

- International standard connectors (chocolate block) for the wiring and cabling are to be used for all connections, no other method is acceptable.

- All IP ratings given refer to Ingress Protection (IP) Codes to AS1939.

NOTE: Simple twisting of wires as a means of connecting wires and cables with protective electrical tape is not acceptable.

#### Earthing/Grounding

- All installed electrical fixtures and fittings are to be earthed to the main earth system for the facility, there are no exceptions to this requirement.

- All protective earthing conductors should be incorporated in the same wiring enclosure as the associated live conductors or in the adjacent vicinity.

- Where a ‘clean’ earth is specified for a particular item of electrical equipment, the manufacturer of the electrical equipment shall be consulted in order to confirm the necessary arrangements.

- Precautions shall be taken against the risk of damage to the earthing arrangement and other metallic part of the electrical installation through electrolysis or galvanic action.

- The size of an earthing conductor shall be such that it meets the requirements of the IEC regulations and is in accordance with the Earth conductor size table.

Earth Conductor Size Table

| Nominal size of live conductor (mm²) | Nominal size of copper earthing conductor (mm²) |  |
| --- | --- | --- |
|  | With copper live conductors | With aluminium live conductors |
| 1 1.5 2.5 | 1* 1.5* 2.5 | - - - |
| 4 6 10 | 2.5 2.5 4 | - 2.5 2.5 |
| 16 25 35 | 6 6 10 | 4 6 6 |
| 50 70 95 | 16 25 25 | 10 10 16 |
| 120 150 185 | 35 50 70 | 25 25 35 |
| 240 300 400 | 95 120 120 | 50 70 95 |
| 500 630 | 120 120 | 95 120 |

* These earthing conductors may be used only where incorporated in a multicore cable or flexible cord.

### LOW VOLTAGE POWER SYSTEMS

#### General

Provide a complete operational low voltage power system, comprising the following and to the Electrical supply mains and Electrical switchboard design schedules:

- Supply from mains power

- Metering.

- Consumers mains and switchboard.

- Submains and sub boards.

- Final subcircuits.

#### Submissions

Technical data: Submit documentation to fully describe the proposed installation. As a minimum provide:

The electrical system design should be supported by documentation to verify compliance with AS/NZS 3000. Basic coordination functions such as cable routes and cupboard layouts should be documented.

- Submain cable routes and support or enclosure method.

- Switchboard cupboard layouts including risers.

#### Accessories

Provide the following and to the Power accessories and Lighting control and fittings schedules:

- General power outlets.

- Isolating switches.

- Three phase outlets.

- Ceiling mounted sweep fans

- Duct heaters

- Wall, window or roof mounted exhaust fans

- Light switches

- Light fittings

- Emergency lighting and exit signs

- Other equipment as identified in the Schedule

#### Junction and terminal boxes

Shall be manufactured from PVC and rated to IP56. They shall come complete with a rigid PVC cover attached by means of screws.

#### Switches

All switches are to be manufactured in compliance with international standards IP24. rate is to include allowance for installation of switches recessed into the wall. Switches are to be installed in locations as shown on the drawings.

#### Wiring systems

Generally to AS/NZS 3000. Nominate other standards if required. The BCA cites AS/NZS 3013 for electrical conductors supplying certain substations or switchboards, classification not less than WS53W, is one deemed-to-comply solution.

Selection: Provide wiring systems appropriate to the installation conditions and the function of the load. All wiring quality to be approved by the Employers representative before installation commences.

#### Power cables

Copper cable generally, multi-stranded except for MIMS. All cabling is to be manufactured to international standard (BS 5467 or BS 6500) and meet all appropriate safety and performance requirements.

Minimum size:

- Lighting subcircuits: 1.5 mm2.

- Power subcircuits: 2.5 mm2.

- Submains: 6 mm2.

Voltage drop: Install final subcircuit cables within the voltage drop parameters dictated by the route length and load.

#### Dummy load tests

Where electrical tests are required and the actual load is not available, provide a dummy load equal to at least 75% of the design load.

### SWITCHBOARDS

#### General

Provide proprietary switchboards to the following and to the Electrical switchboard design schedule:

- Main switchboard.

- Distribution boards.

Distribution boards shall be constructed from steel with a lockable door. Borads shall be sealed to meet a rating of IP56. All cable entry and exit points shall be constructed using suitable sized, proprietary PVC cable glands.

AS/NZS 3439.1 covers the construction, testing, forms of separation and arrangement of type tested and partially type tested assemblies.

AS/NZS 3439.3 covers the particular requirements for low voltage switchgear and controlgear assemblies, such as distribution boards and control panels, intended to be installed in places where unskilled persons have access for their use.

AS/NZS 3439.1 provides detailed guidance for designers specifying switchboard assemblies.

#### Statutory authority’s equipment

Refer to local supply authority service rules to determine their requirements. Install equipment supplied by the statutory authority, and provide wiring to complete the installation.

#### Cable entries

Single core cables rated > 300 A: Arrange to minimise eddy currents.

#### Construction

Fixing: Before making interpanel connections, fix assemblies and metering equipment enclosures into position, level and plumb.

Cable entries: Neatly adapt one or more cable entry plates, if fitted, to accept incoming cable enclosure. Provide the minimum number of entry plates to leave spare capacity for future cable entries. Do not run cables into the top of weatherproof assemblies.

Single core cables rated > 300 A: Pass separately through non-ferrous gland plates. Do not provide metal saddles.

Cable enclosures: Continue cable enclosures to or into assemblies and fit cable entry plates so that the IP rating of the assembly and the fire rating of the cable are maintained.

Cable supports: Support or tie mains and submains cables within 200 mm of terminations.

### SWITCHBOARD COMPONENTS

#### Switch-isolator and combination fuse-switch units

Combined fuse switch units are not commonly used and are reserved for existing installations or for high fault levels.

Rated current: To suit unit installed in enclosure.

Rated fault capacity: Provide units selected for short-circuit making capacity that is at least the fault level at assembly incoming terminals.

Breaking capacity: At least the rated full load current.

Rated duty: Uninterrupted in non-ventilated enclosure.

Operation: Independent manual operation including positive ‘ON/OFF’ indicator.

Locking: Provide for padlocking in the ‘OFF’ position.

Handles: Removable only when switch is in open position.

Fuse links: Isolated when switch contacts are open.

#### Moulded case and miniature circuit breakers

Moulded case circuit breakers are commonly used for current ratings less than 1600 A.

Moulded case breakers to International Standards.

Miniature circuit breakers to International Standards

Fault capacity > 10 kA  circuit breakers to approval of Employers representative

Fault capacity < 10 kA, current rating < 100 A: Miniature overcurrent circuit breakers

Mounting: Mount circuit breakers so that the ‘ON/OFF’ and current rating indications are clearly visible with covers or escutcheons in position. Align operating toggles of each circuit breaker in the same plane.

Clip tray chassis: For miniature overcurrent circuit breakers provide clip tray assemblies capable of accepting single, double, or triple circuit breakers, and related busbars. Provide moulded clip-on pole fillers for unused portions.

#### Residual current devices

Also called earth leakage devices.

Integral type: Incorporate earth leakage in circuit breaker protection operation.

Maximum tripping current: 30 mA.

Residual current devices Types III and IV do not provide adequate personal protection. See AS 3190 clause 5.1. AS 3190 will be superseded (in part) by AS/NZS 61009.1 in the year 2009.

#### Fuses with enclosed fuse links

Fuses are typically used for high fault current installations.

It is the designer’s responsibility to ensure that fuse links are sized to ensure effective discrimination with other in-line protection devices.

Standards: To International Standards

Fault level: Provide fuses suitable for the fault level at the assembly, and which discriminate with other protective equipment.

Let-through energy and peak cut-off current: To suit protected equipment.

Fuse-holders: Mount fuse-holders so that fuse carriers may be withdrawn directly towards the operator and away from live parts. Provide fixed insulation which shrouds live metal when the fuse carrier is withdrawn.

Barriers: Provide barriers on both sides of each fuse link, preventing inadvertent electrical contact between phases by the insertion of screwdriver.

Fuse links: Enclosed, high rupturing capacity type mounted in a fuse carrier. If necessary for safe removal and insertion of the fuse carrier, provide extraction handles. Mount on clips within the spares cabinet.

Identification: Clearly indicate manufacturer or distributor.

#### Contactors

The designer should determine the appropriate duty and rating of the contactors.

Standard: To International Standards.

Rated operational current: Full load current of the load controlled.

Minimum rating: 16 A.

Mounting: Mount with sufficient clearance to allow full access for maintenance, removal and replacement of coils and contacts, without the need to disconnect wiring or remove other equipment.

Interconnection: Do not connect contactors in series or parallel to achieve ratings.

### LIGHTING

The design of lighting systems is a specialist task and guidance parameters are provided by the following standards:

- The AS/NZS 1158 series Parts 0, 1.1, 1.3, 2, 3.1, and 4 provides guidance for public lighting of roadways, pathways and circulation spaces.

- The AS/NZS 1680 series Parts 0, 1, 2.1, 2.2, 2.3, 2.4, 2.5 and 3 applies to interior lighting.

- AS/NZS 1680.0 is cited in the BCA as this applies to interior lighting for safe movement.

- The AS 2560 series Parts 1, 2.1, 2.2, 2.3, 2.4, 2.5, 2.6, 2.7 and 2.8 applies to the design of sports lighting systems.

In a design and install contract verification of the installed system may be necessary. AS/NZS 3827 Parts 1 and 2 provides guidance on lighting system performance and the methods to be used to establish compliance.

Delete the standards not required for this project.

#### General

Provide a complete operational lighting system, tested and commissioned.

Proprietary equipment: Provide only proprietary lights, fittings and accessories.

Modifications and refurbishing: Carry out to the original manufacturer’s standards.

The minimum energy performance standard (MEPS) level for a particular ballast-lamp combination is the maximum permitted corrected total input power of a ballast-lamp circuit specified in AS/NZS 4783.2. clause 6.4 specifies a minimum energy performance standard (MEPS) for combinations of ballasts and type FD lamps. Should a higher standard be required delete this clause and enter the required EEI classification in the following Energy efficiency clause.

The MEPS for fluorescent lamps as specified in AS 4782.2 is based on the initial and maintained efficacy of the lamp and a prescribed CRI. This CRI will probably be lower, and therefore acceptable, compared tho that specified under Fluorescent lamps which is based on the colour rendering requirement of the interior design.

#### Lamps

There is an IEC draft standard for extra-low voltage lighting systems for filament lamps.

Lamps: Provide all lights complete with lamps and accessories.

Verify operation: Install lamps in all lights and verify correct operation before completion

Low voltage lamps: Provide lamps strictly in accordance with the light manufacturer’s recommendation.

On correlated colour temperature (CCT) and colour rendering index (CRI), see the AS/NZS 1680 series. A typical CCT in commercial applications is between 3000 and 4000 K for linear and compact fluorescent lamps.

Dichroic lamps: Provide dichroic lamps with integral reflector which match the design specification.

#### Lighting control system

Provide the following and to the Schedules:

- Lighting switches.

- Dimmers.

- Automatic control systems.

- External light fittings.

- Internal light fittings.

To minimise energy use consider specifying lighting controls such as dimmers, occupancy sensors and daylight sensors.

Documentation: Provide complete technical and operational documentation for the lighting control system where installed.

#### Installation

Supports: Mount lights on proprietary supports by means of battens, trims or packing material to suit location.

#### Completion

Verify the operation of all lights.

Contractor is to replace lamps which have been in service for extended periods during the installation and commissioning process.

### EMERGENCY EVACUATION LIGHTING

#### General

Provide a complete operational emergency evacuation lighting system, tested and commissioned to International Standards.

#### Single-point system lights

The contractor is responsible for locating the single point luminaires for compliance with AS/NZS 2293.

Visual indicator lights: Provide a red indicator, readily visible when the light is in its operating location, which indicates that the battery is being charged.

Inverter system: Provide protection of the inverter system against damage in the event of failure, removal or replacement of the lamp, while in normal operation.

Local test switches: Provide a momentary action test switch, accessible from below the ceiling, on each fitting to temporarily disconnect the mains supply and connect the battery to the lamp.

Common test switches: Provide a common test switch on the distribution board which disconnects main supply to the lights and tests for discharge performance, after testing, this switch must automatically revert to normal operating mode.

#### Batteries

Type: Lead-acid or nickel-cadmium batteries capable of operating each lamp at its rated output continuously at least 2 hours during completion tests and 1.5 hours during subsequent tests.

Battery life: At least 3 years when operating under normal conditions at an ambient temperature of 25ºC and subjected to charging and discharging at 6 monthly intervals.

5 or 6 years is possible in some circumstances. See AS/NZS 2293.2 for system checks, and AS/NZS 2293.1 clause 2.3.

Marking: Indelibly mark each battery with its date of manufacture.

See also AS/NZS 2293.1 clause 3.3.3.5.

#### Power supply to single-point systems

Provide an unswitched active supply to each fitting and exit sign, originating from the test switch control panel.

### TELECOMMUNICATION CABLING

#### General

Provide a complete operational telecommunications cabling system, tested and commissioned to International Standards. Provide accommodation for telecommunications cabling infrastructure complying with relevant clearance requirements from power cable distribution systems.

Include the following and to the Telecommunication equipment schedule:

- Building distributor.

- Backbone cabling.

- Floor distributors.

- Consolidation points.

- Equipment racks and patch cords.

- Horizontal cabling.

- Telecommunications outlets.

- Fly leads.

Amend to suit the project.

AS/NZS 3080 provides guidance on the specification of telecommunications cabling systems.

AS/NZS 3084 provides guidance on the spatial needs and the general arrangement of telecommunications cabling systems, and generally exceed the minimum safety requirements of ACIF TS 009.

Performance warranties are commonly provided by telecommunications cabling system suppliers based on a pre qualified selection of proprietary components.

#### Equipment racks

Type: 19 inch rack.

Free standing racks: Provide adjustable feet.

#### Modular connector patch panels

Terminations: Terminate directly to the modular connector.

Patch cords: Terminate cord ends with appropriate registered jacks.

#### Optical fibre termination panels

Break out trays: Provide fibre optic cable break out trays at each group of fibre optic cable terminations.

Loom cables: Neatly loom cables and lay stripped cables into the break out tray.

Secure cables: Ensure that cables are secured by the sheath and that there is no stress on the fibre optic cores.

#### Patch cords

Provide terminated patch cords for 60% of the total incoming and outgoing ports used.

#### Records

See AS/NZS 3085.1 and AS/ACIF S009.

Record book: Provide a record book at each cross connect.

Records in pencil: Complete the records in pencil for each termination and jumper, providing origin and destination and type of service.

Location: Secure log books in each distribution frame records holder.

#### Cable separation

The separation specified in AS/ACIF S009, is based on insulation grading.

Low voltage cables: Separate telecommunications cables not enclosed in conduits or ducts from low voltage services by at least 150 mm.

Electromagnetic interference (EMI): Provide clearance to minimise the effect of EMI where communications cables are installed parallel and adjacent to power cables carrying loads in excess of 200 A.

Clearance is also needed for EMI purposes, particularly where parallel and adjacent power cables are carrying loads in excess of 200 A.

#### Installation

Crossover: Install cables neatly and without crossovers between cables.

Loom size: Loom cables into groups not exceeding 50 cables, and hold looms in place using reusable cable ties at least 20 mm wide. Do not exert compressive force on the cables when installing cable straps.

#### Telecommunications outlets

Outlets: Provide RJ45 8 way modular jacks except where documented otherwise.

Generally 8 way modular jacks in either RJ45 (most common) or RJ6 form.

Pinouts: The pinouts vary with the application. Determine required pinouts before making cable terminations.

The connections to these modular jacks differ depending on the application. The most common is Pinout type 568A.

#### Fly leads

Provide minimum 2000mm long fly leads to 50% of the outlets installed.

#### Earthing system

AS/ACIF S009 applies, and contains a number of options.

Communication earth system (CES): Provide a communications earth terminal (CET) associated with the local protective earth (PE) system adjacent to each electrical distribution board.

### AUTOMATIC FIRE DETECTION

The contractor is responsible for compliance with AS 1670.1 and the local (statutory) fire authority requirements. Clearly define the following areas of responsibility, which are often overlooked:

- Provision of interconnecting wiring and connection to the emergency warning and intercommunication system (EWIS), sprinkler systems, door holders and mechanical plant, e.g. fire fan control panel.

- Provision of smoke detectors in air handling ductwork and their connection.

- Controlled door holders are sometimes included in the door hardware packages. Determine whether or not they form part of this contract.

- Connection to access control system, security doors and electric door strikes.

#### General

Provide a fully operational system, tested and commissioned in accordance with International Standards.

Describe the general operation of the system, e.g. addressable, air sampling.

The register is available from http://www.activfire.gov.au/. This was formerly the SSL Register of Accredited Products - Fire Protection Equipment.

#### Base station monitoring system connection

Connection: Connect the installation to the fire alarm monitoring base station via telecommunication carrier lines where identified in the Fire detection equipment schedule.

The connection of the system to the local fire alarm monitoring base station requires a dedicated telecommunications line, therefore the contractor must pay a connection fee for this line, as well as rental during the commissioning period.

Specify in the system description schedule if the line rental is to be paid by the contractor during the maintenance period.

#### Installation wiring

ACA may be involved under the Telecommunications Act 1997 if the system is connected to telecommunications cabling - refer to AS/ACIF S009.

Conductor size: > 1.5 mm2 TPI 220 V rated, with red and white insulation.

Sheathing: Red.

#### Fire indicator panels

Provide metal cubicle-type enclosures to locations identified on drawings.

Consider the following:

- Location - preferably shown on the drawings.

- Mounting structure e.g. concealed fixings, or brackets.

- Doors material and finish - usually as for enclosure and hardware (handles, locks, etc.).

#### Detectors

Coordinate with the mechanical services for provision of any duct mounted sampling units (DSUs) and integral or associated smoke detectors.

The contractor is responsible for spacing and location of detectors to AS 1670.1 . See BCA Specification E2.2a Clause 3 for mandatory requirements regarding smoke alarms. Smoke detectors provided to activate a smoke control system must be a separate dedicated system incorporating control and indicating equipment with alarm verification facility and complying with AS 4428.1.

Provide the following detector types as indicated on the drawings:

-Point type heat detectors.

-Duct sampling units.

-Integral heat detector/alarm units.

-Point type smoke detectors.

-Integral smoke detector/alarm units.

#### Self-indicating detectors

Provide a light emitting diode mounted in a clearly visible position, which illuminates whenever detector operation causes an alarm condition to register on the fire indicator panel. Provide self-indicating devices which, if faulty, will not render the detector inoperative under fire conditions.

Mounting positions of light emitting diodes:

- Visible detectors: On the outside of the detector or its base.

- Detectors concealed above ceilings: On the underside of the ceiling immediately below the detector.

- Detectors in other concealed spaces: On a visible panel close to the entry to the concealed space housing the detector.

#### Installation

Consider extension brackets for detectors installed in ceiling spaces.

Install detectors so they can be easily inspected and tested in situ, and readily withdrawn for service.

Generally there are two main types, either holders that are built into the door head and form part of the door suppliers package, or external wall mounted hold open devices which are included in the fire detection contract. In addition to magnetic door holders, there is sometimes a requirement for a connection to electric door strikes, activated by access control systems. The door strikes are generally connected directly to the fire detection system, so that they release in fire mode.

Coordinate with the architects door schedule.

#### Control facilities

Provide ancillary control device circuits and connections for automatically controlling and releasing magnetic door holders to operate the relevant fire doors under fire alarm conditions.

Some doors may open under fire alarm conditions.

#### Fire fan control and indication panels

Provide fire detection and alarm signals for the fire fan control panel to be incorporated by mechanical services.

Refer to AS/NZS 1668.1 clause 4.13.

Circuit identification marking should be shown on record drawings.

### ACCESS CONTROL

In some jurisdictions security systems can only be designed and installed by licensed persons. Obtain licence details, if this is the case.

#### General

Provide a complete operational access control system, tested and commissioned in accordance with International Standards as applicable. Refer to the Access control equipment schedule.

AS 2201 covers intruder alarm systems; it does not specifically cover access control. The standard provides detailed coverage of the design, installation and operation of alarm systems, including the performance requirements of detection devices, monitoring stations, wire free systems and alarm transmission.

AS 2201.1 covers general design, construction, installation and maintenance of intruder alarm systems, as well as outlining, in Section 5, the minimum requirements for any maintenance agreement.

AS 2201.3 nominates the minimum performance and reliability standards including false alarm rates for security alarm detectors.

AS 2201.5 includes alarm transmission via dedicated paths, switched networks and wire free systems.

It is common practice in small installations to describe the performance and function of an access control system only, and the final design and selection of the system and components is the responsibility of the contractor.

#### Processors or panels

Capacity: Provide separate entry/exit control modules for each designated door.

Users: Program the system to match the number of authorised users with unique access codes.

Time zones: At least 3 per day, with provision for weekends and public holidays.

#### Door control devices

Provide electric strikes, electric locks, drop bolts, or similar devices to suit door construction and hardware.

Fail-safe: Connect door control devices in a fail-safe mode to permit exit in the event of power failure.

Authorised products: Provide equipment approved for use by the Employers representative.

Double leaf doors (solid frame): Provide an electric strike or lock on the fixed leaf, connected to the door frame by concealed flexible wiring.

#### Activation

Specify the particular method of obtaining entry for each door, typically:

- Magnetic readers, proximity, card or key. For cards or keys, specify the type of card or key to be supplied and the quantity, including the quantity of pre-programmed cards or keys to be supplied for future issue.

- Key pads, with PIN programming.

- Punched cards.

- Remote, generally combined with an intercom.

Indicate whether local readers or key pads are to operate as stand alone units in the event of failure in the main processor system.

Provide keypads, card readers or other activation devices, and locate next to entry points.

External: Provide weatherproof (IP56) hoods or housings for external units.

Mounting height: 1200 mm from floor level.

#### Vehicle control

Specify the particular method of obtaining entry, typically to match internal door activation. Describe the method of vehicle entry/exit to be provided i.e. boom gates, roller shutters, gates.

Vehicle access control: Provide a vehicle access control system combining connection to vehicular doors and boom gates, and interconnection to the main access control system.

Exit Loop detection: Provide a buried loop detection system adjacent to the exit point to activate boom gates or vehicular doors on approach by a vehicle. Connect so that doors or gates close after a pre-set time.

Push-button, or to match the entry system.

Interlock: Provide a photo electric beam safety interlock.

Interlock function: To prevent door or gate from closing until the vehicle has cleared the exit point.

Push-buttons and readers: Where practicable, provide direct wall mounting for push-buttons or readers; otherwise provide a mounting bollard and extension arm.

Ensure that these are located within easy reach of the driver’s side window.

Mounting height: 1000 mm from floor level.

Reed switches: Provide heavy duty reed switches on both sides of vehicle doors, which generate a door closed indication at the control panel.

#### Intercom

Base station: Provide an intercom base station at each external entry point, interconnected with the individual local stations. Include speakers and microphones.

Construction: Wall mounted flush stainless steel panel.

Weatherproofing: IP56.

Dial: Digital push-button type.

Schedule: Provide a weatherproof (IP56) schedule holder and card identifying individual local stations. Locate next to the intercom panel.

Local station: Provide wall mounted intercom local stations, interconnected with the base stations and external entry points.

Type: Surface mounted, removable handset type.

Operation: Provide an audible tone device to indicate that the individual station is being called, and a press-to-talk switch so that the local station can communicate with the base station only when the switch is held down.

Door control: Provide integral momentary action door release switches to operate the door release or opening mechanisms at each external entry point.

Describe the systems interconnected to the access control system.

- Lift car controls, floors covered, location of readers, hours of operation.

- After hours air conditioning control, location of readers, hours of operation.

Describe the method of interconnection to other services such as lifts, air conditioning, lighting, and the location of readers. Specify services to be connected.

For lift control, designate the lifts that require readers - readers are usually supplied by the security contractor but installed and connected by the lift company responsible for the lift maintenance.

For airconditioning control, where after hours airconditioning is activated by the access control system, clearly define the area of responsibility for interconnection to the mechanical services.

The designer should be aware of the limitations and minimum clearances required in the installation and termination of distribution components especially coaxial cable. This is of particular concern at outlets in maintaining minimum bending radius requirements for cable, allowing for ease of installation and quality of finish of the installed system.

For example, minimum wall box dimensions would need to be 120 mm x 120 mm x 40 mm deep, with the cable terminated with a 90º crimp connector and outlet plate of square appearance. This has the added advantage of allowing for dual outlet sockets and future expansion.

Specify partition widths to accept wall box clearances.

Safety requirements: For isolators, in particular, see AS/NZS 1367 for system design and component selection.

Electromagnetic compatibility (EMC): AS/NZS 1367 states that the requirements of this standard are consistent with those of the Australian Communications Agency (ACA).

### LABELLING

If proprietary marking systems are required, for example, circuit identification, specify the system to be used, otherwise it can be assumed that handwritten indelible pen marking will be acceptable.

#### General

Provide labels including control and circuit equipment ratings, functional units, notices for operational and maintenance personnel, incoming and outgoing circuit rating, sizes and origin of supply and kW ratings of motor starters.

#### Identifying labels

Provide labels fixed to access panels, doors, covers and escutcheon panels and internal equipment, indicating the relevant information and componentry.

#### Single-line diagrams

Usually only required for main assemblies.

Custom-built assemblies: Provide single-line diagrams.

Format: Non-fading print, at least A3 size, showing the situation as installed.

Mounting: Enclose in a folder and fix close to assembly.

#### Marking cables

If particular labelling methods (including fixing, lettering or colours) are required, provide details.

Identify the origin of all wiring by means of legible indelible marking.

Identification labels: Provide durable labels fitted to each core and sheath, permanently marked with numbers, letters or both to suit the connection diagrams.

#### Telecommunications cabling

Label telecommunications cables. cross connects and outlets.

Labels: Label cables to indicate the origin and destination of the cable. Label outlets to show the origin of the cross connect, the workstation or outlet number, and the port designation.

#### Location marking

Cable route markers should be provided for all underground services.

Accurately mark the location of underground cables with route markers consisting of a marker plate set flush in a concrete base.

Location: Place markers at each joint, route junction, change of direction, termination and building entry point and in straight runs at intervals of not more than 100 m.

Concrete bases: 200 mm diameter x 200 mm deep, minimum.

Direction marking: Show the direction of the cable run by means of direction arrows on the marker plate. Indicate distance to the next marker.

Plates: Brass, minimum size 75 x 75 x 1 mm thick.

Plate fixing: Waterproof adhesive and 4 brass or stainless steel countersunk screws.

Marker height: Set the marker plate flush with paved surfaces, and 25 mm above other surfaces.

#### Labelling – minimum lettering heights

Main assembly designation: 25 mm.

Distribution assembly designations: 15 mm.

Small proprietary distribution boards: 10 mm.

Main switches: 10 mm.

Outgoing functional units: 8 mm.

Identifying labels (on outside of cabinet rear covers): 4 mm.

Danger, warning and caution notices: 10 mm for main heading, 5 mm for remainder.

Other labels including equipment labels within cabinets: 3 mm.

#### Label colours

Generally black lettering on white background except as follows:

- Main switch and caution labels: Red lettering on white background.

- Danger, warning labels: White lettering on red background.

#### Fixing

General: Fix labels securely.

Fixing methods: Use screws and double-sided adhesive. Fixed in extruded aluminium sections attached to panels with rivets or countersunk screws.

Permanent fixing: Fix labels permanently in place.

Refer to drawings, BOQ and Electrical schedules for details and locations of all fixtures, fittings and cabling.