# water services

Worksection application

This worksection is applicable to simple hydraulic installations in which the hydraulic design will be undertaken by the contractor without the involvement of a specialist hydraulic consultant. It deals with hot and cold water services, sanitary plumbing and drainage, stormwater, natural gas and LP gas installations.

References to services that do not form part of the project works (e.g. LPG systems) should be deleted.

See the Commentary for important cautionary notes on the use of this worksection.

Related material located elsewhere in NATSPEC

Related material may be found in other worksections. See for example:

- Service trenching.

- Roofing for roof plumbing.

Worksection(s) on which this worksection relies

The following worksections must be included, with this worksection, to provide a complete specification:

- General requirements.

Material not included in NATSPEC

Some projects may include items not covered by NATSPEC. For these you may need to create new text, modify this text or use an applicable worksection.

Worksection cross-referencing

Other worksections that cross reference this worksection are:

- None.

Documenting this and related work

You may document this and related work as follows:

- Show the locations of hose reels on the drawings.

- Show the location and type of sanitary fixtures on the drawings.

- Roof plumbing should be covered in the Roofing worksection and detailed on the drawings.

- Locate subsoil drains on the drawings.

- Show the location and arrangement of solar hot water heaters on the drawings.

- Show locations and types of gas appliances on the drawings.

## General

### Aims

#### Responsibilities

Provide water services systems subject to the site and other constraints below:

The system design may be described in terms of the performance required.

For contractual reasons this summary should not attempt to be a 'Scope of Work' or to imply that it includes ALL work although the content may appear to be very similar to what has traditionally been included in 'Scope of Work' clauses.

Do not use vague phrases like 'to the complete satisfaction of the superintendent' or blanket phrases like 'and all other work necessary to compete the contract'.

On completion the installed systems should be verified according to the performance parameters established. Expand or edit to suit the project. The list of headings is not exhaustive but corresponds generally to the content of this worksection.

- Cold water services: Connect the cold water supply system to the water source with a stop valve at the connection point. Provide the water source if required to suit the particular conditions as defined on the drawings. Provide the cold water installation to the draw-off points or connections to other services.

This is typical text. Edit to suit the project.

- Hot water services: Provide the hot water installation from the cold water connection points to the draw-off points or connections to other services.

This is typical text. Edit to suit the project.

- Hose reel system: Provide the hose reel system where defined on the drawings and in the BOQ.

Describe the required system. Delete if not applicable.

- Sanitary plumbing and drainage: Provide the plumbing and drainage system where defined on the drawings and in the BOQ.

Describe the required system.

- Stormwater: Provide the stormwater system where defined on the drawings and in the BOQ.

Describe the required system.

- Subsoil drainage: Provide the subsoil drainage system where defined on the drawings and in the BOQ.

Describe the required system. Delete if not applicable.

Include the name of the gas, either 'Natural gas' or ' Liquefied petroleum gas' and pressure. (This worksection is only applicable to these gas types.) Include the source of supply and extent of the installation. If LPG, include the storage arrangements. As these may be leased include supply and payment arrangements. Delete if not applicable.

Describe the site constraints on the hydraulic services.

See the Commentary for more information and suggestions on constraints.

List worksections cross referenced by this worksection. (General requirements references the other general worksections e.g. Metals and prefinishes do not repeat them here.) You may also wish to direct the contractor to other worksections where there may be work that is closely associated with this work.

The Hydraulic general requirements worksection should not be deleted as it contains material on which this worksection depends.

Some water systems must be maintained to AS/NZS 3666.2, under the BCA. For more advice on microbial control, refer to SAA/SNZ HB32.

This definition is based on the wording in the Plumbing Code of Australia but expanded to include natural gas. The Network Utility Operator is also commonly known by names like the supply authority, water board etc.

The Definitions subclause can be edited to suit the project or deleted if not required.

### Inspection

#### Notice

Give sufficient notice so that inspection may be made of the following:

- Underground pipework prior to concealment.

- Above ground pipework prior to concealment.

See the Commentary for other possible inclusions.

### Submissions

#### Execution details

Before starting the respective portions of the installation, submit the following for approval from the Employers representative:

- Embedded services: Proposed method for embedding services in concrete walls or floors or chasing into concrete or masonry walls.

- Fixing of services: Typical details of locations, types and methods of fixing of services to structure.

- Inaccessible services: If services will be enclosed and not accessible after completion, submit proposals for location of service runs and fittings.

- Proposals for location of exposed piping.

#### Samples

Provide samples listed in the Water services samples schedule.

## Execution

Refer to the Water system piping schedule for details of all pipe types.

### Installation generally

#### Accessories

Provide the accessories and fittings necessary for the proper functioning of the systems, including taps, valves, outlets, pressure and temperature control devices, strainers, gauges and pumps.

Isolating valves: provide valves so that isolation of parts of the system in the event of leaks or maintenance causes a minimum of inconvenience to building occupants.

#### Arrangement

Edit to suit project and ensure intended access is shown on the drawings and that the plant is arranged to permit inspection, maintenance and removal.

In hospitals and similar situations extend to exclude locations over patients who may not be able to move to avoid leaks.

Ensure that access to meet statutory requirements is shown on the drawings. This is particularly true of high level equipment and roof mounted equipment. See AS 1470, AS 1657, AS/NZS 1892.1 and AS/NZS 2865 for relevant requirements.

Services and equipment: Locate and arrange so that:

- Failure of plant and equipment (including leaks) does not create a hazard for the building occupants and causes a minimum or no damage to the building, its finishes and contents.

- maintenance operations can be carried out in a safe and efficient manner, with a minimum of inconvenience and disruption to building occupants and without damaging adjacent structures, fixtures or finishes.

#### Embedded pipes

The embedding of pipes under pressure in concrete is widely regarded as poor practice and one to be avoided. Some standards such as AS 2118.9 prohibit embedding entirely while others discourage the practice. The precautions in AS 2896 are used here for situations where embedding cannot be avoided. The Concrete in situ worksection requires that concrete not be poured until pressure testing has been successfully completed.

Do not embed pipes that operate under pressure in concrete or surfacing material of a building without prior written approval. If embedding is approved:

- Install in continuous lengths without fittings wherever possible.

- Do not lay across joints between adjoining sections of concrete through which reinforcement does not extend.

- Pressure test and rectify leaks before the concrete is poured.

#### Penetrations and fixing

See also BCA Clause F5.6 and Specification F5.2 for restrictions on chasing etc. intended to limit sound transmission.

Limitations: Do not penetrate or fix to the following without prior approval:

- Structural building elements including external walls, fire walls, fire doors and access panels, other tested and rated assemblies or elements, floor slabs and beams.

- Membrane elements including damp-proof courses, waterproofing membranes and roof coverings.

Fire rated building elements: Seal penetrations with a system that maintains the fire rating of the element.

Membranes: If approval is given to penetrate membranes, provide a waterproof seal to the approval of the Employers representative between the membrane and the penetrating component.

#### Piping

Install piping in straight lines, plumb and to uniform grades. Arrange and support the piping so that it remains free from vibration and water hammer, while permitting movement in both structure and services. Keep the number of joints to a minimum. Prevent direct contact between incompatible metals.

Concealment: If practicable, conceal piping and fittings requiring maintenance or servicing so that they are accessible within non-habitable enclosed spaces such as roof spaces, subfloor spaces and ducts. Provide at least 25 mm clearance between adjacent pipelines (measured from the piping insulation where applicable).

Cover plates: Where exposed piping emerges from wall, floor or ceiling finishes, provide cover plates of stainless steel or non-ferrous metal finished to match the piping.

For buildings supported independently of the underlying ground, differential movements can occur between the suspended ground floor of the building and the ground in which the pipes are buried. Examples include piered slabs constructed on fill-as-formwork or on void formers on reactive ground (also referred to as expansive soil).

The movement control joint is most appropriately located at the point where the pipe is last effectively restrained by the building (either at the point of building-in or at the last supporting strap where the pipe is hung from the structure).

Pipe support materials: To be the same as the piping or galvanized or non-ferrous metals, with bonded PVC or glass fibre woven tape sleeves where needed to separate dissimilar metals.

#### Pits

Location: Install below-ground water meters, control valves and gas regulators in concrete access pits with removable pit covers.

Internal dimensions: To give 300 mm clear space all around the fittings in the pit.

Concrete: Grade M-200, 100 mm thick, with reinforcement fabric.

Pit covers: To be minimum of 5mm thick steel covers with finger holes for easy removal.

Installation: Grade floor to a point on one side and drain to the stormwater drainage system. Carry the pit walls up to 50 mm above finished ground level. Cast in the pit cover frame flush with the top. Trowel the top smooth.

#### Valve boxes

Location: Install underground isolating valves in concrete access pits with removable pit covers.

Identification: Mark the box covers with the name of the service.

### Installation of fixtures

#### General

Accessories: Use manufacturer's brackets and accessories where these are available and suitable for the mounting substrate.

Protection: Deliver fixtures to site protected from damage under site conditions by coatings, coverings and packaging. Remove only sufficient protection to permit installation.

#### Installation

If critical show dimensions such as mounting heights and set out on the drawings. Make sure that the dimensions conform to the requirements of applicable standards and codes such BCA and the AS 1428 series.

Connections: Connect to each fixture supply and waste services. Install plumb and level.

Cutting and fitting: If it is necessary to cut and/or fit substrate to install an item carry out this before the surface is finished or painted. Remove items when required for painting and protect until re-installed. Reinstall when painting and finishing is complete. Cap or plug the open ends of pipes.

Substrate and fixings: Before installation make sure that the substrate to which the fixtures are to be installed is adequate. In solid walls confirm adequacy of the material at fixing locations.

Additional text and/or details on the drawings may be required to ensure fixing details are adequate for the substrate materials involved and likely loads, including those from possible abuse.

### Painting, finishes and marking

#### Exceptions

Do not paint chromium or nickel plating, anodised aluminium, glass reinforced plastic, stainless steel, non-metallic flexible materials and normally lubricated machined surfaces.

#### Finishes

Finish exposed piping, including fittings and supports, as follows:

- In internal locations such as toilet and kitchen areas: Chrome plate copper piping with bright finish.

- Externally and steel piping and iron fittings internally: Paint.

- In concealed but accessible spaces (including cupboards and non-habitable enclosed spaces): Leave copper and plastic unpainted except for identification marking. Prime steel piping and iron fittings.

Valves: Finish valves to match connected piping.

#### Marking and labelling

Specify project marking systems, detailing what is to be marked and how.

Mark services and equipment to provide a ready means of identification.

- Locations exposed to weather: Provide durable materials.

- Pipes, conduits and ducts: Identify and label.

Consistency: Label and mark equipment using a consistent scheme across all services elements of the project.

### Hot and cold water services

#### Fittings and accessories

Provide the fittings necessary for the proper functioning of the water supply system, including taps, valves, backflow prevention devices, temperature control devices, strainers.

AS/NZS 3500.4 clause 1.9.2 requires water that is supplied to sanitary fixtures used primarily for personal hygiene purposes in early childhood centres, schools, nursing etc. to be ≤ 45°C and ≤ 50°C in all other buildings. It provides several acceptable solutions including thermostatic mixing valves and hot water heaters designed to deliver water at ≤ 50°C.

#### Line strainers

Type: Low resistance, Y-form bronze bodied type, with screen of dezincification resistant brass, stainless steel or monel.

Screen perforations: 0.8 mm maximum.

#### Piping insulation

The 2003 edition of AS/NZS 3500.4 includes extensive requirements for energy efficiency including piping insulation in Section 8. Maps in the standard define Climate regions form which the required insulation thermal performance can be determined.

Application: Fit insulation tightly to piping surfaces without gaps. Minimise number of joints. Insulate fittings for the same thermal resistance as the piping insulation. Install the insulation on unions and other items requiring service so that it is readily removable. Provide supports formed to fit around the insulation so the insulation thickness is reduced by < 10%.

Material: Select from the following:

- Polyester in moulded tubular sections faced with factory bonded aluminium foil laminate or integral polyester scrim.

- Polyolefin foam: Cross linked closed cell polyolefin foam faced with factory bonded aluminium foil laminate.

#### Tapware

Provide the tapware in accordance with the Sanitary fixtures schedule.

Nominate type in the Sanitary fixtures schedule if not covered by proprietary item e.g. vandal-proof, plastic, metal, glass. Finish and colour may also need to be stated. See Template specification. AS/NZS 3718 specifies requirements for metallic taps, plastic taps, handsprays, mixing taps, mechanical (non-thermostatic), tap sets and jumper valves.

Metal heads and handles: Provide brass fittings or suitably bush to prevent electrolysis and growth.

Plastic heads and handles: Provide break-resistant fittings of a compact nature, to prevent fracture and exposure of jagged or rough edges.

Tap positions: Locate hot tap to the left of or above, the cold tap.

#### Thermostatic mixing valves

See the Commentary for more information.

Water temperature regulated by a single hand control, capable of delivering water at the temperature of either of the supply systems and at any temperature in between and suitable for controlling single or multiple outlets, as appropriate. Refer to the Sanitary fixtures schedule.

Controls: Incorporate the following:

- A temperature sensitive automatic control which maintains temperature at the pre-selected setting and rapidly shuts down the flow if either supply system fails or if the normal discharge water temperature is exceeded.

### Water heaters

General requirements for installation of water heaters are specified in AS/NZS 3500.4 Section 5 and Section 6. Supplementary heating for solar systems is specified in AS/NZS 3500.4 Section 6.

Specify here requirements not shown on the drawings.

AS/NZS 3500.4 prescribes a minimum storage temperature of 60C to inhibit the growth of legionella bacteria. It further sets the maximum temperatures for the delivery at fixtures leading to the use of a tempering valve, water mixing valve or other approved device.

Refer to AS 3498 derived from parts of AS 1056, also AS/NZS 2712 (see below), AS/NZS 3350 Parts 2.21 and 2.35 and AS 4552.

#### Standard electric systems

Since 1 October 1999 all unvented electric storage hot water heaters manufactured in or imported into Australia have been required to comply with the Minimum Energy Performance Standards (MEPS) Regulations of AS 1056.2. This performance is available at www.energyrating.gov.au. Specifiers desiring greater energy efficiency could consider setting a lower maximum MEPS value. For example, the maximum heat load to AS 1056.2 for a 315 litre water delivery is 2.66 kW.h/day but heaters are available with losses as low as 2.17 kW.h/day, a reduction of almost 20%. Some heaters listed at www.energyrating.gov.au do not meet the standard.

Provide standard electrical water boilers as identified in the BOQ to locations identified on the drawings. Refer to the Water heater schedule.

This applies to electric storage heaters. Delete if gas. State the supply authority tariff concession (if any) for which the heater is to be suitable e.g. off peak.

#### Solar water systems

Provide a proprietary automatic water heater comprising solar collector and storage container, with or without supplementary heating unit and including connections, controls and necessary fittings.

### Hose reels

#### General

Provide hose reels with swivel hose guides in accordance with the Fire hose reels schedule.

Given the design impact of hose reels they should be located on the architectural drawings. For special cases consider including:

- Nozzle material: If nothing specified probably plastic but brass is also available.

- Hose material: e.g. rubber or PVC.

- Painting system: If manufacturer's standard is not sufficient e.g. full gloss, solvent-borne, interior. Refer to the Metals and prefinishes worksection for other available systems.

### Stormwater

Roof plumbing is covered in the Roofing worksection. If there are design requirements they should be covered in that worksection. Roof drainage system design is dealt with in AS/NZS 3500.3 Section 3.

#### Cleaning

During construction, use temporary covers to openings and keep the system free of debris.

#### Downpipe connections

Turn up underground drainage pipelines to finish 50 mm above finished ground or pavement level.

#### Access Pits

Cover levels: Locate the top of covers or gratings, including frames as follows:

- In paved areas: Flush with the paving surface.

- In landscaped areas: 25 mm above finished surface.

#### Stormwater drains

Preferably show the type and size of stormwater pipelines and jointing and bedding requirements on the drawings. Alternatively, requirements not shown on the drawings or specified in AS/NZS 3500.3 or the worksection, may be specified here.

See AS/NZS 3500.3 clause 2.5 for types of materials and limitations on the use of each material for stormwater installations. Consult with relevant authorities about other restrictions on the use of particular materials.

Provide stormwater drains to connect downpipes, surface drains, subsoil drains and drainage pits to the outlet point or discharge point.

Downpipe connections: Turn up underground drainage pipelines with bends to meet the downpipe, finishing 50 mm (nominal) above finished ground or pavement level. Seal joints between downpipes and drains. Alternatively, terminate downpipe minimum of 100mm above adjacent ground level and discharge water to surface run off area. Allow for scour protection to bottom of downpipe.

Show location on the drawings.

#### Lined surface drains-grated trenches

Provide precast or cast in situ concrete lined trenches with painted or galvanized steel gratings.

Show location on the drawings.

### Subsoil drains

#### General

Provide subsoil drains to intercept groundwater seepage and prevent water build-up behind walls and under floors and pavements. Connect subsoil drains to surface drains or to the stormwater drainage system as applicable.

The location of subsoil drains should be shown on the drawings. See AS/NZS 3500.3 Section 6 and Appendix M for a method of design.

Connection: Connect subsoil drains to the stormwater drainage system.

Filters: UV resistant geotextile material with a permeability ≥ 10 times that of the native soil and capable of retaining particles of 0.25 mm size. Securely fit or join the sock at each joint.

Subsoil drains: Provide proprietary perforated plastic pipe.

### Sanitary plumbing and drainage

#### Vent pipes

Staying to roof: If fixings for stays penetrate the roof covering, seal the penetrations and make watertight.

Terminations: Provide bird-proof vent cowls of the same material and colour as the vent pipe.

#### Sanitary fixtures

Provide sanitary fixtures in the Sanitary fixtures schedule complete with all accessories necessary for correct installation and use.

### Completion

This clause does not include regular maintenance, for example on thermostatic mixing valves. Add if required.

#### Testing

Hydrostatic tests: Do not install insulation until the piping has been tested. Pressure test cold and hot water services to ensure that all pipework is free from leaks. Include pipe joints, valve seats, tap washers and strainers. Repair as necessary, replace if damaged and retest.

#### Completion

Completion and testing requirements are dealt with in detail in the respective sections of the AS/NZS 3500 series and AS 5601.

Hot and cold water services: On completion, flush pipelines using water and leave them clean.

Stormwater and wastewater services: On completion, flush the system using water and leave clean.

#### Charging

On completion of installation, commissioning, and testing, fill the hot and cold water systems with water, turn on control and isolating valves and the energy supply and leave the water supply system in full operational condition.

This requires the contractor to supply the initial fill of LPG. The LPG supply contract may require otherwise.

#### Operation and maintenance manuals

These are typical provisions. Edit to suit the project.

Provide written operating and maintenance instructions containing:

- Contractor's contact details for service calls.

- Manufacturer's maintenance and operation literature.

- Description of day-to-day operation.

#### Record drawings

It is important that the record drawings show the actual, as opposed to the design, location of services, particularly buried services.

Provide a drawing of the system as installed. Show dimensions, types and location of the services in relation to permanent site features and other underground services. Include all changes made during commissioning and the maintenance period.

Diagrams: Include diagrammatic drawings of each system.

Services below ground: Where pipes and fittings are below ground show the depth and dimensioned references that will allow the future location of the service for maintenance or expansion.

Storage type: e.g. tank or cylinder.