# Generating sets

Worksection application

This worksection is applicable to the provision of proprietary, packaged, stand-by generating sets powered by reciprocating diesel engines, and includes controls and ancillary equipment. They may be self-contained, enclosed external units, or installed singly or in groups inside a building.

The requirement for a stand-by generator will be determined by the BCA, the design brief or both. The BCA considers safety requirements and the client brief may include additional loads such as computers, or patient support systems in hospitals.

Related material located elsewhere in NATSPEC

Related material may be found in other worksections. For example:

- There are no directly related NATSPEC worksections.

Worksection(s) on which this worksection relies

The following worksections must be included, with this worksection, to provide a complete specification:

- General requirements.

- Liquid fuels.

- Electrical general requirements.

- Low voltage power systems.

Material not included in NATSPEC

Some projects may include items not covered by NATSPEC. For these you may need to create new text, modify this text or use an applicable worksection.

This worksection does not cover stand alone, power generating sets (i.e. systems that provide the normal source of supply).

Worksection cross-referencing

Other worksections that cross reference this worksection are:

- None.

Documenting this and related work

The following areas of responsibility may need to be ascertained by the designer before the preparation of the contract documents (for package documentation):

- Interconnection with the main building electrical services e.g. are transfer switches to be located in the main switchgear and controlgear assemblies or the generating set control and distribution board?

- Supply and installation of the generating set control and distribution board.

- Provision of main fuel tank, piping, pumps and alarm systems. This often forms part of the mechanical services trade package. See the Liquid fuels worksection.

- Provision of exhaust system, particularly in high rise or multiple generating set installations.

- The type of cooling system required i.e. connection to cooling towers, or self contained radiators.

- The provision of silencers for generating set room cooling air.

These will require coordination with other specification worksections.

Refer to AS/NZS 3009, for guidance about the areas that require emergency power for hospital projects, and to AS/NZS 4510 for isolated medical use supply systems.

## General

### Aims

#### General

Provide proprietary packaged stand-by generating set(s) incorporating the following:

- Engine cooling system.

- Combustion air system.

- Exhaust system.

- Liquid fuel system.

- Acoustic enclosure.

- Control system.

- Connection to low voltage power system.

Delete components as necessary.

In particular the responsibility and functionality of the interface to the normal power system may need to be expanded as a separate section under Installation.

AS 3010.1 covers minimum safety standards for generating sets. It does not set out performance or construction requirements.

See AS 4509.1 for information on the safety requirements of domestic stand-alone (not stand-by) power systems which, besides generating sets, includes arrays, wind turbine generators and micro-hydro generators.

AS 4509.2 provides guidelines for the design of stand-alone power systems. AS 4509.3 covers installation and maintenance requirements of the systems.

### Interpretations

#### Definitions

Net continuous rated output (or prime rating): Net continuous electrical output available at alternator terminals, not including the electrical power consumed by the generating set’s dependent and essential auxiliaries.

Net short-time rated output (or stand-by rating): Net electrical output available from the generating set for 1 hour in every 12 hours at net continuous rated output, not including electrical power consumed by the generating set’s dependent and essential auxiliaries.

Start response time: Total elapsed time from receipt of start signal to final connection to load.

### Inspection

#### Notice

Give sufficient notice so that inspection may be made of each completed generating set and associated systems before connection to electrical services.

### Submissions

Refer to the Generator set performance schedule for details before providing technical data and drawings for any generator.

#### Technical data

Submit technical data including the following:

- Technical description and specifications of each generating set, including output curves for base load and stand-by conditions, alternator and engine data, automatic voltage regulator, synchronising and load sharing modules and auxiliaries.

AS 1359.101 clause 7.1 states that it is the responsibility of the manufacturer of the machine to interpret the results obtained by thermal endurance testing as appropriate to machine type and application.

- For dielectric tests, occasional excess current, momentary excess torque for motors, overspeed, short-circuit current for synchronous machines, etc. see AS 1359.101 Section 8.

- Net continuous rated output.

- Net short-time rated output.

- Voltage regulation grade.

- Generating set efficiency at 50%, 75% and 100% load.

- Evidence that the engine type has previously passed cold starting tests at the minimum ambient site temperature.

#### Shop drawings

Submit shop drawings indicating the following:

- Location and size of fuel tanks.

- Physical size of generating set base and clearances for maintenance.

- Location and estimated size of control and distribution boards.

- Maximum mass and overall dimensions of each separable assembly.

- Access clearances for operational maintenance and dismantling.

- Control diagrams.

- Details of control panels

- Details of foundations and anti-vibration mountings.

## Products

### General

In most cases the generating sets selected are supplied with manufacturer’s standard components. The provision of non standard items is likely to impose cost and time penalties on the project.

#### Multiple generating sets

For multiple generating sets operating in parallel, provide generating sets of the same make and type.

Delete if single generating set required.

Consider circulating currents.

Detail the project specific performance requirements for the sequencing, control and interworking of the sets to function as a single emergency power supply. Include the sequence of events to occur when normal power is restored.

#### Mounting

Mount the engine and alternator units on a common structural steel frame to support the generating set assembly and the engine local control board.

Vary if engine local control board is excluded.

#### Coupling

Directly couple the engine and generator shafts with a self-aligning type coupling, capable of transmitting the engine maximum output torque under operating conditions, including starting and overload.

### Alternators

#### General

Voltage waveform: Sinusoidal, with total wave form deviation not exceeding 10%.

May need to be varied for generating sets below 300 kV.A – see manufacturer.

Excitation: Provide self-regulated brushless type exciters.

Alternatively, directly-driven excited.

Overspeed: Withstand a speed of 1.2 times unit rated speed for both alternator and engine.

Alternator underspeed withstand: Normal operation at net continuous rated output at a speed of 0.95 times unit rated speed, without overheating.

Number of poles: 4.

Enclosure classification: IP21, with screened ventilation openings.

AS 1359.20 references AS 1939 which is superseded by AS  60529. Alternatively, IP44.

That is, self-cooled open machine, fan mounted on shaft. Alternatively, water cooled. If air cooling involves ducted air supplies and filters, specify here. If water cooling involves cooling circuits other than an integrally mounted radiator, e.g. cooling towers, piping, specify here.

Drives life expectancy. AS 2768 is based on an IEC standard. Class 180 is equivalent to Class H and corresponds to a temperature-rise limit of 125C. See AS 1359.101 Table 7.10. May vary for a.c. windings and field windings.

#### Anti-condensation heaters

Delete if not required.

Provide at least 2 anti-condensation heaters within the winding enclosure.

Rating: Rate heaters to maintain the windings and insulation at least 6C above ambient temperature when the alternator is at rest and one heater is in service.

Location: Locate a heater at each end of alternator windings in a position which allows heat transfer to the winding insulation by convection, without exceeding maximum allowable insulation temperature. Do not fix heaters to windings.

Terminations: Connect heaters to separate identified terminals within a separate accessories terminal box which is connected to a permanent supply.

Identify terminals.

Connection diagram: Provide a connection diagram for the heaters. Locate within the terminal box.

#### Winding thermistors

Provide thermistors to alternator stator windings.

Thermistor type: Positive temperature coefficient.

Thermistor temperatures:

- Engine shutdown: 160C.

- Winding temperature high pre-alarm: 140C.

#### Terminal boxes

Construction: Provide metal terminal boxes. Size to allow the current transformers, power and control cables and cable lugs to be neatly installed and terminated with necessary clearances between live parts and the box, and without placing undue strain on termination points.

Supply cable terminal box: Provide removable lid and side covers.

Terminals: Provide star connected windings. Bring both ends of each winding out to separate terminals. Establish a neutral terminal.

Sealing: Provide neoprene or bonded cork gaskets between terminal boxes and their frames and covers.

### Engines

#### General

Standards: The AS 4594 series covers internal combustion engines, but is primarily intended for the land, rail and marine transportation sector.

Two-stroke engines may be acceptable. Consider the following:

- Engine type e.g. compression ignition, petrol, etc.

- Fuel type e.g. for fuel oils Class A1 (or A2) to BS 2869, or specify the fuel and its lower calorific value.

- Engine speed e.g. 1480 r/min for a 4 pole 50 Hz generating set.

- Turbocharging limits and aspiration. Specify particular requirements, if any.

Sizing: When sizing the engine, take into account the nature of connected loads including auxiliaries, harmonics and transient operation.

Bearings: Provide front and rear main bearings, so that crankshaft alignment is not affected by dismantling of the alternator.

#### Governing

Consider the following:

- Type e.g. Type 1 (single speed governing) for normal supply systems.

- Class e.g. M3. The governing accuracy class will relate to generating set and voltage regulator characteristics, and the required system stability. For accuracy classes higher than A2, consult the manufacturer.

- Speed control adjustment required on the control panel.

Provide electronic or mechanically controlled governors which enable engines to operate continuously at 1480 r/min from no-load to the maximum rated electrical load connected to the alternator. Provide filters which ensure that harmonics or switching spikes generated by the load do not interfere with the operation of the governor, overspeed or underspeed cut out devices.

Delete if not required e.g. for mechanical governor; also a little excessive for less critical types of supply. M3 designates “high requirements of speed-governing accuracy over a wide range of engine speed”. Vary if required. Also state type of governing (1, 2, 3 or 4) and any technical requirements of governing systems. See AS 4594.4 clause 8 and Table 1.

### Fuel storage

#### General

Provide daily fuel tank capacity and bulk storage capacity to the capacities identified in the Generator set fuel tanks schedule.

### Controls

See the Commentary for more information.

#### General

Provide automatic and manual modes, or manual modes only, depending on generator set capacity to start and shut down generating sets in the selected sequence and, if operating in parallel, share the load in proportion to their rated kW capacities.

Specify selected sequence.

#### Manual sequence control

Provide controls to manually synchronise and shut-down each generating set. Include emergency stop, meters, selector switches, check sychroniser and status indicating lights.

#### Automatic start control

Provide for the following:

- When a “start” signal is received, generating sets start automatically, come on-line and, when synchronised, connect to the load.

- Connection of alternators for sequential control of load sharing/shedding.

- Shutdown of alternate machines.

#### Automatic engine shutdown

Provide for generating sets to run to suit the load demand until receipt of the mains “restored” signal is received. At this point the automatic sequenced engine shutdown signal must be activated after an adjustable time delay of 0 – 30 min.

#### Emergency and fault shutdown

Provide a shutdown control system which disconnects the alternators, and shuts down engines upon the occurrence of fault conditions.

Specify fault conditions for shutdown, and for indication e.g. low fuel, engine start failure, auxiliary starting equipment failure, engine overheating, generating set overtemperature, generating set overvoltage, generating set undervoltage or engine speed (frequency) change.

In some instances e.g. low oil pressure, a warning may be adequate.

Provide for the following conditions to register as audible and visible alarms and to cause each generating set main circuit breaker to open immediately and each generating set to immediately shutdown:

- Emergency stop push-button: Pressed.

- Generating set: Over voltage.

- Generating set: Over current.

- Engine: Overspeed.

- Engine oil pressure: Low.

- Daily fuel tank: Low.

- Jacket water temperature: High.

#### Automatic synchronising

Provide synchronising modules which automatically synchronise each incoming alternator supply frequency and phase angle to the live busbars.

Delete if not applicable.

#### Emergency stop push-buttons

Generating sets < 2 m long: Provide one push-button per generating set.

Other generating sets: Provide 2 push-buttons per generating set. Locate one on each side or locate one of the push-buttons in the engine local control board.

Type: 40 mm diameter red, palm operated type mounted in a metal wall box. Wire to disconnect the generator and immediately shut down the engine when the controls are in the automatic or manual mode.

### Control panels

#### General

Provide control panels, switchgear and controlgear assemblies required to enable the safe operation of the generating set and the interconnections with the low voltage supply service.

In a majority of cases the control panels are provided by the generating set supplier/manufacturer.

In some cases, the control systems will be incorporated into the main switchgear and controlgear assembly or generating set control and distribution board, which may be provided under a separate trade package. State if PLC is required.

Fully document the system control panel using the schedules as included in Switchboards – custom built or using the single line diagram and drawings:

Delete if not applicable.

#### Engine local control board

For each generating set, provide the following minimum level of information and equipment:

- Key operated local engine start/stop control.

- Controls for auto/off/manual/load test.

- Emergency manual shutdown.

- Speed indicator, kW meter, frequency meter, ammeter, and hours run meter.

- Indicator showing generating set under local control.

- Oil pressure indicator.

- Coolant temperature indicator.

- Automatic voltage regulator consisting of the following:

- Switch to select manual or automatic voltage control.

- Solid-state type automatic voltage regulator.

- Under and overvoltage sensing.

- Over and underspeed sensors.

### Batteries and chargers

#### General

It is preferable to have a separate battery for the control system, so that the drain during cranking does not affect power to the control systems.

Provide separate batteries and charger systems for the following:

- Engine start.

- Control and alarm functions.

#### Chargers – control and alarm batteries

Select the charger to suit the batteries supplied.

For class A sets (e.g. those backing up a UPS), the batteries should be able to charge from 50% to 95% capacity in 4 hours.

### Starting

Specify starting aids e.g. thermostatically controlled water jacket and sump heaters, time switch controlled engine lubrication.

#### Electric starting

Air starting is an alternative. Minimum allowable interval between successive start attempts may require discussion with the engine manufacturer.

Provide starter motors, batteries and chargers, and associated control equipment to automatically start each engine.

Wiring: Wire starter motors so that starter motor solenoid contacts are on the active side and field windings are at earth potential when the motor is de-energised. Provide an interlock, connected directly to the engine, to prevent the starter motor operating when the engine is running.

After 3 start attempts, with no intermediate delays, the set should lock out to allow the fault to be found.

#### Starting batteries

Locate in proprietary battery holders attached to the generating set, or on purpose-built stands next to the set and constructed of timber or other corrosion resistant material. Isolate batteries from vibration.

Capacity: Sufficient to crank the engine for 3 successive attempted starts, repeated at 5 min intervals.

Isolator: Provide a lockable isolator to prevent accidental starting.

#### Starting batteries chargers

Mains power: Connect chargers to the mains power to ensure that power is maintained to the charger under all supply conditions.

This degree of instrumentation may not be required.

### Acoustic enclosures

The clause deals with exterior generating sets and anticipates proprietary enclosure systems. Internal enclosures would be dealt with as part of the building fabric and require coordination with architectural, acoustic and mechanical consultants.

Delete if not required.

#### General

Provide weatherproof acoustic enclosures to surround generating sets, including inlet and outlet sound attenuators.

#### Sound pressure level limit

85 dB (A) at 12 locations 1 m from the enclosure exterior surface, at 1.5 m above floor level, measured with the generating set operating at constant maximum rated full load output, with doors closed and service penetrations sealed.

Designate the 12 locations or state “to be nominated by the contract administrator”.

#### Doors

Provide doors of same material as the enclosure. Provide door stays to each door.

#### Ventilation

Provide ventilation to the enclosure so that:

- With generating sets running at full rated output the enclosure temperature rise does not exceed 10C.

- Hazardous concentrations of toxic or explosive fumes and gases are prevented.

## Execution

### General

#### Plinths

Provide reinforced concrete plinths for floor mounted equipment, sized to suit equipment footprints.

#### Resilient mounts

Provide at least 6 resilient mounting blocks between the frame and the plinth.

Show on the drawings the location of the generating set and the natural frequency of the floor system. Alternatively, make provision in Tendering for requesting contractors to advise maximum static and dynamic loads, and the vibration frequencies and amplitudes of the generator set during normal operational conditions (check out the effect of the generating set operation on the building structure before approving the generating set).

#### Drip trays

Provide removable drip trays under those parts of the assembly where fuel or lubricant leakage may occur. Provide overflow outlet pipes taken to a point where a receptacle can be fitted under the pipe outlet.

Capacity: At least 1.5 times the oil capacity of the engine sump.

Material: 1.6 mm galvanized steel with brazed joints and rolled edges.

### Engine cooling

Describe the method of cooling required e.g. remote radiators, liquid cooling.

#### General

Provide a cooling system consisting of radiators, fans and pumps.

Cooling air ductwork: Connect the cooling air outlet to generator room cooling air outlet.

Delete if not required.

### Engine air intake

#### General

Filters: Provide dry type air intake filters of sufficient capacity to permit continuous engine operation for 200 hours before filter servicing becomes necessary.

Delete if not required.

Fans: Provide a fan selected for the installed system air pressure drop. Include power absorbed by the fan under site operating conditions when calculating generator output.

Installations with high air pressure drop through louvres and ductwork may require non-standard fans. The additional power absorbed by these fans effectively de-rates the generator output.

### Exhaust system

In most cases, the exhaust system is designed to meet the building design. Describe the exhaust system required, including materials, and clearly indicate various areas of responsibility (where relevant).

Specify engine exhaust discharge:

- Material.

- Silencer grade.

- Allowable noise level.

#### General

Provide exhaust piping from the engine complete with silencers, piping, ductwork, supports and expansion devices.

#### Weatherproofing

Provide weatherproof flashing, sleeves and acoustic seals where the exhaust system penetrates the roof or external walls.

### Fuel system

Refer to the Liquid fuels worksection for storage tanks, transfer pumps and piping.

In general, copper components, particularly pipe, should not be used with fuels for diesel engines because of the risk of plating the injectors.

#### Stop valves

Provide stop valves on the inlet to, and outlets from, the daily service tank.

### Completion

#### Completion tests

Testing and commissioning is an important part of the generating set installation and, in particular, the way in which the generating set interacts with the building electrical services. It is not unusual to have a generating set system that appears to function correctly until it is called upon during a power outage. Therefore testing and demonstration of the controls and sequencing are probably more important than individual tests applied to each unit.

Schedule the specific tests required for the project, including additional site tests e.g. noise measurements, high voltage tests.

For each generating set carry out the following:

- Check tightness of connections and securing devices.

- Verify correctness of operation of protection devices and systems including sensor settings. Simulate actual conditions as far as possible, in order to test responses to faults imposed.

- Cold start with the engine having been at rest for the previous 24 hours.

- Continuous operational trial consisting of:

- 4 hours at 100% rated power.

- 1 hour at 110% rated power.

- 30 min at 75% rated power.

- 30 min at 50% rated power.

- Record fuel consumption for each step of the continuous trial.

- Continuous operational trial: During the trial, measure the following at maximum intervals of 30 minutes:

- Generator kW and kVAr output.

- Generator output voltage.

- Generator output current.

- Generator output frequency.

- Oil pressure and water temperature.

Synchronisation and load sharing tests: For generating sets running in parallel perform tests to verify automatic synchronisation and load sharing including the following:

- Sequence start and shutdown of each generating set.

- Parallel operation of generating sets.

- Synchronising of generating sets.

- Operation of controls, switchgear and auxiliaries.

#### Temporary test loads

Provide test loads including power and control wiring, ancillary equipment and test instruments to achieve the kW, kvar and necessary load steps.

Consider specifying additional data relevant to control equipment items, e.g. type and rating of generating set output control, sensing voltage range and set point adjustment of the automatic starting system, the voltage adjustment range of the manual generating set voltage control, the panel controls of the automatic voltage regulator, the fault conditions applicable to the safety shutdown, fault indication, and fault annunciation systems.