## Cover
United Nations Office for Project Services
Bill of Quantities
Project: Renovations of Pharmacy Storage Block at Sanyati Mission Hospital,Mashonalands West- Zimbabwe- Lot 4
BILL No. 12 - Pharmacy Storage Block
September 2013

## contents (sub)
United Nations Office for Project Services
Bills of Quantities
Project: Renovations of Pharmacy Storage Block at Sanyati Mission Hospital, Mashonalands West- Zimbabwe: Lot 4
Bill No.12: Pharmacy Storage Block
| CONTENTS |  | PHARMACY STORAGE BLOCK
|  | A | Preliminaries - Refer Bill No. 01
|  | B | Demolitions and Prepartion Works
|  | C | Excavations & Earthworks
|  | D | Concrete Work
|  | E | Walling
|  | F | Thermal & Moisture Protection
|  | G | Metal Work
|  | H | Roof Covering, Ceiling & Roof Drainage
|  | J | Doors and Windows
|  | K | Finishes
|  | L | Painting
|  | M | Electrical Installation
N
P
|  | N | Provisional Sums
September 2013

## Summary
United Nations Office for Project Services
Bill of Quantities
Project: Renovations of Pharmacy Storage Block at Sanyati Mission Hospital, Mashonalands West- Zimbabwe: Lot 4
Bill No. 12 : Pharmacy Storage Block
SUMMARY
| Description | Amount | Amount ( Per m2) | %
|  | US $ | US $
Bill No. 12
A | Preliminaries - Refer Bill No. 01
B | Demolitions and Preparation Works
C | Excavations and Earth Work
D | Concrete Work
E | Walling
F | Thermal and Moisture Protection
G | Metalwork
H | Roofworks, Ceiling & Roof Drainage
J | Doors and Windows
K | Finishes
L | Painting Work
M | Electrical Installation
N | Provisional Sums
Summary of Bill Carried to Grand Summary ( Lot 4)
| Total Gross Floor Area (m2 ) | 50
Price per SQ. m
Price per SQ. ft
25x300mm high timber valance board fixed to edges of the portal frames including necessary fittings screws and nails etc. Rate shall include for application of approved wood preservative as directed.

## BoQ
United Nations Office for Project Services- Sudan Operations Centre
Bill of Quantities - Bill No. - 12: Pharmacy Block
Project: Renovation to Existing Pharmacy Storage Block at Sanyati Mission Hospital ( Lot 4)
Mashonalands West, Zimbabwe
Item | Description | Qty | Unit | Rate $ | Amount $
B | DEMOLITION AND PREPARATION WORKS
The following shall be taken into consideration and made provisions in pricing the Demolition & Pre-preparation Works bill:
i. | The Tenderer / Contractor shall have a joint inspection with the Engineer to identify both materials & works to be demolished / replaced before starting the demolishing & renovation works. | Note
ii. | During the joint inspection as stipulated above, The Engineer has the right to decide on the parts of the existing works which are not to be demolished and to be continued as part of the permanent works, and the Tenderer / Contractor & the Engineer shall be agreed clearly on the scope of work as per the determination of the Engineer as described above, complying with the Contract Documents, before starting the work. | Note
iii. | Any materials from the existing structures shall be removed with diligence and due care. During the cause of demolishing, all necessary precautions shall be taken to prevent any damage to works or structures which have been identified to be retained as a part of the permanent works. | Note
iv. | Any material removed from existing structures is the property of the Employer / Client & therefore all reusable materials shall be selected, listed & delivered to Employer's premises by the Contractor jointly with the Engineer's representative and as directed by the Engineer. For the purposes of interim & final payments in connection herewith, the Contractor shall keep records & present the Engineer the materials delivered to client. | Note
v. | All debris to be cart away off site as directed by the engineer. | Note
vi. | All new works are measured separately. | Note
vii. | Rate for demolishing & renovation shall include preparation of the surfaces to receive new works where applicable. | Note
viii. | The existing building conditions to be checked and proper support to be provided before commencing the demolition & renovation works. The contractor should provide adequate safety at site during the demolition works. The rate shall include carefully removal of reusable materials and handing over, providing adequate safety at site, cart away the debris from site or as directed by the engineer. | Note
Wall demolition
B.1 | Demolition of existing 200mm thick brick/ masonry wall : approximately 13m2: remove all debris arising and pile where directed. | 1 | Item
Floor demolitions
B.2 | Hack out existing cement and sand screed floor finish: V- shaped: approximately 2 square metres prepare surfaces to receive new cement and sand screed flooring : apply new floor screed, steel trowelled hard and smooth: make good any work disturbed: remove all arisings from site | 1 | Item
Wall preparation
B.3 | Hack out cement and sand rendered finish: V-shaped: approximately 3 square metres: prepare surfaces to receive new cement sand render : apply new cement and sand render including mesh wire: steel trowelled hard and smooth: make good any work disturbed: remove all arisings from site | 1 | Item
Existing metal grilles
B.4 | Carefully remove 1 No. metal grille including openable grille door: overall size 6800mm long x 2100mm high : fixed to concrete or brickwork:Store on site for hand over to the client | 1 | Item
Windows and frames
B.5 | Carefully remove 1 No. existing metal window and glass ( W1): Overall size 1600 x 1500mm high : fixed to concrete or brickwork:Store on site for re-use | 1 | Item
Doors and frames
B.6 | Carefully remove 1 No. existing single leaf wooden door and frame ( D1): size 900 x 2100mm high : fixed to concrete or brickwork: Store on site for handover to the client | 1 | Item
B.7 | Ditto: 1 No. Door frame Only ( DF) :size 900 x 2100mm high | 1 | Item
Services
B.8 | Disconect and seal off all existing electrical services: protect all service lines against damage during construction renovations | 1 | item
Electrical fittings
B.9 | Remove existing light fittings accessories ( 1 No. fan, 1 Tube light, conduits, switches) and wirings: carefully store on site for hand over to the Client or for re-use as determined by the Engineer. | 1 | item
B | Demolition and Preparation Works |  | To Summary | US $
C | EXCAVATIONS AND EARTHWORKS
Unless other wise stated, Rate quoted shall include for:-
a) back filling with selected excavated material & consolidating. Surface treatment; compaction before filling / foundation.
b) disposal of surplus soil as directed & keeping all excavations free from water unless other wise measured separately.
c) any additional excavation for working space.
d) Trees ( if any) will require protection
Excavation & Earthworks
C.1 | Clearing and preparation of the site, removal of vegetable top soil upto a depth of about 150mm deep ( average) including cutting down of small trees not exceeding 600mm wide girth & disposing from the compound to the designated location on site | 21 | m²
Back filling around building
C.2 | Filling and raming around building with gravel or other equal and approved good quality imported material ( average 150mm deep): compact well | 4 | m³
Anti-termite treatment
C.3 | Anti - termite treatment to fillings and tops of foundations: applied in accordance with the manufacturer's printed instructions ( Treatment should be done 1.0 metres from the edges of external walls) | 42 | m²
Precast concrete slabs
C.4 | 600 x 600 x 50mm Precast concrete slabs: laid on and including 50mm thick well compacted sand bed | 20 | m²
C | Excavation and Earth Works |  | To Summary | US$
D | CONCRETE WORKS
a | Rate shall include for form work depositing, handling, hoisting into position, vibrating, curing etc. and making good after removal of formwork etc. | Note
b | Reinforcements are paid separately unless otherwise specified in the item | Note
c | Rate shall include for supplying and laying of gauge 1000 polythene on ground, where concrete is in direct contact with ground, before pouring concrete unless other wise measured separately. | Note
In Situ Concrete
D.1 | Supplying and placing of Gr.25 concrete as specified to Ground beams as directed: include forming 1 No. pocket size 150mm deep x 200mm wide in existing blockwork | 0.21 | m³
D.2 | Ditto: Tie beams: including forming 2 No. pockets in existing wall each size 100mm deep x 200mm wide | 0.21 | m³
D.3 | Ditto: sloped ramps; well tamped | 0.13 | m³
Reinforcement: (All provisional)
| Rate to include for supplying, cleaning, cutting, bending, fabricating, placing and the provision of all necessary temporary fixings and supports etc. including binding wires, bends, hooks, tying wires, chairs, distance blocks, steel separators/spacers (designed laps and m.s. chairs if any included in quantities) | Note
High Tensile steel reinforcement (to BS 4449 and characteristic strength fy = 460N/mm2) and Mild steel reinforcement ( to BS 4449 and characteristic strength fy = 250N/mm2)
D.4 | Y8 mild steel reinforcement bars | 22 | Kg
D.5 | T12 high yield reinforcement bars | 40 | Kg
D.6 | Supplying & laying of BRC mesh fabric reinforcement Ref: A142 to B.S 4483 in ramps (Note :Rate shall include for laps & wastage) | 3 | m²
Formwork
D.7 | Formwork to vertical sides: ground beams | 3 | m2
D.8 | Ditto: Roof tie beams | 3 | m2
D.9 | Ditto: vertical edges of ramps: 75-100mm wide | 4 | m
D | Concrete Works |  | To Summary | US $
E | WALLING
| Rate shall include for lifting, handling, weighting all rough and fair cutting, plumbing angles, normal straight cutting, forming rebated reveals and raking out joints for plastering. | Note
Brick work
E.1 | 230mm Thick well burnt bricks:reinforced at every alternate course: bedded and jointed in cement and sand (1:5 ) mortar to walls externally ( One brick) | 23 | m²
E.2 | Fired Clay Brick Cills to windows: 150mm x 150mm x 10mm thick : bedded in cement and sand mortar( 1:5) | 2 | m
E | Walling |  | To Summary | US $
F | THERMAL AND MOISTURE PROTECTION
a | Any Water proofing treatments required to be done by a specialized supplier with 10 year Guarantee acceptable to the Engineer and supplier to be approved by the Engineer before the procurement. | Note
Damp proof course
F.1 | Horizontal damp proof course: 230mm wide: bituminous: laid horizontally on screeded 20 mm thick (1:4) screeded beds to receive brick walling. | 5 | m
F | Thermal and Moisture Protection |  | To Summary | US $
G | METALWORK
Definitions
| “Welding” is deemed to be in accordance with the specification and for the material to which it is to be used. Gusset plates, shoe plates, ends, caps, cleats, brackets, stiffeners, bolts, etc., have been included to the rate of the associated steel work in which they occur. | Note
| a] For the description of materials and workmanship refer "Specification of works", "preambles" and "Drawings". | Note
| b] Rate shall include for | Note
| b.1] All shop fabrication work, marking, delivery, unloading, hoisting, erecting and fixing as per detail drawings. | Note
| b.2] All welds are 6mm thick fillet weld & allowance for rolling margin. | Note
| b.3] The weight of weld metal in welded constructions. | Note
| b.4] Members of any length. | Note
| b.5] Cutting to size and shape and joints in the running length. | Note
| b.6] Grinding to a smooth finish, unless otherwise required. | Note
| b.7] Machine drilled bolt, holes, bolts, nuts and washers, cleats, shoe and gusset plates and all other connections. | Note
| b.8] After fabrication wire brushed to clean the all steel surfaces and spray painted with two coats of quick drying metal primer zinc phosphate & two coats of matt anti corrosive with necessary accessories. | Note
Metal security grilles
G.1 | Window grillework to fit window opening size 1600mm wide x 1500mm high; in approved pattern: fixed to concrete or brickwork and as per UNOPS Engineer's approval (Rate shall include for painting as specified) | 5 | No
G.2 | Ditto: size 600mm wide x 900mm high | 1 | No
G | Metalwork |  | To Summary | US $
H | ROOFWORKS, CEILING AND ROOF DRAINAGE
| Rate shall include; | Note
a.01 | All, rivets, nails, clips, strips and delivering and fixing in position. | Note
a.02 | All timber shall apply Priming backs & applying two coats of an approved wood preservative before fixing. | Note
a.03 | All timber including plywood sheets shall have Final Finish; Two coat of wood preservative, two coats of primer, two coats of wood sheen spray paint. | Note
a.04 | Roof plumbing shall be measured & grouped separately; | Note
Roof Drainage
Gutters
H.1 | Supplying & fixing of galvanised eave gutters of cross section 100mm x 125mm or as specified, including all fixing accessories: complete with 4 No. outlets and 4 No stopped ends | 32 | m
H.2 | Extra over gutters for 4 No stopped ends: cross section 100mm x 125mm | 4 | No
H.3 | Extra over gutters for holes for downpipes: size 75mm x 100mm | 4 | No
Down pipes
H.4 | Supplying & fixing of 75 x 100 mm diameter rain water down pipes: fixed to concrete or block work with metal straps at 1000mm centres vertically to walls | 12 | m
H.5 | Extra over for swanneck fittings | 4 | No
H.6 | Ditto: for shoes | 4 | No
H | Roof Covering , Ceiling & Roof Plumbing |  | To Summary | US $
J | DOORS AND WINDOWS
a | The work shall include supply, fabricate and installation of doors, windows, to be finish as per the respective specification & drawings. | Note
b | Drawings and specifications | Note
b.01 | The contractor shall submit shop drawings for the approval of the Architect & Engineer, prior to fabrication. | Note
b.02 | The contractor shall refer to all relevant specifications and drawings prior to pricing and it shall be his responsibility to complete the said works to the entire satisfaction of the Engineer at no additional cost. | Note
b.03 | All samples shall be provided for Engineer's approval prior to purchase of material. | Note
b.04 | Where swing doors has been specified prices shall include for provisions of floor hinges. | Note
c | Rates shall include;
c.01 | Hoisting and fixing in position, drilling and making good. | Note
c.02 | Brass nails, brass screws, rawl plugs etc,. | Note
c.03 | Framing together all work in accordance with the best practices. | Note
c.04 | Final Finish; Two coats of primer, two coats of approved gloss spray paint. | Note
c.05 | Rate to include for providing sundry items related to the door & windows like glass blocks etc.. where necessary as a Architectural feature to the door or window. | Note
c.06 | Rate shall include for 5mm thick clear float glass/ wired glass /tinted glass /translucent glass as appropriate to suit the respective doors and windows as shown in the drawings. | Note
d | Rates shall include for fixing frame, door sash / window casement brass fixing screws, lock sets with 3 keys manufactured in Europe to be used on all doors.
g | Sizes
g.01 | The sizes given in the drawings and description of Bill of Quantities are finished sizes and subject to same permitted in the specifications. | Note
g.02 | The contractor shall check the measurement of openings physically at the site before fabricating the doors & windows. | Note
g.03 | Mullions and transoms as appropriate. The sizes are as given in the detail drawing. | Note
h | Ironmongery
h.01 | All the locks shall be union / Yale or approved equivalent supplied by authorized dealer appointed by the manufacturer & approved by the Architect. | Note
h.02 | All ironmongery shall be heavy quality brass of approved European manufacture subject to approval of the Architect, ironmongery samples should be submitted for approval. | Note
j | Painting / Final Finish
j.01 | Unless otherwise stated all surface of doors and windows and casements shall be finished with , two coats of red oxide primer, two coats of approved anticorrosion paint. | Note
Doors
J.1 | Metal door: 44mm: double leaf : size 1500mm wide x 2030mm high, 2 No. equal leaves each size 750mm wide x 2030mm high : complete with 300mm wide x 3mm thick welded metal vents at the top: 200mm mm wide x 4mm thick steel door frame fully welded and mitred at corners: infilled with 3mm diameter sheet metal : include for all necessary door locks and any required iron mongery, priming coat & fixing to concrete, brickwork or blockwork: as Door Type D1 | 1 | No
J.2 | Grilled door ( D2 ): single leaf, single swing: size 900 x 2100mm high: comprising of 50mm metal framework welded: infilled with 35mm diameter grilles welded at 100mm centres vertically, including all necessary door locks, iron mongery, final finish and fixing to concrete or blockwork: make good any disturbed work | 1 | No
Windows
J.3 | Take out from Store: Clean and install metal Window Type W1, size 1600mm x1500mm high overall: supply and fix any necessary necessary fasteners, iron mongery, final finish, & fixing to concrete or brickwork | 1 | Item
Glazing
J.4 | Glazing to steel sashes: include putty: 4mm thick clear sheet glass | 4 | m²
J | Doors & Windows |  | To Summary | US $
K | FINISHES
a | The contractor is advised to refer to the specification prior to pricing of this section of work | Note
b | The rate shall include for all temporary rules, screeds, grounds etc. for raking out joints of new brick work or hacking new concrete for key, internal & curved angles, joints between different surfaces arises quirks, inter sections between curved or irregular surfaces, etc. and all making good around pipes, sanitary fittings & the like. | Note
c | All samples shall be provided for approval by the Engineer prior to purchase of materials. | Note
Wall Finishes
Internal wall finishes
K.1 | Cement and sand (1:1:5) plaster set in Rhino set: finished smooth with lime putty or approved equivalent on internal faces, on brickwalls or concrete surfaces. | 23 | m²
External wall finsishes
K.2 | One coat of cement & sand (1:5) plaster finished semi rough with wood float on external faces, on brickwalls or concrete surfaces | 10 | m²
K | Finishes |  | To Summary | US $
L | PAINTING
a | Rate shall include for preparation of surface cleaning down, smoothing, knotting, stepping etc. protection of floors and fitting, removing & replacing door and window, furniture, and cleaning windows etc.upon completion. | Note
b | Paint shall be from approved colour with approved manufacturer. | Note
Wall painting
L.1 | Touch up walls: prepare and apply one coat of primer and two coats of weather shield emulsion PVA based paint of approved colour and quality to external faces of walls | 10 | m²
L.2 | Touch up: prepare and apply one coat of primer and two coats of PVA emulsion paint of approved colour and quality to internal faces of walls | 45 | m²
Plinth Painting
L.3 | Prepare and apply one coat of primer and two coats of weather shield paint of approved colour and quality to external faces of brick walls : all to match existing | 3 | m²
Wood preservative
L.4 | Prepare and apply two coats of wood preservative : to existing trusses and other roof structural timber surfaces. | 34 | m²
Metal windows and grilles
L.5 | Prepare and apply one coat of primer and two finishing coats of high gloss metal paint of approved colour and quality to windows and grilles | 20 | m²
Metal doors and grilles
L.6 | Prepare and apply one coat of primer and two finishing coats of high gloss metal paint of approved colour and quality to metal doors | 9 | m²
Rainwater sundries
Prepare and apply one coat of primer and two finishing coats of high gloss metal paint of approved colour and quality to:
L.7 | Rainwater downpipes | 4 | m²
L.8 | Gutters | 9 | m²
L | Painting |  | To Summary | US $
M | ELECTRICAL INSTALLATIONS
a | Except where specifically stated, all costs associated with provision of all holes, openings, chases, ducts and other builders' work required for installation and make them good, shall be included in the rates. | Note
b | Testing and commissioning of the electrical installation is to be carried out by the contractor and Cost of such testing and reports to be included in the rates unless otherwise mention separately. | Note
c | All types of fittings, materials, painting and finishes shall be approved by the Engineer prior to installation. | Note
Prime Cost Sum
M.1 | Allow a Prime Cost Sum of US Dollars Two Thousand ( US $ 2000) for Electrical Installations and the Supply of Fittings as per UNOPS Engineer's Instructions | 1 | Sum
M.2 | Add: a Percentage (% ) for Profit |  | %
M.3 | Add a Sum for Attendance | 1 | Sum
M | Electrical Installation |  | To Summary | US$
N | PROVISIONAL SUMS
a | The work to be done and or materials to be provided which is covered by the following Provisional Sums form part of the Works and shall be completed within the Time for Completion for the applicable Section or Portion of the Works. | Note
b | Provisional Sums and the associated items for Contractor's overheads and profit set down below shall be deducted from the Contract Sum and the value of work done and/or Materials provided to which such Provisional Sums relate shall be determined as follows: | Note
c | In respect of those parts of the Works described below as to be carried out by the contractor, nominated supplier, nominated sub contractor under the Engineers instruction, the said value shall in each case comprise: | Note
| (i) the actual amount paid or due to be paid by the Contractor to the nominated supplier or nominated Subcontractor, on the instructions of the Engineer: plus | Note
| (ii) in respect of the associated items for Contractor's overheads and profit set down below, an amount being a percentage rate of the actual amount paid or due to be paid as aforesaid, calculated at the rate inserted below against the applicable item. | Note
d | In respect of those parts of the Works not described below as to be carried out by Nominated Supplier or Nominated Subcontractors, the Engineer shall ascertain and determine by measurement the value of work done and/or Materials provided to which the applicable Provisional Sum relates in accordance with Clause (Valuation of Variation Orders) of the Conditions of Contract. | Note
e | Those parts of the Works covered by the following Provisional Sums are to be carried out by the Contractor, Nominated Supplier, Nominated Subcontractors or any other nominated authority , as determined by the Engineer. | Note
Builder's Works
N.1 | Allow a Provisional sum of US Dollars One Hundred ( US $ 100) for Builder's Works in Connection with Air Conditioner ( 1 No.) | 1 | PS
N.2 | Allow provisional sum of US Dollar Five Hundred ( US $ 500) to cover possible additional costs due to any item not covered in the measured Bills of Quantities | 1 | PS
N | Provisional Sums |  | To Summary | US $

## helping data-prices (hidden)
UNOPS - United Nations Office for Project Services | [8 empty] | NEW CONSTRUCTIONS
Bill of Quantities - Bill No. 02 | [8 empty] | Electrical Work | = | 7928.1
Project: xxxxxxxxxxxxxxxxxxxxxxxxxxxx
Government of Southern Sudan | [8 empty] | Bore Hole & Water Tank | = | 4241.6
[9 empty] | Civil Works | = | 231765.55 | - | 14021.7 | = | 217743.85
Item | Trade |  | Level | Description | Qty | Unit | Rate US$ | Amount US$ | Septic Tank & Sockage Pits | = | 1852
A | D |  |  | Excavation and Earth Work |  |  |  |  | Unit Rate for Electrical works | = | 24.02
| D |  |  | Unless other wise stated, Rate shall include for |  |  |  |  | Unit Rate for Civil works | = | 659.83
| D |  |  | a) back filling with selected excavated material & consolidating. Surface treatment; compaction before filling / foundation.
| D |  |  | b) disposal of surplus soil as directed & keeping all excavations free from water unless other wise measured separately.
| D |  |  | c) any additional excavation for working space.
A1 |  |  |  | Excavation & Earthwork Supports
A1.1 | D |  |  | Provisional amount for bulk excavation for site levelling as directed by the Engineer, maximum up to 1.5m deep in any material except rock requiring blasting, rate shall include for removal of surplus soil as directed, with in the site. | 5625 | m2 | 2.83 | 15918.75
A1.2 | D |  |  | Excavation of pits for column foundations up to 1.5m deep in any material except rock requiring blasting and removal of surplus as directed. | 5 | m³ | 5.28 | 26.4
A1.3 | D |  |  | Excavation of trenches for wall foundations up to 1.5m deep in any material except rock requiring blasting and removal of surplus as directed. | 43 | m³ | 5.28 | 227.04 | REHABILITATIONS
A2 |  |  |  | Filling & Back filling |  |  |  |  | (It is assumed that the existing foundations and walls are being used as it is)
A2.1 | D |  |  | Filling under columns foundation with gravel or other approved quality imported filling material. Spreading, watering and well ramming in 150mm. Layers. | 4 | m³ | 9.24 | 36.96 | Electrical Work | = | 7928.1
A2.2 | D |  |  | Filling under floors with gravel or other approved quality imported filling material. Spreading, watering and well ramming in 150mm. Layers. | 120 | m³ | 9.24 | 1108.8 | Bore Hole & Water Tank | = | 4241.6
A3 | D |  |  | Antitermite treatment |  |  |  |  | Civil Works | = | 155334.09
[9 empty] | Septic Tank & Sockage Pits | = | 1852
A3.1 | D |  |  | Anti - termite treatment to building area to approved specialist contractor's specification and technical literature (Rate to include for 5 years warranty to be issued ) | 355 | m2 | 6.6 | 2343
[9 empty] | Unit Rate for Electrical works | = | 23.32
A |  |  |  | Excavation and Earth Works |  | To Summary | US$ | 19660.95 | Unit Rate for Civil works | = | 456.86
B |  |  |  | Concrete Work
| F |  |  | Rate shall include for form work depositing, handling, hoisting into position, vibrating, curing etc. and making good after removal of formwork etc. | Note
| F |  |  | Reinforcements are paid separately unless otherwise specified in the item | Note
| F |  |  | Rate shall include for supplying and laying of gauge 1000 polythene on ground, where concrete is in direct contact with ground, before pouring concrete unless other wise measured separately. | Note
B1 |  |  |  | In Situ Concrete
B1.1 | F |  |  | supplying and placing of Gr.15 (1:3:6) concrete as specified in the drawings | 13 | m3 | 232.65 | 3024.45
GENERATOR ROOM
B1.2 | F |  |  | ditto for Gr.20 (1:2:4) concrete | 31 | m3 | 353.32 | 10952.92
B2 |  | F |  | REINFORCEMENT |  |  |  |  | Unit Rate | = | 270.96
| F |  |  | Rate to include for supplying, cleaning, cutting, bending, fabricating, placing and the provision of all necessary temporary fixings and supports etc. including binding wires, bends, hooks, tying wires, chairs, distance blocks, steel separators/spacers (designed laps and m.s. chairs if any included in quantities)
| F |  |  | Tor steel reinforcement (to BS 4449 and characteristic strength fy = 460N/mm2) and Mild steel reinforcement ( to BS 4449 and characteristic strength fy = 250N/mm2)
B2.1 | F |  | L1 | supplying and placing of r/f for concreting as specified in the drawing | 1500 | kg | 1.47 | 2205
|  |  |  | From Work | 1 | m2 | 24.57 | rate only
D
B | [5 empty] | Concrete Works To Summary | US$ | 16182.37
C | G |  |  | Masonry Work
| G |  |  | Rate shall include for lifting, handling, weighting all rough and fair cutting, plumbing angles, normal straight cutting, forming rebated reveals and raking out joints for plastering. | Note
C1 |  |  |  | Random Rubble Masonry Work
| G |  |  | Up to DPC level
C1.1 | G |  |  | 150 x 225 mm random rubble masonry work in cement sand (1:5) mortar in foundations & necessary other places. | 80 | m³ | 185.24 | 14819.2
C2 |  |  |  | Brick Work
C2.1 | G |  |  | 112mm thick walls in standard burnt clay bricks in 1:5 cement sand mortar for walls | 5 | m² | 14.86 | 74.3
C2.2 | G |  | L1 | 225mm thick walls in standard burnt clay bricks in 1:5 cement sand mortar for walls | 45 | m² | 29.71 | 1336.95
C2.3 | G |  |  | 400mm thick walls in standard burnt clay bricks in 1:5 cement sand mortar for walls | 590 | m² | 39.61 | 23369.9
C |  |  |  | Masonry Work |  | To Summary | US$ | 39600.35
D | H |  |  | Water Proofing
| H |  |  | Water proofing treatments, over well cleaned and exposed structural floors in toilet, roof slab with crystalline cement based material XYPEX or equivalent approved by the Engineer. Rate shall include for applying of water proofing to walls up to a minimum height of 100mm from the floor. Also rate shall include for applying 1:3 Cement sand rendering protective screed thickness not less than 12mm, angle fillets, surface finished with smooth neat cement finish and maintaining of necessary slopes for the floors. | Note
| H |  |  | Water proofing treatments to be done by a specialized supplier with 10 year Guarantee acceptable to the Engineer, & supplier to be approved by the Engineer before the procurement. | note
D1 |  |  |  | Water Proofing on Bath Room
D1.1 | H |  |  | supplying and applying of water proofing agent as specified in the drawing or directed by the Engineer | 15 | m² | 24.75 | 371.25
D2 | H |  |  | Damp Proof Course
D2.1 | H |  |  | Horizontal damp proof course ; consisting with two coats of approved material blinded with river sand on and including 20mm thick cement and sand (1:3) screed on rubble foundations. | 28 | m² | 8.18 | 229.04
D3 | H |  |  | Damp Proof Membrane
D3.1 | H |  |  | Horizontal damp proof membrane consisting of gauge 1000 polythene membrane laid on compacted earth filling (measured) in ground floor measured net. The rate shall include for laps & wastage. | 125 | m² | 3.1 | 387.5
D |  |  |  | Water Proofing |  | To Summary | US$ | 987.79
E | J |  |  | Structural Timber Work
| J |  |  | Note :
|  |  |  | a] For the description of materials and workmanship refer "Specification of works", "preambles" and "Drawings". | Note
J
|  |  |  | b] Rate shall include for | Note
J
|  |  |  | b.1] All shop fabrication work, marking, delivery, unloading, hoisting, erecting and fixing as per detail drawings. | Note
J
|  |  |  | b.4] Members of any length. | Note
J
|  |  |  | b.5] Cutting to size and shape and joints in the running length. | Note
J
J
E1 | J |  |  | Fabricating and erecting of Roof Frame Structure
E1.1 |  |  |  | supplying and placing of 75x100 HW timber wall plate | 11 | m | 6 | 66
E1.2 |  |  |  | supplying and placing of 50x150 HW timber ridge plate | 6 | m | 6 | 36
E1.2 |  |  |  | supplying and placing of 50x100 HW timber rafters | 35 | m | 4 | 140
E1.2 |  |  |  | supplying and placing of 50x50 HW timber purlins | 120 | m | 2 | 240
E |  |  |  | Structural Timber Works |  | To Summary | US$ | 482
F | J |  |  | Structural Metal Works
| J |  |  | Definitions
| J |  |  | “Welding” is deemed to be in accordance with the specification and for the material to which it is to be used. Gusset plates, shoe plates, ends, caps, cleats, brackets, stiffeners, bolts, etc., have been included to the rate of the associated steel work in which they occur. | Note
| J |  |  | Note :
|  |  |  | a] For the description of materials and workmanship refer "Specification of works", "preambles" and "Drawings". | Note
J
|  |  |  | b] Rate shall include for | Note
J
|  |  |  | b.1] All shop fabrication work, marking, delivery, unloading, hoisting, erecting and fixing as per detail drawings. | Note
J
|  |  |  | b.2] All welds are 6mm thick fillet weld & allowance for rolling margin. | Note
J
|  |  |  | b.3] The weight of weld metal in welded constructions. | Note
J
|  |  |  | b.4] Members of any length. | Note
J
|  |  |  | b.5] Cutting to size and shape and joints in the running length. | Note
J
|  |  |  | b.6] Grinding to a smooth finish, unless otherwise required. | Note
J
|  |  |  | b.7] Machine drilled bolt, holes, bolts, nuts and washers, cleats, shoe and gusset plates and all other connections. | Note
J
|  |  |  | b.8] After fabrication wire brushed to clean the all steel surfaces and spray painted with two coats of quick drying metal primer zinc phosphate & two coats of matt anti corrosive on necessary accessories. | Note
J
F1 | J |  |  | Fabricating and erecting framed structures
| J |  |  | Trusses and built-up girders
F1.1 |  |  |  | 150x50x2mm box iron roof frame as per drawings and specifications. | 175 | m | 32.34 | 5659.5
D
[6 empty] | Page Total Carried to Collection | US$ | 5659.5
Holding Down Accessories
F1.2 |  |  |  | Holding down accessories for portal frame, to be fixed to the column at roof end, including MS bolts, base plates, welding & other steel accessories as per the detail drawings. | 50 | nos | 25 | 1250
F1.3 |  |  |  | Allow sum for any other item required for the construction and completion of the roof framework, which are not covered under the above items. | 1 | Item | 50 | 50
D
[6 empty] | Page Total Carried to Collection | US$ | 1300
COLLECTION
|  |  |  | Page - 6 |  |  |  | 5659.5
|  |  |  | Page - 7 |  |  |  | 1300
F |  |  |  | Structural Metal Works |  | To Summary | US$ | 6959.5
G | P |  |  | Roof Covering & Roof Ceiling & Roof Plumbing
| P |  |  | Rate shall include; | Note
| P |  |  | (1) All, rivets, nails, clips, strips and delivering and fixing in position. | Note
| P |  |  | (2)All timber shall apply Priming backs & applying two coats of an approved wood preservative before fixing. | Note
| P |  |  | (3)All timber shall have Final Finish; Two coat of wood preservative, two coats of primer, two coats of wood sheen spray paint. | Note
| P |  |  | (4)Roof plumbing shall be measured & grouped separatly; | Note
G1 |  |  |  | Roof Covering
G1.1 | P |  |  | Supplying & fixing of approved colour Zn/Al roofing sheet ( 0.47mm ) on Galvanized steel purling with necessary fasteners and other fixing arrangements including capping on and Gable sides of the Roof covering (Galvanized Purling measured and paid separately) | 516 | m² | 27.96 | 14427.36
G1.2 |  |  |  | supply & fixing of heat insulation foil according to the manufacture's specifications. (rate shall include for all necessary items to complete the work.) | 490 | m²
Lip Channel Purlins
G1.3 |  |  |  | Supplying & fixing of Lip Channel purlins, 100 x 50 x 2mm, on structural steel roof trusses (measured) with all the necessary fixing arrangements. | 600 | m | 23.76 | 14256
| P |  |  | Ridges
G1.4 | P |  |  | Supplying & fixing Zn/Al ( Approved Colour) ridge cap in position complete with necessary roofing screws or hooks. | 66 | m | 18.87 | 1245.42
Valance / Barge Board
G1.5 | P |  |  | 25x300mm high timber valance board / barge board fixed to edges of the portal frames including necessary fittings screws and nails etc. Rate shall include for application of approved wood preservative as directed. | 125 | m | 12.99 | 1623.75
D
[6 empty] | Page Total Carried to Collection | US$ | 31552.53
G2 | P |  |  | Flat Roof Ceiling
| P |  |  | Supplying & fixing of plywood flat ceiling including necessary framing work. Rate shall include for necessary beadings washers and screws etc.,
G2.1 | P |  | L1 | fixing of ceiling as specified in the drawing | 275 | m² | 51.85 | 14258.75
G3 |  |  |  | Roof Plumbing
Q
Roof Gutters & Down Pipes - Zn/AL
G3.1 | P |  |  | Gauge 22 aluminium sheet valley gutter 750mm girth (approx.) bent to shape and fixed on and including 25mm thk approved type treated timber gutter boarding. Rate shall include for painting with two coats of anti-corrosive, one coat of etching primer. | 14 | m | 15.73 | 220.22
G3.2 |  |  |  | Supplying & fixing of Zn/Al square eave gutters of cross section 300mm x 175mm or as specified, including all necessary accessories, as per detail. | 112 | m | 15.73 | 1761.76
Q
G3.3 |  |  |  | Supplying & fixing of 150mm x 150mm Zn/Al square rain water down pipes with necessary accessories as per detail drawing. | 92 | m | 16.66 | 1532.72
Q
D
[6 empty] | Page Total Carried to Collection | US$ | 17773.45
COLLECTION
|  |  |  | Page - 8 |  |  |  | 31552.53
|  |  |  | Page - 9 |  |  |  | 17773.45
G |  |  |  | Roof Covering ,Roof Ceiling & Roof Plumbing |  | To Summary | US$ | 49325.98
H | K |  |  | Metal Work
| K |  |  | The work shall include supply, fabricate and installation of doors, windows and partitions out of extrusions of Al/Mg/Si Alloy designation 6080 or 6063 with powder coated surface finish having a minimum coating thickness of 60-80 microns as per the respective specification and the drawings. | Note
| K |  |  | Aluminium door sections to be of,
Sash
K
- 65mm x 40mm minimum outer rail
| K |  |  | - 100mm x 40mm minimum bottom rail
- 90mm x 40 mm minimum lock rail
| K |  |  | Frame - 70mm x 40mm minimum outer frame | Note
| K |  |  | Windows sections to be of,
| K |  |  | Outer frame - 45mm x 25mm minimum
|  |  |  | Sash Outer rail - 40mm x 25mm minimum | Note
K
|  |  |  | It shall be the Contractor's responsibility to check the sizes of all openings on site, prior to fabrication. | Note
K
|  |  |  | The contractor shall submit shop drawings for the approval of the Engineer, prior to fabrication. | Note
K
|  |  |  | The contractor shall refer to all relevant specifications and drawings prior to pricing and it shall be his responsibility to complete the said works to the entire satisfaction of the Engineer at no additional cost. | Note
K
|  |  |  | All samples shall be provided for approval by the Engineer prior to purchase of material. | Note
K
|  |  |  | Rates for windows shall unless otherwise measured separately include for all necessary locks and ironmongery of approved make as specified to match the doors and windows. | Note
K
|  |  |  | Rates shall include for approved weather strip, mastic sealant, pointing, caulking, jointing, backing etc., as specified. | Note
K
| K |  |  | Rate shall include for 5mm thick clear float glass/ wired glass /tinted glass /translucent glass as appropriate to suit the respective doors and windows as shown in the drawings, stainless steel screws, rawl plugs, neoprene gaskets, Aluminium hinges and stainless steel bar hinges, fabrication and installation etc. | Note
| K |  |  | Rate shall include for door locks of English make or better, stainless steel push plates and stainless steel door handles. | Note
| K |  |  | Where swing doors has been specified prices shall include for provisions of floor hinges. | Note
| K |  |  | Rate to include for providing sundry items related to the door & windows like Glass blocks etc.. where necessary as a Architectural Feature to the door or window. | Note
H1 |  |  |  | Doors
H1.1 | L |  |  | Door type D1, size 1000x2500mm high overall, comprising of 100 x 75 mm aluminium door frame & 32mm thick PVC coated door sash as per detail drawing . Rate shall include for all locks, iron mongery, final finish, & fixing to concrete or brickwork, all as per detail and to the approval. | 10 | nos | 423.5 | 4235
H1.2 | L |  |  | Door type D2, size 900x2500mm high overall, comprising of 100 x 75 mm aluminium door frame & 32mm thick PVC coated door sash as per detail drawing . Rate shall include for all locks, iron mongery, final finish, & fixing to concrete or brickwork, all as per detail and to the approval. | 2 | nos | 381.15 | 762.3
H1.3 | L |  |  | Door type D3, size750x2100mm high overall, comprising of 100 x 75 mm aluminium door frame & 32mm thick PVC coated door sash as per detail drawing . Rate shall include for all locks, iron mongery, final finish, & fixing to concrete or brickwork, all as per detail and to the approval. | 5 | nos | 343.04 | 1715.2
H2 |  |  |  | Windows Fixed Glass & Fanlights
H2.1 | L |  |  | Window type W1, size 1200x1600mm high overall, comprising of 100 x 75 mm aluminium window frame & 32mm thick glazed aluminium window sash as per detail drawing. Rate shall include for all necessary fasteners, iron mongery, final finish, & fixing to concrete or brickwork, all as per detail and to the approval. | 31 | nos | 337.92 | 10475.52
H2.2 | K |  |  | Fanlight type F1, size 500x900mm high overall, comprising of 100 x 75 mm aluminium window frame & 32mm thick glazed aluminium top hung window sash with opaque glass as per detail drawing. Rate shall include for all necessary fasteners, iron mongery, final finish, & fixing to concrete or brickwork, all as per detail and to the approval. | 5 | nos | 84.48 | 422.4
H |  |  |  | Metal Work |  | To Summary | US$ | 17610.42
I | T |  |  | Floor ,Wall & Ceiling Finishes
| T |  |  | The contractor is advised to refer to the specification prior to pricing of this section of work | Note
| T |  |  | The rate shall include for all temporary rules, screeds, grounds etc. for raking out joints of new brick work or hacking new concrete for key, internal & curved angles, joints between different surfaces arises quirks, inter sections between curved or irregular surfaces, etc. and all making good around pipes, sanitary fittings & and the like. | Note
| T |  |  | All samples shall be provided for approval by the Engineer prior to purchase of materials. | Note
I1 | T |  |  | Wall / Ceiling Finishes
I1.1 | T |  |  | 15mm thick cement & sand (1:5) plaster finished semi rough with wood float on external faces, on brick / concrete surfaces | 560 | m² | 18.74 | 10494.4
I1.2 | T |  |  | 15mm thick cement lime sand (1:1:5) plaster finished smooth with lime putty or approved equivalent on internal faces, on brick / concrete surfaces. | 535 | m² | 20.62 | 11031.7
Wall Tiling
I1.3 |  |  |  | Supplying & fixing of approved ceramic wall tiles, size 300x200x7mm or any other approved size and colour fixed with straight joints both ways in coloured grout to match with the tiles and including 25mm. thick cement and sand 1:3 screed bedding on concrete floors. | 38 | m² | 35 | 1330
I2 | T |  |  | Floor finishes
I2.1 | T |  |  | 20mm. thick cement and sand 1:3 screed finished smooth with coloured cement floating. | 275 | m² | 20.62 | 5670.5
Skirting
I2.2 | T |  |  | 100mm high 12mm thick skirting in 1:3 cement sand mortar, projected or finish to walls and finished including forming grooves and smooth with coloured cement floating. | 24 | m² | 52.3 | 1255.2
| T |  |  | Plinth Plaster
I2.3 | T |  |  | 20mm. thick cement and sand 1:3 plinth plaster finished smooth with coloured cement floating. | 77 | m² | 20.62 | 1587.74
D
[6 empty] | Page Total Carried to Collection | US$ | 31369.54
| T |  |  | Ceramic floor tiling
I2.5 | T |  |  | Supplying & fixing of non-slip, homogeneous ceramic floor tiles, from a reputed and accepted manufacturer, size 200x200x7mm or any other approved size and colour fixed with straight joints both way in coloured grout to match with the tiles and including 25mm. thick cement and sand 1:3 screed bedding on toilet floors. | 12 | m² | 35 | 420
D
[6 empty] | Page Total Carried to Collection | US$ | 420
COLLECTION
|  |  |  | Page - 12 |  |  |  | 31369.54
|  |  |  | Page - 13 |  |  |  | 420
I |  |  |  | Floor, Wall & Ceiling Finishes |  | To Summary | US$ | 31789.54
J | V |  |  | Painting
| V |  |  | Rate shall include for preparation of surface cleaning down, smoothing, knotting, stepping etc. protection of floors and fitting, removing & replacing door and window, furniture, and cleaning windows etc.upon completion. | Note
| V |  |  | Paint shall be from approved color with approved manufacturer. | Note
J1 |  |  |  | Wall & Ceiling Painting
J1.1 | V |  |  | Prepare and apply one coat of primer and two coats of weather shield paint of approved colour and quality to external faces of walls & column faces. | 560 | m² | 19.14 | 10718.4
J1.2 | V |  |  | Prepare and apply one coat of primer and two coats of emulsion paint of approved colour and quality to internal faces of walls & columns | 535 | m² | 19.14 | 10239.9
J1.3 |  |  |  | Prepare and apply one coat of primer and two coats of emulsion paint of approved colour and quality to ceiling faces | 275 | m² | 19.14 | 5263.5
J |  |  |  | Painting |  | To Summary | US$ | 26221.8
K | Q |  |  | Water Supply, Sewerage & Drainage Work (Plumbing)
| Q |  |  | Plumber
| Q |  |  | Unplasticized polyvinyl chloride (uPVC) pipes shall be used in the plumbing installation and they must confirm in every respect to the requirements of BS 4514. | Note
| Q |  |  | All fittings and pipe specials used in the plumbing installation shall be suitable and compatible with all respects to the pipe line to which fittings and specials are fixed. | Note
| Q |  |  | All sanitary fittings & fixtures shall be American Standards or approved equivalent. | Note
| Q |  |  | Rates for plumbing work shall include for:-
| Q |  |  | (a) Complying with the relevant British or any other standard as given under the specifications and with the regulations of the Local Authority and or any other relevant authorities. | Note
| Q |  |  | (b) Cutting and waste of pipes etc., and joining pipes. | Note
| Q |  |  | (c) All specials such as elbows, bends, tees, junctions, plugs, reducers and similar pipe fittings except for valves which will be measured separately. | Note
| Q |  |  | (d) Connecting pipes to sanitary fixtures and appliances. | Note
| Q |  |  | (e) Casing to brick walls etc. and making good all works disturbed. | Note
| Q |  |  | (f) Necessary screws, nails sockets, connection back nuts standard pipe fixing or supporting clips, saddles, brackets, holder bats, straps etc. | Note
| Q |  |  | (g) Connecting of different types of pipes. | Note
| Q |  |  | (h) Testing and disinfection after completion. | Note
| Q |  |  | (j) Excavation, backfilling, disposal of surplus soil for items which were specifically mentioned. | Note
| Q |  |  | Rates for sanitary fittings shall include for:-
| Q |  |  | (a) Fittings such as taps, waste water outlet, internal overflows etc. and supporting brackets, incidental materials for fixing, unless otherwise measured separately. | Note
| Q |  |  | (b) Assembling, jointing together fixing components parts, and jointing to pipes including necessary coupling and for leaving perfectly clean and in perfect working order on completion. | Note
| Q |  |  | (c) Jointing and connecting of pipes to sanitary fittings. | Note
| Q |  |  | (d) Testing and commissioning of the installation. | Note
| Q |  |  | (e) Making good of the work disturbed. | Note
| Q |  |  | (f) Submitting samples for the approval of the Engineer. | Note
| Q |  |  | (g) Protecting the works. | Note
| Q |  |  | Rates for drainage work shall include for :-
| Q |  |  | (a) Laying of pipes to falls. | Note
| Q |  |  | (b) Excavation, backfilling, disposal of surplus soil | Note
| Q |  |  | (c) All pipe specials such as bends, junctions, elbows, tees etc. | Note
| Q |  |  | (d) Connection to sides of manholes etc. | Note
| Q |  |  | (e) Providing sleeves etc., when pipes pass through walls, foundations etc. | Note
| Q |  |  | (f) Giving notices, obtaining permits, paying fees, fixing, testing and commissioning etc. | Note
K1 | Q |  |  | Cold Water Installation
| Q |  |  | Type 1000uPVC pipe with all necessary specials laid in water distribution system buried in brick walls / floor or clipped to any location where necessary.
K1.1 | Q |  |  | 20mm diameter. | 15 | m | 3.13 | 46.95
K1.2 | Q |  |  | 25mm diameter. | 15 | m | 4.34 | 65.1
K1.3 |  |  |  | 32mm diameter. | 25 | m | 5.42 | 135.5
K1.4 |  |  |  | 40mm diameter. | 25 | m | 3.78 | 94.5
K1.5 |  |  |  | 50mm diameter. | 10 | m | 4.34 | 43.4
K2 | Q |  |  | Taps and Valves
All taps and valves should be brass "Pegler" manufactured UK or approved equivalent, finish to be chrome plated or as per detail and as approved by the Engineer. Rate to include for joints to pipe work.
Bib Tap
K2.1 |  |  |  | 20mm diameter Bib Tap | 3 | nos | 6.5 | 19.5
| Q |  |  | Gate valve
K2.1 | Q |  |  | 25mm diameter gate valve. | 4 | nos | 9.75 | 39
| Q |  |  | Angle valve
K2.2 | Q |  |  | 25mm diameter angle valve. | 4 | nos | 9.75 | 39
Non Return valve
K2.3 |  |  |  | 50mm diameter non return valve | 2 | nos | 16.25 | 32.5
Drain valve
K2.4 |  |  |  | 50mm diameter drain valve | 2 | nos | 16.25 | 32.5
Check valve
K2.5 |  |  |  | 50mm diameter check valve | 2 | nos | 16.25 | 32.5
Isolating valves
K2.6 |  |  |  | 40mm diameter isolation valve. | 2 | nos | 13 | 26
K2.7 |  |  |  | 50mm diameter isolation valve. | 2 | nos | 16.25 | 32.5
D
[6 empty] | Page Total Carried to Collection |  | 638.95
Strainer
K2.8 |  |  |  | 50mm mm diameter Strainer | 2 | nos | 16.25 | 32.5
Flexible connection
K2.9 |  |  |  | 50mm diameter Flexible connection | 4 | nos | 16.25 | 65
Piping Specialties including joints to pipe work
K3 | Q |  |  | Water Tank
K3.1 | Q |  |  | Supplying and installation of 2000 liter capacity UV protected & anti microbiological protection plastishell water tank on top of RCC structure (RCC structure measured separately ) (Rate to include for 63mm diameter washout pipe with IV valve and over flow pipe as shown on the drawings.) | 2 | nos | 910 | 1820
K3.2 | Q |  |  | 63mm diameter brass gate valve for inlet pipe. | 1 | nos | 29.25 | 29.25
K3.3 | Q |  |  | 63mm diameter brass gate valve for washout pipe. | 1 | nos | 29.25 | 29.25
K3.4 | Q |  |  | Supplying and fixing of 63mm diameter approved quality ball valve | 1 | nos | 29.25 | 29.25
K3.5 | Q |  |  | Supplying and fixing of brass non-return valve for inlet pipe | 1 | nos | 29.25 | 29.25
Water tank structure
|  |  |  | Rate shall include for form work depositing, handling, hoisting into position, vibrating, curing etc. and making good after removal of formwork etc. |  | Note
K3.6 |  |  |  | supplying and placing of Gr.20 (1:2:4) concrete for water tank structure | 4 | m3 | 388.65 | 1554.6
K3.7 | F |  | L1 | supplying and placing of r/f for concreting as specified in the drawing | 200 | kg | 1.47 | 294
K3.8 |  |  |  | supplying and fixing of ladder as depicted in the drawing | 1 | LS | 100 | 100
K3.9 |  |  |  | construction of 112mm thick guard wall as depicted in the drawing | 12 | m² | 14.86 | 178.32
K4 |  |  |  | Waste and Sewage Disposal
Q
Type 600 uPVC pipe with all necessary specials laid for internal and external waste and sewage Disposal system buried in brick walls / floor, clipped to any location or laid through ground soil where necessary.
Q
[6 empty] | Page Total Carried to Collection | US$ | 4161.42
K4.1 |  |  |  | 40mm diameter. | 10 | m | 3.78 | 37.8
Q
K4.2 |  |  |  | 50mm diameter. | 10 | m | 4.34 | 43.4
K4.3 |  |  |  | Fittings to 50 mm pipe work | 5 | nos | 5.2 | 26
Q
K4.4 |  |  |  | 90mm diameter. | 10 | m | 5.45 | 54.5
K4.5 |  |  |  | Fittings to 90 mm pipe work | 5 | nos | 6.5 | 32.5
K4.6 |  |  |  | 110mm diameter. | 20 | m | 7.05 | 141
Q
K4.7 |  |  |  | Fittings to 110 mm pipe work | 5 | nos | 16.25 | 81.25
K5 |  |  |  | UPVC Pipe Ancillaries
Q
UPVC ancillaries shall be as per drawing including all connections and supports
K5.1 |  | D |  | Supplying and fixing of uPVC trapped floor clean out including Stainless Steel grating. | 5 | nos | 25 | 125
Q
K6 |  |  |  | Excavation for Pipes Works
Q
K6.1 |  |  |  | Excavation and back fill to pipe trench for normal pipe laying areas, depth not exceeding 1.0m deep as per detail drawing. (Rate shall include for screed concrete work) | 50 | m | 5 | 250
K7 |  |  |  | Sanitary Fittings
Q
Rate shall include for supplying and installation of sanitary fittings with all accessories
Q
K7.1 |  |  |  | Supplying & fixing of low level water closet with 'S' or 'P' trap outlet, approved colour, complete with 9 liter capacity cistern and fittings, seat cover, flexible connections and necessary water connection etc. | 3 | nos | 195 | 585
Q
K7.2 |  |  |  | Supplying & installation of pedestal type wash basin of approved colour, complete with ideal standard pillar tap, waste water connection with chain and plug, chromium plated bottle trap, flexible connections & necessary water connection etc. | 3 | nos | 123.5 | 370.5
Q
K7.3 |  |  |  | Supply & fixing of stainless steel kitchen sink with approved quality (European Manufactured), single bowl & single draining board including 1/2" dia chromium plated sink tap, chromium plated bottle trap & flexible connections & necessary water connection etc. | 1 | nos | 104 | 104
Q
[6 empty] | Page Total Carried to Collection | US$ | 1850.95
Supplying and installation of sanitary accessories
Q
Unless other wise stated all sanitary accessories shall be chromium plated brass or Stainless Steel approved by the Engineer.
Q
K7.4 |  |  |  | Towel Rail. | 2 | nos | 22.75 | 45.5
K7.5 |  |  |  | Toilet Paper Roll Holder | 2 | nos | 16.25 | 32.5
Q
K7.6 |  |  |  | Soap tray | 2 | nos | 9.75 | 19.5
Q
K7.7 |  |  |  | Coat hook | 2 | nos | 22.75 | 45.5
Q
K7.8 |  |  |  | Hand bidet showers for water closet areas. | 2 | nos | 16.25 | 32.5
Q
K7.9 |  |  |  | Supplying & fixing of plain glass mirrors, size 450mm x 600mm, with chromium plated clips and plugs to fix to wall including necessary accessories. | 3 | nos | 52 | 156
K8 |  |  |  | Waste & Sewer Manholes, Septic tank & Soakage pit
K8.1 |  |  |  | Construction of septic tank as depicted in the drawing. (rate shall include for all necessary items for the completion of septic tank according to the drawing) | 1 | nos | 1600 | 1600
K8.2 |  |  |  | Construction of sockage pit as depicted in the drawing. (rate shall include for all necessary items for the completion of sockage pit according to the drawing) | 1 | nos | 252 | 252
K8.3 | Q |  |  | Construction of man hole, size 600x600mm internally as per drawings with invert depth not exceeding 1000mm. (rate shall include for all necessary items for the completion of man hole according to the drawing) | 2 | nos | 42 | 84
K8.4 | Q |  |  | Construction of man hole, size 450x450mm internally as per drawings with invert depth not exceeding 1000mm. (rate shall include for all necessary items for the completion of man hole according to the drawing) | 2 | nos | 24 | 48
K9 |  |  |  | Testing & commissioning the entire installation | 1 | item | 50 | 50
[6 empty] | Page Total Carried to Collection | US$ | 2365.5
COLLECTION
|  |  |  | Page - 16 |  |  |  | 638.95
|  |  |  | Page - 17 |  |  |  | 4161.42
|  |  |  | Page - 18 |  |  |  | 1850.95
|  |  |  | Page - 19 |  |  |  | 2365.5
K |  |  |  | Water Supply, Sewerage & Drainage Work (Plumbing) |  | To Summary | US$ | 9016.82
S
L |  |  |  | Electrical Installation
S
|  |  |  | Rates in Bill of Quantities shall include all necessary materials Cables, conduits, PVC sunk box, bulbs, switches etc.) and labour required to complete the electrical installation to good working order. | Note
S
|  |  |  | Except where specifically stated, all costs associated with provision of all holes, openings, chases, ducts and other builders' work required for installation and make them good, shall be included in the rates. | Note
S
|  |  |  | Testing and commissioning of the electrical installation is to be carried out by the contractor and Cost of such testing and reports to be included in the rates unless otherwise mension seperately. | Note
S
|  |  |  | All types of fittings, materials, painting and finishes shall be approved by the Engineer prior to installation. | Note
S
L1 |  |  |  | Main Distribution Board
S
MCCB, MCB shall be manufactured by Merlin Gerin , F&G, Moler or equivalent & approved by the Engineer.
| S |  | L1
L1.1 |  |  |  | Supply and installation of switch gear cubicle made out of (2mm thickness) sheet steel enclosure (IP54) powder coated to the approval of the engineer.
| S |  | L1
Control panel for 160A . 3 Phase supply
| S |  | L1
| S |  | L1 | 01 Nos 125 A , Manual Change Over Switch
04 Nos 60 A , 4P MCCB
01 Nos 125 A , 4P 25kA, MCCB
| S |  | L1 | 01 Nos 30 A , 2P MCB
04 Nos 5 A , MCB
| S |  | L1 | 160A TPN bus bar
| S |  | L1
| S |  | L1 | Earth faulty relay
| S |  | L1 | Cu earth bar
| S |  | L1 | Voltmeter & selector switch
| S |  | L1 | Ammeter & selector switch
Phase indicator lamps
Surge arrestors
| S |  | L1 | Indicator bulbs
|  |  |  | Wiring & other installation cost | 1 | item | 975 | 975
D
[6 empty] | Page Total Carried to Collection | US$ | 975
S
L2 |  |  |  | Sub Distribution Board (DB-001)
| S |  | L1
L2.1 |  |  |  | Supply and installation of switch gear cubicle made out of (2mm thickness) sheet steel enclosure (IP54) powder coated to the approval of the engineer with following equipment.
S
Control panel for 60A . 3 Phase supply
| S |  | L1
03 Nos 32A , 2P RCCB (30mA)
03 Nos 40A , 2P RCCB (30mA)
01 Nos 40A , 3P RCCB (30mA)
| S |  | L1 | 01 Nos 60A , 3P RCCB (30mA)
15 Nos 10 A , 1P MCB
01 Nos 16 A , 1P MCB
03 Nos 20 A , 1P MCB
03 Nos 15 A , 2P MCB
03 Nos 40 A , 2P MCB
04 Nos 40 A , 3P MCB
01 Nos 60 A , 2P MCB
| S |  | L1
| S |  | L1 | Set of Cu bus bars with neutral
| S |  | L1 | Cu earth bar
| S |  | L1 | Phase indicator lamps
|  |  |  | Wiring & other installation cost | 1 | item | 712 | 712
| S |  | L1
L3 |  |  |  | Final Circuit Wiring
| S |  | L1
Rates for final circuit wiring shall include all necessary switches, sockets, materials Cables, conduits, PVC sunk box, & junction boxes, draw wires, etc. and labour required to complete the electrical installation to good working order.
| S |  | L1
Light Point Wiring
| S |  | L1
L3.1 |  |  |  | Wiring and installation (including supply of all materials) of the light points using approved type PVC insulated PVC sheathed 1 mm2 copper cable and 2.5mm2 Earth cable drawn through securely fixed concealed PVC conduit. (Switches shall be ABB / Clipsal / Orange / Tenby or equivalent) | 35 | nos | 38 | 1330
| S |  | L1
Ceiling Fans
| S |  | L1
L3.2 |  |  |  | Wiring & installation (including supply of all material, earth wire & switch) for ceiling fans using approved type 1 mm2 PVC/PVC copper cable & 2.5mm2 earth wire drawn through securely fixed PVC conduits. | 8 | nos | 38 | 304
D
[6 empty] | Page Total Carried to Collection | US$ | 2346
| S |  | L1
5ASocket Outlet
| S |  | L1
L3.3 |  |  |  | Supply & installation of 5A fused shuttered switched socket outlet to comply with relevant BS standard (Clipsal, Orange, Crabtree/ Tenby/ABB or equivalent). Wiring (including supply of earth wire & all other material required ) of above socket outlet using approved type 2.5mm2 PVC/PVC copper cable & 2.5mm2 earth wire drawn through securely fixed concealed PVC conduit in a ring circuit. | 11 | nos | 1.5 | 16.5
| S |  | L1
13ASocket Outlet
| S |  | L1
L3.4 |  |  |  | Supply & installation of 13A fused shuttered switched socket outlet to comply with relevant BS standard (Clipsal, Orange, Crabtree/ Tenby/ABB or equivalent). Wiring (including supply of earth wire & all other material required ) of above socket outlet using approved type 2.5mm2 PVC/PVC copper cable & 2.5mm2 earth wire drawn through securely fixed concealed PVC conduit in a ring circuit. | 11 | nos | 12.5 | 137.5
| S |  | L1
15ASocket Outlet
| S |  | L1
L3.5 | S |  | L1 | Supply & installation of 15A fused shuttered switched socket outlet to comply with relevant BS standard (Clipsal, Orange, Crabtree/ Tenby/ABB or equivalent). Wiring (including supply of earth wire & all other material required ) of above socket outlet using approved type 2.5mm2 PVC/PVC copper cable & 2.5mm2 earth wire drawn through securely fixed concealed PVC conduit in a ring circuit. | 2 | nos | 14.3 | 28.6
| S |  | L1
L4 |  |  |  | Fittings & Equipments
| S |  | L1
Ceiling Fans
| S |  | L1
L4.1 |  |  |  | Supply and installation of 56" sweep ceiling fan (KDK, or as specified) complete with regulator, fan hook, extension rod & attachment - Guarantee cards should be provided from accredited agent before installation. | 8 | nos | 87.75 | 702
| S |  | L1
Light Fittings
| S |  | L1
L4.2 |  |  |  | Supply and installation of 40W Single tube (1200mm long ) fluorescent fitting complete with plane Aluminium reflector and mirrored grill, choke, power factor correcting capacitor , terminal block etc. (accessories - thorn/Philips or equivalent & fitting - imported with 24 gauge sheet steel shade with powder coated finish, should be insect proof) | 35 | nos | 32.5 | 1137.5
[6 empty] | Page Total Carried to Collection | US$ | 2022.1
L4.3 |  |  |  | Supply and installation of toliet mirror lamp fitting complete with 11 W CFL (Philips or equivalent) Lamp suitable for indoor use including all other necessary accessories like terminal block etc. (accessories - thorn / Philips or equivalent & fitting - Imported with 24 gauge sheet steel powder coated, insect proof) | 3 | nos | 32.5 | 97.5
S
L5 |  |  |  | Cables & Cable Trays
S
L5.1 |  |  |  | 10mm² 4C cables from MDB to Distribution units (Cu/PVC/PVC) | 20 | m | 5 | 100
L5.2 |  |  |  | 50 x 50 mm cable tray | 50 | m | 5 | 250
S
L6 |  |  |  | Electro - Mechanical Installations
Supply and install the following factory assembled and tested plant and equipment complete with control panels and sound attenuators; including all necessary supports, anti-vibration and anti-sound fittings as Drawings & Specification , all interconnecting ductwork and connections, and electrical connections to local isolators(Power suply - M/S)
AC Units
L6.1 |  |  |  | AC units, Suspended package type, all as per specification and having capacity of:
|  |  |  | 24,000 BTU | 2 | nos | 750 | 1500
L6.3 |  |  |  | Motor
|  |  |  | Supply & fixing of 1HP motor as described in the specification (rate shall include for all necessary items for the completion of installation) | 1 | nos | 487.5 | 487.5
L7 |  |  |  | Earthining Arrangement
L7.1 |  |  |  | Supply and installation of approved type earthining system as approved by the engineer in order to keep the earth resistance below 10 ohms. The earth bar at the main distribution board should connect to the earth electrode with a 16mm2 PVC/CU cable and, should interconnect the earth bars at each DB with the main panel with 4mm² PVC/CU cables. | 1 | item | 100 | 100
L8 |  |  |  | Testing & commissioning the entire installation | 1 | item | 50 | 50
[6 empty] | Page Total Carried to Collection | US$ | 2585
COLLECTION
|  |  |  | Page - 21 |  |  |  | 975
|  |  |  | Page - 22 |  |  |  | 2346
|  |  |  | Page - 23 |  |  |  | 2022.1
|  |  |  | Page - 24 |  |  |  | 2585
L |  |  |  | Electrical Instalation |  | To Summary | US$ | 7928.1
Y
M |  |  |  | Miscellaneous & Sundry Items
M1 |  |  |  | Masonry Work
Y
M1.1 |  |  |  | Forming openings in walls and other architectural features as shown in the drawings. | 1 | item | 25 | 25
M2 |  |  |  | Glass Blocks
M2.1 |  |  |  | Supply and fixing in position 200 x 200 x 100 mm glass blocks from a reputed and accepted manufacturer to the approval of the Architect, fixed in 230mm thick masonry walls as per detail drawings. | 2 | m² | 250 | 500
M2 |  |  |  | Generator Room
M2.1 |  |  |  | construction of generator room as depicted in the drawing. (rate shall include for all necessary items need to complete the constructions) | 15 | m² | 275 | 4125
M |  |  |  | Miscellaneous & Sundry Items |  | To Summary | US$ | 4650
Z
N |  |  |  | Provisional Sums
Z
|  |  |  | The work to be done and or materilas to be provided which is covered by the following Provisional Sums form part of the Works and shall be completed within the Time for Completion for the applicable Section or Portion of the Works. | Note
Z
|  |  |  | Provisional Sums and the associated items for Contractor's overheads and profit set down below shall be deducted from the Contract Sum and the value of work done and/or Materilas provided to which such Provisional Sums relate shall be determined as follows: | Note
Z
|  |  |  | (a) In respect of those parts of the Works described below as to be carried out by the contrctor, nominated supplier, nominated sub contractor under the Engineers instruction, the said value shall in each case comprise: | Note
Z
|  |  |  | (i) the actual amount paid or due to be paid by the Contractor to the nominated supplier or nominated Subcontractor, on the instructions of the Engineer: plus | Note
Z
|  |  |  | (ii) in respect of the associated items for Contractor's overheads and profit set down below, an amount being a percentage rate of the actual amount paid or due to be paid as aforesaid, calculated at the rate inserted below against the applicable item. | Note
Z
|  |  |  | (b) In respect of those parts of the Works not described below as to be carried out by Nominated Supplier or Nominated Subcontractors, the Engineer shall ascertain and determine by measurement the value of work done and/or Materilas provided to which the applicable Provisional Sum relates in accordance with Clause (Valuation of Variation Orders) of the Conditions of Contract. | Note
Z
|  |  |  | Those parts of the Works covered by the following Provisional Sums are to be carried out by the Contractor, Nominated Supplier, Nominated Subcontractors or any other nominated authority , as determined by the Engineer. | Note
N1 |  |  |  | Supply and installation of Lightning Protection System complete in accordance with the Electrical and Mechanical Specification and Drawings. | 1 | item | 500 | 500
[6 empty] | Page Total Carried to Collection | US$ | 500
N2 |  |  |  | Shop Drawings & As Built Drawings
Z
N2.1 |  |  |  | Preparation of "Shop" drawings for for the requirment of the construction | 1 | item | 50 | 50
Z
N2.2 |  |  |  | Preparation of "As built" Drawings for the requirements of relevant authority or as directed by the Engineer. | 1 | item | 50 | 50
N3 |  |  |  | Making a bohe hole for water requiremnt in the building. | 1 | item | 750 | 750
[6 empty] | Page Total Carried to Collection | US$ | 850
COLLECTION
|  |  |  | Page - 27 |  |  |  | 500
|  |  |  | Page - 28 |  |  |  | 850
N |  |  |  | Provisional Sums |  | To Summary | US$ | 1350

## helping - data - prices (hidden)
UNOPS -United Nations Office for Project Services
Bill of Quantities - Building
Project: xxxxxxxxxxxxxxxxxxxxxxxxxxx
SUMMARY
| Description | Amount | Amount | Amount
|  | US$ | ( Per SQ.M ) | %
A | Excavation and Earth Work | 19660.95 | 57.83 | 9%
B | Concrete Work | 16182.37 | 47.6 | 7%
C | Masonry Work | 39600.35 | 116.47 | 17%
D | Water Proofing | 987.79 | 2.91 | 0%
E | Structural Timber Works | 482 | 1.42 | 0%
F | Structural Metal Works | 6959.5 | 20.47 | 3%
G | Roof Covering, Roof Ceiling & Roof Drainage | 49325.98 | 145.08 | 22%
H | Metal Work | 17610.42 | 51.8 | 8%
I | Floor, Wall & Ceiling Finishes | 31789.54 | 93.5 | 14%
J | Painting Work | 26221.8 | 77.12 | 12%
K | Water Supply, Sewerage & Drainage Work | 9016.75 | 26.52 | 4%
L | Electrical Installation | 7928.1 | 23.32 | 3%
M | Miscellaneous & Sundry Items | 4650 | 13.68 | 2%
N | Provisional Sums | 1350 | 3.97 | 1%
Summary of Bill Carried to Grand Summary
231765.55
| Total Gross Floor Area (m2 ) | 340
| Price per SQ. m | 669.53
| Price per SQ. ft | 62.22
25x300mm high timber valance board fixed to edges of the portal frames including necessary fittings screws and nails etc. Rate shall include for application of approved wood preservative as directed.

## Sheet1 (hidden)
| Timber Beam | [8 empty] | MS Plate | [10 empty] | Angle | [8 empty] | plate
| 100 x200 mm |  |  | 100x250 |  |  | 150 x250 |  |  | 12 mm MS plate |  |  | 08 mm MS plate |  |  | 06 mm MS plate |  |  | 05 mm MS plate |  | 50x75x6mm L Angle |  |  | 100x50x6mm L Angle |  |  | 50x50x6mm L Angle |  |  | 40x6mm steel plate | [8 empty] | M12 bolt
| Length | Nos. | Total | Length | Nos. | Total | Length | Nos. | Total | Area (m²) | Nos. | Total | Area (m²) | Nos. | Total | Area (m²) | Nos. | Total | Area (m²) | Total | Length (m) | Nos. | Total | Length (m) | Nos. | Total | Length (m) | Nos. | Total | Length (m) | Nos. | Total | Length (m) | Nos. | Total | Length (m) | Nos. | Total | Nos | Nos. | Total
Member Length (m) / Area (m²) | 6 | 1 | 6 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 4 | 2 | 8
| 3.12 | 2 | 6.24 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 2 | 4 | 8
| 1.56 | 2 | 3.12 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
| 1.5 | 1 | 1.5 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
|  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
[20 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 |  |  | 0
[20 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 |  |  | 0
[20 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 |  |  | 0
[20 empty] | 0 | [8 empty] | 0 | [8 empty] | 0 |  |  | 0
[29 empty] | 0 | [8 empty] | 0 |  |  | 0
[29 empty] | 0 | [8 empty] | 0 |  |  | 0
Total Length / Area |  |  | 16.86 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 16
Unit weight (kg/m) , (kg/m²) | [6 empty] | 19 |  |  | 94.2 |  |  | 62.8 |  |  | 47.1 |  |  | 39.2 |  | 5.6 |  |  | 6.84 |  |  | 4.47
Timber Unit rate -m Nos | 15 | [37 empty] | 1.47
Material cost |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
Timber cost |  |  | 252.9 | [37 empty] | 23.52
TOTAL WEIGHT OF THE TRUSS (KG) |  |  | 0 |  | Total Span: | 5.65
Cost |  |  | 422.92 |  | Cost per m: | 74.85
Material |  |  | 0
Timber cost |  |  | 276.42
Fabrication & Handling |  |  | 0
Fabrication & Handling |  |  | 91.22
Painting |  |  | 55.28
Erection |  |  | 0