## Sheet1
Appendix 1
RFP Title: Renovation of Main electrical rooms flooring & ventilation system at WHO Regional Office in Egypt
RFP 8/2024/23
Main Electrical rooms renovations
| Item | Unit | Quantity | Unit price (USD) | Total price (USD)
Civil works
1 | chipping of the existing slab,disposal of debris , pouring new RCC (one mesh of Ø 6mm steel works) slab with thickness of 10cm sloped to 8cm with bonding additives to ensure boding to old slab, with new two layers of epoxy paints rated for outdoors use | LS | 1 |  | 0
Steel doors mdofication
2 | Modifcation of the existing steel doors to reduce its height by 10-13cm; with addition of new steel epoxy painted hollow box section below the door for structural support, repainting of the doors & all other accessories to finish the works | No. | 7 |  | 0
RCC floor beams
3 | cast in situ of RCC floor beams with cross section of 200x200mm with Ø12mm steel rods ncluding formwork, spacers, supports, and all necessary accessories and preparation work. | m | 18 |  | 0
Axial Inline fan
Supply & install of factory assemled fan sesctions, manufactured by S&P,Greenheck or (approved eual) complete with electrical connections, flexible connectors, hanger,supports, motors suitable for high temperature operation and all other accessories to finish the works
4 | Fan section (5,850 CFM) at ESP 0.35 Inch with 3 phase motor | No. | 1 |  | 0
5 | Fan section (4,500 CFM) at ESP 0.35 Inch with 3 phase motor | No. | 3 |  | 0
6 | Fan section (4,600 CFM) at ESP 0.35 Inch with 3 phase motor | No. | 2 |  | 0
7 | Inline fan (700 CFM) at ESP 0.25 Inch with 3 phase motor | No. | 1 |  | 0
8 | Inline fan (1,000 CFM) at ESP 0.25 Inch with 3 phase motor | No. | 1 |  | 0
Sheet metal duct works
Supply & install of factory fabricated sheet metal duct works complete with hangers,supports,fittings,flexible connections,duct liners,turning vanes, duct mounted access doors,high quality sealants, supporting duct frames and all other accessories
9 | Sheet metal duct work (according to SMACNA, only net quantities to be paid) | Kg | 1300 |  | 0
Replacement of existing MCCs
10 | Replacement of the existing MCC with new breakers,contactors,push buttons, internal wiring, lamps, IP-54 enclosure with high quality components manufactured by schneider or approved equal | LS | 1 |  | 0
New Thermostat
11 | Supply & install of new industrial thermostat instead of existing ones that will operate the fan at a set point to be specified by the operator (manufactured by siemens or approved equal) | No. | 9 |  | 0
Demolish & dismanlte works
12 | Demolsih & dismanle of the existing fans, duct works to be modified & handing over of dismantled items to the client | LS | 1 |  | 0
Testing & balancing
13 | Provide all labor and materials required to complete the testing and balancing required according to the specification through a certified third party company with all materials scaffoldings and all accessories to finsih the work | LS | 1 |  | 0
Total (USD) |  |  |  |  | 0
Notes
1 | Contractor must perform a site visit prior to bid submission to assess site conditions
2 | contractor shall provide shop drawings and material submittals and samples for approval prior to the start of works
3 | contractor to provide as built drawings before the handing over of the works
4 | contractor to provide all connections required for the installation of DDC control fieled devices
5 | All hangers,supports, steel works shall be painted with high quality epoxy paints
6 | Safety procedures to be followed during execution and safety of all workers shall be the contractor liability