## Registration Center-Basateen
REQUEST FOR QUOTATION - RFQ/YEMSA/SUP/2024/54 Annex D2- Financial form for Solar Power System for Registration Center - Basateen, Aden
ELECTRICAL WORKS
Item | Item Detials | Unit | Qty. | Brand | Origin | Unit Price | Total Price
No. | [5 empty] | [USD] | [USD]
1 | Solar PV Module:
| Supply, install, test, and commissioning of solar panels not less than 680 W AND 144 CELLS,N Type and should be comprising of either mono-crystalline or polycrystalline; - The module type must conform with CE and IEC 61215, IEC 61730, IEC 61701 or equivalent standards; - Module conversion efficiency should be equal to or greater than 20.6 % under STC -The PV manufacturer should be approved as tier-1 - The module shall be provided with a junction box with IP67; - The PV module shall perform satisfactorily in temperature between – 40 oC to +85 oC; - The rated output power of any supplied module shall have tolerance of 0-5 W; - The supplied module DC voltage should be not less than 1000 VDC; - The product warranty should be at least 15 years. - The item and the cable must be hidden, covered with PVC pipes, and fixed on the roof. - All the works must be done according to the specifications and instructions of supervised engineer. | Pcs | 96
2 | Battery Inverter
| Supply, install, test, and commissioning of single Phase, Pure Sine wave, 240 V, 50 Hz, hybrid inverter/charger including all accessories required for parallel operation as per technical specifications; - The inverter shall produce pure sine wave form with provision for battery charger, and it can be configured individually or in parallel; - Output frequency shall be 50 Hz; - power factor 1; - Maximam operating Temperature 0-55C; - PV input voltage 100-500V; - MPPT Rang voltage 125-425 V; - DC input :48VDC and 190A; - Total Harmonic Distortion shall be less than 3%; - Designed for indoor enclosure IP 20; - Maximum efficiency should be not less than 90 % at full load; - To be certified to meet at least CE and UL marking and complaint with IEC 62109; - The device should be integrated with LED indicators and LCD display; - It shall allow adjustment of battery voltage and charging current; - The device shall allow connection to grid and/or backup generator(s); -Battery Tybe laid acid or lithium; -PV input lightining ,out put over current,out put over voltage,surge,out put shorted protection are integrated; - The charging function of the inverter/charger shall include battery charging functionality; and the inverter shall be wired in ways that make use of the inverter’s battery charging functionality if the installation includes either mains power or a diesel generator; - Protections required: AC overload and load short circuit, overvoltage, overheating and battery reverse polarity; - The inverter with MPPT type (Maximum Power Point Tracking (MPPT) type), efficiency not less than 92 %; - The inverter shall allow internet connection for remote monitoring - Product warranty shall be 5 years. | Notes
2.1 | 8 kw | Pcs | 6
3 | Solar Battery (Lithium Iron Phosphate Battery LIFE PO4) with Racks:
| Supply, install, test, and commissioning of lithium Iron Phosphate Battery LIFE PO4 bank voltage shall be 48 volts, with steel racks. - Batteries shall be 48V cell, rated voltage 51.2 V,Discharge current 100 A,Peak Discharge Current 200 A,Cut Off Discharge voltage 44.8 V,Charge Current not less than 60 A,Charge Voltage 58.4 V Weight not less than 125kg; - Battery cyclic life shall be at least 6000 cycles at 80% depth of discharge (DOD)and 8000 cycle at 50% depth of discharge(DOD); - Reliable performance at high operating temperatures of up to 50° C; - Wires connected to batteries shall utilize appropriately sized and rated lugs or terminals and proper hardware; battery shall be installed in a secured, well-ventilated powerhouse, or in an outdoor rated enclosure; - Optional for LCD display or communication; - Product warranty shall be 5 years; warranty certificates shall be provided by the manufacturer. | Notes
3.1 | Battery Capacity : 200 Ah;10kwh | Pcs | 6
4 | DC Combiner Box (DCCB)
| Supply, install, test, and commissioning of DC Combiner Box - 5 input,2 output DC Combiner Box; - The DCCB to be provided for termination of connecting cables. The DCJB shall be made of metal or UV resistant material and suitable for outdoor installation,IP65, - All wires/cables must be terminated through cable lugs; - DC output circuit: In accordance with the maximum current X 1.25, 1000 VDC breaker; - DC fuse rating for each string:1000V, 15 A; - Built in surge protection device; - Product warranty shall be 2 years. | Pcs | 6
5 | DC Cabling
| Supply, install, test, and commissioning of DC Cabling -1kV, Flexible stranded copper per EN 60228 , TUV certified. Insulation: Halogen-free, thermoset polyolefin. Jacket : low smoke non-halogenated, flame retardant, oil, abrasion, chemical and sunlight resistant meeting UL 44, UL 854. - All cables shall be marked properly according to approved design so that cable can be easily traced& identified and hidden; - PV array to battery circuit(s) to be sized for maximum 3% voltage drop at rated array power (Imp); - Cable ends connections are to be made through suitable lugs or terminals, crimped properly & with use of cable glands;this item is including the cables and cable trays -Perforated type Galvanized steel cable trays, cable tray covers, clamping bolts and other cable tray accessories such as coupler plates, bends, tees, reducers, vertical elbows in manufactured accordance with ASTM A653 SS, Grade 33, coating designation G90. | Notes
5.1 | (2C*10 sqr.mm) (Red& Black) | Role | 4
5.2 | (1C*50 sqr.mm) (Red& Black) | Role | 4
5.3 | (1*50 mm2) red 1000v flex to connect from inverters to DC breaker and to batteries installed inside trench and end are connected via proper terminals | M | 24
5.4 | (1*50 mm2) black 1000v flex to connect from inverters to DC breaker and to batteries installed inside trench and end are connected via proper terminals | M | 24
6 | AC Cabling
| Supply, install, test, and commissioning of AC Cabling -Stranded type, TUV certified, double insulation material 1kV XPLE/PVC/CU - All cables shall be marked properly according to approved design so that cable can be easily traced and identified and hidden; - All outdoor exposed wiring to be protected from UV radiation and physical damage, all cabling above ground should be suitably mounted inside cable trays with proper covers; - XLPE insulated and PVC sheathed single or multi core flexible copper cables meeting IEC 60227 and IEC 60502; - Cable ends connections are to be made through suitable lugs or terminals, crimped properly & with use of cable glands. - include remove tiles and excavation trench as per site condition | Notes
6.1 | 4*16 mm | M | 60
7 | Battery DC Breakers Box
| Supply, install, test and commissioning Battery DC Breakers Box has : - 2* 250A 2P DC breakers (in and out); - DC 1000V,10KA; - the box including all the required accessorries. | Pcs | 6
8 | Earthing System
| Supply, install, test and commissioning Earthing System as per technical specifications and drawings including cabling, cable lugs, earthing rods and all required accessories - Each array structure of the PV modules should be grounded properly; - All metal casing/shielding of the system and its components should be thoroughly grounded; -Earthing pit - Earth resistance should be tested in presence of site engineering representative by calibrated earth tester, the earth resistance should not be more than 5 Ohm. - Earthing installation in accordance with the IEE Wiring regulations, BS 7671 - All conductive materials shall be copper. - The size of conductor shall be according to table 54.7 of IEE – BS 7671 – IEC 60365-5-54. -All should be according to the specifications and instructions engineer | L.S | 1
9 | Lighting Protection System
| Supply, install, test and commissioning Lighting Protection System as per technical specifications and drawings including cables, mast and all required accessorries. - lighting arrester shall be copper. - All metal casing/shielding of the system and its components should be thoroughly grounded; -Earthing pit - Earth resistance should be tested in presence of site engineering representative by calibrated earth tester, the earth resistance should not be more than 5 Ohm. - Earthing installation in accordance with the IEE Wiring regulations, BS 7671 - All conductive materials shall be copper. - The size of conductor shall be according to table 54.7 of IEE – BS 7671 – IEC 60365-5-54. | L.S | 1
10 | protection board
| Supply, install, test, and commissioning of : - under and over voltage protection device both of them input and output. - under and over current protection device both of them input and output. - AC circuit breaker MCB 100A single phase for input and out put main gride electricity. | Pcs | 1
11 | Other Components
11.1 | Supply, install, test and commissioning ball Extinguisher - Warranty: at least two years. | Pcs | 6
11.2 | Supply, install, test and commissioning of 1.5 RT(18000 Btu) Spilt Air Condition dual inverter type include alternate operation and temperature control unit with all wiring requirements; - Adjustable fan speed; - Voltage: 220-240; - Frequency: 50 Hz; - Single phase; - Noise level shall not exceed 45 dB; - Star rating 3 star or above; - Suitable for wall mounting; - Outdoor unit shall be housed inside painted metal gage made of mild steel. -The product warranty should be at least 1 years and 5 year for providing spare part | Pcs | 2
11.3 | Supply, install, test and commissioning of 1 RT(12000 Btu) Spilt Air Condition dual inverter type include alternate operation and temperature control unit with al wiring requirements; - Adjustable fan speed; - Voltage: 220-240; - Frequency: 50 Hz; - Single phase; - Noise level shall not exceed 45 dB; - Star rating 3 star or above; - Suitable for wall mounting; - Outdoor unit shall be housed inside painted metal gage made of mild steel. The product warranty should be at least 1 years and 5 year for providing spare part | Pcs | 6
11.4 | Supply, install, test and commissioning of 0.75 RT(9000 Btu) Spilt Air Condition dual inverter type include alternate operation and temperature control unit with al wiring requirements; - Adjustable fan speed; - Voltage: 220-240; - Frequency: 50 Hz; - Single phase; - Noise level shall not exceed 45 dB; - Star rating 3 star or above; - Suitable for wall mounting; - Outdoor unit shall be housed inside painted metal gage made of mild steel. The product warranty should be at least 1 years and 5 year for providing spare part | Pcs | 10
11.5 | Ceiling fans AC/DC : - Supply and installation of ceiling fans fixed to ceilings with low power consumption 40 w , 220V 1400 mm , 3 blades ; with remote controlling speed and all supplies and connections inside black plastic pipes (PVC) and bent - in the bending areas - using springs, copper wires and boxes with fixing with screws, up to the assembly point with all necessary components to complete the work as required and approved by the supervise engineer. | Pcs | 10
11.6 | Supply and installation of Steel Iron frame including RCC bases to carry solar planes as a group according to the needed arrays, the solar panels in each array should be with an angle of 15 degree with vertical supports,. Installing steel iron bases consist of a main holder with two circular columns of galvanized iron with a thickness of 4 mm fixed and anchored in concrete bases (50x50x80) cm. The iron column is carrying an iron frame the iron frame (which carry the panels) is made of (50x50x5) mm mild steel(iron) angle, fixed and installed on an iron beams of (30x60) mm. The structure is surrounded by an iron profiles frame of (30x60) mm carried by two flange steel beams of (40x80) mm, install of a steel box (35x60x50) cm that covers the wires combiner box, install of hinges and closed with a lock and under the metal structure, the bases should be 2 m high and the steel (high quality steel) used in the base should be approved by the Engineers and can withstand all static loads, painting all iron/steel surfaces with high quality rustproofing coat. The mounting structures and the foundations must be designed structurally to be suitable to withstand all static loads (weight of modules, wind loads etc) that might occur according to the Site conditions. The mounting structure components are bonded together to guaranty potential equalization, The work includes transportation to the project site, and everything needed to complete the work according to drawing, specifications and instructions of the engineer | L.S | 1
GRAND TOTAL OF SOLAR POWER SYSTEM OF REGISTRATION CENTER IN BASATEEN in USD |  |  |  | 0