## FO
ANNEX C - FINANCIAL OFFER FORM
RFQ-HCR-SYR-2024-72
FOR SUPPLY, DELIVERY AND INSTALLATION OF 60KVA/50KW GENERATOR FOR UNHCR OFFICE IN SWEIDA– SYRIA.
Name of Bidder (Company):
Currency of Offer (please indicate):
| Validity of Offer: | 90 days
# | Description | QTY | UoM | Unit price DDP | Total Price DDP
1 | Generator (60KVA/50KW) Brand-new Electrical generator; capacity: 60 KVA; Engine (diesel, Key start / auto start, Prime Power: 60KVA/50KW, Standby Power 66KVA/55KW, cooling type: water cooled, speed: 1500 rpm), Alternator (3 phase, 380 V, 50 Hz, 4 poles, IP: 23, power factor: 0.8, windings: 100% copper), control panel (model year after 2023, automatic engine starting & stopping, automatic shutdown on fault condition, alarm channels: Under/Over speed, Charge alternator failure, Emergency stop, Low oil pressure, High engine temperature, Fail to start, Loss of speed sensing signal, Metering: Volts, Amps, Frequency Hz, Engine Speed RPM, Engine Oil Pressure, Engine Temperature, Plant Battery Volts, Engine Hours Run. Weather and sound-proof canopy: manufactured with a steel outer skin, and is lined with fireproof, acoustic material, min. 75db / 3m, locking doors. | 1 | Set |  | 0
2 | Automatic changeover/transfer switch (ATS): With Capacity according to the capacity of the generator, Type of operation: Auto. & Manual, 4 poles, Components: Relays, Contactors, Auxiliaries, Timers, Reader, Phase failure, Lamps, Selectors, Emergency stop, | 1 | Set |  | 0
3 | Cabling: Provision and installation of Cable 4x50 Sqm NYY, Cu/ PVC shield and PVC filling with all accessories (lugs, glands, and Etc.) and the required length, (20 m) | 20 | M |  | 0
4 | Provision and installation of Breaker MCCB 3 Phase, 3 Poles (Brass), capacity 125 A, within the metal panel and all accessories (lugs, glands, and Etc.), the new ATS should work with existing ATS of backup generator. | 1 | Unit |  | 0
5 | Provision and installation of changeover Breaker 3 Phase, 4 Poles (Brass) 125 A, with all accessories (lugs, glands, and Etc.) | 1 | Unit |  | 0
6 | Provision and installation of metal Panel suitable for MCCB breaker and changeover breaker and indicator lamps, thickness 1.5 mm at least Thermal paint with metal lock and rain cover. | 1 | Set |  | 0
7 | Installation service: Required, including all accessories (turnkey operation): (Location: UNHCR Office, As-Suwayda Governorate – Syria) | 1 | LM |  | 0
Total Cost |  |  |  |  | 0
IMPORTANT: DO NOT CHANGE THE FORMAT OF THIS FORM - All Prices/Rates shall be on an ALL INCLUSIVE basis; - The estimated values for quantities and total amounts under "rates on as-needed/by-request basis" shall be used for evaluation purposes only in order for UNHCR to compare offers; - The "Total Fixed Costs and Rates on as-needed basis" shall be fixed for the duration of the contract; - The standard payment terms of UNHCR are net 30 days upon satisfactory delivery of goods and/or services, receipt of the invoice (and supporting documents) and acceptance thereof by UNHCR. - All bank charges resulting to payments made to the Service-Provider by UNHCR Syria shall be shouldered by the Service-Provider;
By signing on this document, , which I am duly authorized to sign for, I confirm that I have read and understood all related documents as provided by UNHCR. This is also to confirm that our company shall abide by our bid until its validity expires.
(person authorised to sign on behalf of the Bidder)
Signature over Printed Name
Position Title
Date and Place Signed
STAMP OF THE COMPANY