## 1-FRONT COVER.
BILL OF QUANTITIES (BoQ)
PROJECT
Subject:
Supply, delivery and test of 3 Submersible pumps units (bowel assembly, Motors, Cables, Control panels, Raiser Pipes, etc.) Complete with all required connections, gaskets, bolts and accessories, to be delivered to National Water & Sanitation Authority Al Ghaydah Branch- NWSA- AL-GHAYDAH’s Warehouses
IN
Al Ghaydah District Al Maharah Governorate YEMEN
PACKAGE/ REFERENCE NO :
IUS-AF2-UWS-GAYD-004

## Price Quotation
Subject: Supply, delivery and test of 3 Submersible pumps units (bowel assembly, Motors, Cables, Control panels, Raiser Pipes, etc.) Complete with all required connections, gaskets, bolts and accessories, to be delivered to National Water & Sanitation Authority – Al Ghaydah Branch- NWSA- AL-GHAYDAH’s Warehouses, Al Ghaydah District - Al Maharah Governorate
IUS-AF2-UWS-GAYD-004
Bill of Quantity
General Notes: The price includes Supply, delivery and Test of 3 Submersible pumps units (bowel assembly, Motors, Cables, Control panels, etc.) complete with all required connections, gaskets, bolts and accessories, to be delivered to National Water & Sanitation Authority – Al Ghaydah Branch (NWSA-AL GHAYDAH) - NWSA- AL-GHAYDAH’s Warehouses, Al Ghaydah District - Al Maharah Governorate
Sir. No. | Description | Unit | Qty. | Rate | Cost
|  |  |  | U.S. $ | U.S. $
1 | Supplying, deliver and testing Submersible pumps and Heavy-duty submersible Motor complete with all requirements and accessories for:
Wells #: 8,9 & 10 at Fawri Water Wells Field Al Maharah Governorate
1.1 | Supplying, deliver and testing of Submersible pumps and Heavy-duty submersible Motor, under the following conditions: | Set | 3 | 0 | 0
Ø submersible pumps of Q: 54 m3/hr, H: 200 m, with all required reducers or connection pieces between pumps and risers.
Ø Heavy duty submersible motor, The diameter of the motor should not more than 8’’, borehole diameter 250 mm.
Ø Motor Power Shall not less than: 1.15 of pump power.
Ø Installation Depth (85 m)
The Submersible Pumps and Motors shall be complete with all others important feature specified in the Section of technical specification.
2 | Supplying, deliver and testing of Solar Pumping Inverter Controller with all requirements and accessories for:
Wells #: 8,9 & 10 at Fawri Water Wells Field Al Maharah Governorate
2.1 | Supplying, deliver and testing of Solar Pumping Inverter Controller, under the following conditions: | No. | 3 |  | 0
Ø Power: should be not less than 1.2 of motor power.
Ø Three phase output, voltage range 380-420 V.
Ø Efficiency: Not less than 95%.
Ø Output Frequency: 0 - 50Hz.
Ø Input DC open circuit voltage not less than 900 V.
Ø Lower level of MPP voltage shall not greater than 450 V.
Ø Upper level of MPP voltage shall not less than 850 V.
Ø Should have built in data loggers.
Ø Must be operate solar and grid at the same time.
Ø Should be equipped with Programmable inputs and outputs.
Ø Protections required: Over-Voltage, pump Over-Current, pump Over-Load, Overtemperature, pump Phase Loss, pump Short-Circuit, ground fault, solar low power, DC Input Anti-reverse, AC output unbalance and Dry run.
Ø Internet of GPS have to be provided for remote monitoring.
Ø Product warranty shall be not less than 2 years."
The Solar Pumping Inverter Controller shall be complete with all others important feature specified in the Section of technical specification.
3 | Supplying, deliver and testing of Output Reactor with all requirements and accessories for:
Wells #: 8,9 & 10 at Fawri Water Wells Field Al Maharah Governorate
3.1 | Supplying, deliver and testing of Output Reactor, under the following conditions: | No. | 3 |  | 0
Ø Rated Operating Voltage: 380V~1140V 50Hz
Ø Power: should be not less than 1.2 of motor power.
Ø Operating Frequency: 50 Hz
Ø Operating Ambient Temperature：-25℃~50℃
Ø Insulation Resistance: Core-winging, DC 1000V, resistance≥100M ohm
Ø Protection class: IP20
Ø Insulation class: F
Ø Product warranty shall be not less than 2 years.
The Output Reactor shall be complete with all others important feature specified in the Section of technical specification.
4 | Supplying, deliver and testing of PV Combiner Box (DCCB) with all requirements and accessories for:
Wells #: 8,9 & 10 at Fawri Water Wells Field Al Maharah Governorate
4.1 | Supplying, deliver and testing of PV Combiner Box, under the following conditions: | No. | 3 |  | 0
Ø Not less than 8 inputs, 1 output DC Combiner Box.
Ø The DCCB to be provided for termination of connecting cables.
Ø Suitable for outdoor installation, IP65, waterproof and anti-dust.
Ø All wires/cables must be terminated through cable lugs.
Ø DC fuse rating for each string:1000V, not exceed 20 A.
Ø Built in Reverse Protection Diode.
Ø Built in DC circuit breaker.
Ø Built in surge protection device.
Ø Product warranty shall be 2 years.
The PV Combiner Box shall be complete with all others important feature specified in the Section of technical specification.
5 | Supplying, deliver and testing of AC Control Box with all requirements and accessories for:
Wells #: 8,9 & 10 at Fawri Water Wells Field Al Maharah Governorate
5.1 | Supplying, deliver and testing of AC Control Box, under the following conditions: | No. | 3 |  | 0
Ø Enclosure class should be not less than IP65, waterproof and anti-dust.
Ø All wires/cables must be terminated through cable lugs.
Ø All required wires/cables and busbars must be included,
Ø Built in Reverse Protection Diode.
Ø Built in AC & DC circuit breakers.
Ø Built in surge protection device.
Ø Forced Air Cooling type via fans.
Ø The VFD & Output reactor must be located in.
Ø Product warranty shall be 2 years.
The AC Control Box shall be complete with all others important feature specified in the Section of technical specification.
6 | Supplying, deliver and testing of Molded Case Circuit Breaker (MCCB) with all requirements and accessories for:
Wells #: 8,9 & 10 at Fawri Water Wells Field Al Maharah Governorate
6.1 | Supplying, deliver and testing of Molded Case Circuit Breaker (MCCB), under the following conditions: | No. | 3 |  | 0
Ø MCCB Protection Type: Thermal Magnetic Based
Ø MCCB Current Rating: 100A
Ø MCCB Poles: 4 POLE
Ø MCCB Breaking Capacity: 25kA
Ø Rated Operational Voltage: 690 V AC, 500 V DC
Ø Include NEMA 3R enclosure:
· Powder-coated steel construction
· Lockable front door, wall mounted type, Direct handles, Locking devices, Auxiliary contacts and Protective plates.
· ways at least, shock and vibration proof contacts.
· Conform to BS EN 60947-3 and UL 1008 Listed.
Ø Product warranty shall be 2 years.
The Molded Case Circuit Breaker (MCCB) shall be complete with all others important feature specified in the Section of technical specification.
7 | Supplying, deliver and testing of Submersible Level Transmitter (Water level Sensor) with all requirements and accessories for:
Wells #: 8,9 & 10 at Fawri Water Wells Field Al Maharah Governorate
7.1 | Supplying, deliver and testing of Submersible Level Transmitter (Water level Sensor), under the following conditions: | No. | 3 |  | 0
Ø Measuring range: 1m-500m
Ø Working temperature: -20~60℃
Ø Shell protection: IP69
Ø Accuracy: 0.25% F.S
Ø Material: SS 304 probe, rubber wire:
Ø Product warranty shall be 2 years.
The Submersible Level Transmitter (Water level Sensor) shall be complete with all others important feature specified in the Section of technical specification.
8 | Supplying, deliver and testing of Pressure Switches with all requirements and accessories for:
Wells #: 8,9 & 10 at Fawri Water Wells Field Al Maharah Governorate
8.1 | Supplying, deliver and testing of Pressure Switches, under the following conditions: | No. | 3 |  | 0
Ø Setting range: 2 – 20 bar
Ø Contact system: TPST and SPST
Ø Electrical rating: 12 A, 400 V
Ø Electrical connection: Screw terminals
Ø Contact material: Silver
Ø Differential: Adjustable
Ø Degree of enclosure: IP43 or IP55
Ø Product warranty shall be 2 years.
The Pressure Switches shall be complete with all others important feature specified in the Section of technical specification.
9 | Supplying, deliver and testing of Submersible Cable with all requirements and accessories for:
Wells #: 8,9 & 10 at Fawri Water Wells Field Al Maharah Governorate
| Supplying, deliver and testing of Submersible Cable, under the following conditions: | Note
Ø Voltage rating:450/750VAC.
Ø Type of Conductor: copper, flexible, finely, multi stranded.
Ø Insulation: black poly chloroprene, HO7RN -F or equivalent material.
Ø All cables shall be marked properly according to approved design so that cable can be easily traced and identified.
Ø Cable ends connections are to be made through suitable lugs or terminals, crimped properly & with use of cable glands.
The Submersible Cable shall be complete with all others important feature specified in the Section of technical specification.
9.1 | Submersible Cable Size: 3 cores × 35 mm2 | m | 300 |  | 0
9.2 | Submersible Cable Size: 3 cores × 1.5 mm2 (for Level Sensor) | m | 300 |  | 0
9.3 | Cable Size: 2 cores × 1.5 mm2 (for Pressure Switch) | m | 60 |  | 0
10 | Supplying, deliver and testing of Power Cable Splice Kit with all requirements and accessories for:
Wells #: 8,9 & 10 at Fawri Water Wells Field Al Maharah Governorate
10.1 | Supplying, deliver and testing of Power Cable Splice Kit, under the following conditions: | Kit. | 12 |  | 0
Ø Conductor Amount: Multiple, Single
Ø Dielectric Strength: 500 mV
Ø Insulation Outside Diameter Range: 10 - 16 mm, 10 - 19 mm, 16 - 25 mm, 25 - 40 mm
Ø Material: Epoxy
Ø Maximum Cable Outside Diameter: 15.2 mm, 25.4 mm, 39.7 mm
Ø Maximum Conductor Size: 18.5 mm², 35 mm², 95 mm²
Ø Maximum Insulation Outer Diameter: 15.875 mm, 25.4 mm, 39.688 mm
Ø Minimum Conductor Size: 10 mm², 18.5 mm², 35 mm²
Ø Minimum Insulation Outer Diameter: 10.312 mm, 15.875 mm, 25.4 mm
Ø Product Colour: Black
Ø Product Type: Splice
Ø Splice Type: Inline
Ø Voltage: 5 kV
Ø Voltage Application: Medium Voltage
Ø Kit Contents:
· Mold Body
· Pouring Spouts
· Electrical Tape
· Resin
The Power Cable Splice Kit shall be complete with all others important feature specified in the Section of technical specification.
11 | Supplying, deliver and testing of Heat Shrink Tubing Kits with all requirements and accessories for:
Wells #: 8,9 & 10 at Fawri Water Wells Field Al Maharah Governorate
11.1 | Supplying, deliver and testing of Heat Shrink Tubing Kits, under the following conditions: | Kit. | 6 |  | 0
Ø Material: Flexible Polyolefin
Ø Colour: Black
Ø Dielectric Strength: 900 mV
Ø Voltage: 600 V
Ø Maximum Operating Temperature: 135 ℃
Ø Minimum Shrink Temperature: 100 ℃
Ø Shrink Ratio: 2:1
Ø Length of each piece: Not less than 150mm
Ø Kit Includes 102 pieces: (with the following sizes)
· Size 3/16" (4,8 mm), No. of Pieces 30
· Size 1/4" (6,4 mm), No. of Pieces 28
· Size 3/8" (9,6 mm), No. of Pieces 20
· Size 1/2" (12,7 mm), No. of Pieces 14
· Size 3/4" (19,1 mm), No. of Pieces 6
· Size 1" (25,4 mm), No. of Pieces 4
The Heat Shrink Tubing Kits shall be complete with all others important feature specified in the Section of technical specification.
12 | Supplying, deliver and testing of Riser Pipe with all requirements and accessories for:
Wells #: 8,9 & 10 at Fawri Water Wells Field Al Maharah Governorate
12.1 | Supply Riser Pipe (uPVC Super Heavy), with All Accessories Required for Installation Pump According to the following technical specification: | No. | 108 |  | 0
Ø Ø PIPE (OD): OD – 113mm (4”), ND:100mm
Ø Pipe Wall Thickness:As specified in the table for Super Heavy class.
Ø Pipe Joint System: Square Type Threads with Coupler, rubber ring and Safety lock
Ø Pipe Length: 3m
Ø Working pressure: 35 Bar
Ø Includes the following accessories:
- Lowering Fixture and Pump Guard set - (3 Set)
- Top and Bottom Adaptors / Connectors set - (3 Set)
The Riser Pipe (uPVC Super Heavy) shall be complete with all others important feature specified in the Section of technical specification.
13 | Supplying, deliver and testing of Stainless-Steel Vertical Check Valve with all requirements and accessories for:
Wells #: 8,9 & 10 at Fawri Water Wells Field Al Maharah Governorate
13.1 | Supply Stainless-Steel Vertical Check Valve, under the following conditions: | No. | 3 |  | 0
Ø Nominal Diameter (DN): 100mm
Ø Connection Type: According to the raiser pipes.
Ø Nominal Pressure (PN): PN25
Ø Material:
• Body Material: 304 Stainless Steel
• Spring Material: 304 Stainless Steel
• Valve Core: 304 Stainless Steel
• End Seal: PTFE
The Stainless-Steel Vertical Check Valve shall be complete with all others important feature specified in the Section of technical specification.
14 | Supplying, deliver and testing of Well Cap / Cover with all requirements and accessories for:
Wells #: 8,9 & 10 at Fawri Water Wells Field Al Maharah Governorate
14.1 | Supply Well Cap / Cover, under the following conditions: | No. | 3 |  | 0
Ø Diameter: 14”
Ø Min. thickness: 18 mm
Ø Material: made from A36 or equivalent CS plate
Ø Paint type: Painted by Anti-corrosion Paint at least two coats (premier and finishing layer)
Ø Other requirements:
· Fabricated with stiffeners and holes for pump and sensor cables
· Stiffeners shall be holed for lifting purposes
The Well Cap / Cover shall be complete with all others important feature specified in the Section of technical specification.
15 | Supplying, deliver and testing of Pipe Hangers & Supports with all requirements and accessories for:
Wells #: 8,9 & 10 at Fawri Water Wells Field Al Maharah Governorate
15.1 | Supply Pipe Hangers & Supports, under the following conditions: | No. | 9 |  | 0
Ø Hangers Diameter: for pipes of 4” dia.
Ø Min. thickness: 18 mm
Ø Length: more than 14”
Ø Material: made from A36 or equivalent CS plate
Ø Paint type: Hot-Dip Galvanized (50HHDG)
Ø Bolt, nuts and washers: Stainless Steel Grade A2/304
The Pipe Hangers & Supports shall be complete with all others important feature specified in the Section of technical specification.
16 | Supplying, deliver and testing of Bulk Water Meters with all requirements and accessories for:
Wells #: 8,9 & 10 at Fawri Water Wells Field Al Maharah Governorate
16.1 | Supply of Bulk Water Meters, under the following conditions | No. | 3 |  | 0
Ø Type: Horizontal (vertical where specified) helix type with completely waterproof encased gear train, magnetic transmission and registration, shielded against tampering or any external magnetic field.
Ø Sizes: Ø 4’’ (100mm)
The Bulk Water Meters shall be complete with all others important feature specified in the Section of technical specification.
17 | Supplying, deliver and testing of Double Flange Gate Valve with all requirements and accessories for:
Wells #: 8,9 & 10 at Fawri Water Wells Field Al Maharah Governorate
17.1 | Supply of Double Flange Gate Valve, under the following conditions | No. | 3 |  | 0
Ø Diameter: 4” (100mm)
Ø O-ring & gasket: EPDM
Ø Working Pressure: 16 bars
Ø Body cover: Ductile Iron GGG 40
Ø Stem (spindle): Stainless steel grade A2/304.
Ø Stem (Nut): Bronze
The Double Flange Gate Valve shall be complete with all others important feature specified in the Section of technical specification.
18 | Supplying, deliver and testing of Double Flange Non-Return Valve with all requirements and accessories for:
Wells #: 8,9 & 10 at Fawri Water Wells Field Al Maharah Governorate
18.1 | Supply of Double Flange Non-Return Valve, under the following conditions | No. | 3 |  | 0
Ø Diameter: 4” (100mm)
Ø O-ring & gasket: EPDM
Ø Working Pressure: 16 bars
Ø Body cover: Ductile Iron GGG 40
Ø Flange: B.S.4504 (PN16)
Ø Max. Service Temp.: 60°C - 70°
The Double Flange Non-Return Valve shall be complete with all others important feature specified in the Section of technical specification.
19 | Supplying, deliver and testing of Pressure Gauge with all requirements and accessories for:
Wells #: 8,9 & 10 at Fawri Water Wells Field Al Maharah Governorate
19.1 | Supply of Pressure Gauge, under the following conditions | No. | 3 |  | 0
Ø Material of Gauge Case: AISI 304 stainless steel fitted with laminated
Ø Gauge Diameter: 100mm
Ø Inner Scale: from 0 to 25 Bar
Ø Bottom Connection: ½ “
Ø Accessories:
• Isolation Stainless steel 1/2-inch Ball valve of the same pressure rating.
• In addition to the connection fittings (GI nipples, sockets, reducers, etc.)
The Pressure Gauge shall be complete with all others important feature specified in the Section of technical specification.
20 | Supplying, deliver and testing of Single Small Orifice Air Valve with all requirements and accessories for:
Wells #: 8,9 & 10 at Fawri Water Wells Field Al Maharah Governorate
20.1 | Supply of Single Small Orifice Air Valve, under the following conditions | No. | 3 |  | 0
Ø Design: Fully compliant to BS EN 1074-4
Ø Maximum operating temperature: 90°C
Ø Diameter Bottom Connection (female): 1”
Ø Nominal Pressure (PN): PN16
Ø Minimum operating pressure: 0.3 bar
Ø Accessories:
• Female threaded inlet as standard
• Ball valve isolating valve
• Ball valve isolating valve and flange
• Inlet flange
• Male threaded inlet
The Single Small Orifice Air Valve shall be complete with all others important feature specified in the Section of technical specification.
TOTAL COST OF - IUS-AF2-UWS-GAYD-004 - BOQ (USD) |  |  |  |  | 0