Section II: Schedule of Requirements:

RFQ title: Supply, Delivery, and Test New AC submersible Drop Cables with all accessories  For Water and Sanitation Local Corporations – Taiz City - Yemen.

Technical specifications for Goods and Comparative Data Table:

# Scope  :

- The project scope includes the supply, delivery, inspection, and testing of new goods as outlined in the below table and detailed in the technical specifications, bills of quantities, and other tender documents. These goods  will be delivered to the warehouses of Water and Sanitation Local Corporations/Authorities  in the specified destination cities:

| LOT 3 -Supply, Delivery, and Test New AC submersible Drop Cables with all accessories For Water and Sanitation Local Corporations – in specified destination cities - Yemen. |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Sub Project ID | Destination City | Bill Item # | Well ID | Description | Unit | Qty |
| IUS-PR-UWS-OPS-TAZ-006-LOT 3 | Taiz city | Bill#11-B--1 | - | Submersible Cable 3 cores × 35 mm2 | m | 900 |
| IUS-PR-UWS-OPS-TAZ-006-LOT 3 | Taiz city | Bill#11-B--2 | - | Submersible Cable 3 cores × 25 mm2 | m | 500 |

# GENERAL

- Delivery and unloading:  To warehouses of Local water and sanitation corporations-in specified destination cities as mentioned in the  scope above.

- Technical Documents and Certificates: Documentary evidence to prove that the material and design is according to specifications.

- Standards: All goods shall comply with the requirements of the latest issue (with up to date amendments) of the appropriate standard or standards of the American Society for Testing of Material (ASTM) British Standards Institution (BS) or International Organisation for Standardisation (ISO) standards, German Standards (DIN) or their equivalents as approved by the Purchaser. Once the Bid has been accepted and a Contract awarded, the successful Bidder shall furnish two (2) original copies of the standards with which the goods are complying in English.  If the original standards are in a language other than English, then authenticated English translations must be submitted in addition. Where reference is made to a particular manufacturer's product, such reference shall be taken only as an indication of design and quality unless otherwise stated.

- Climate:   All materials and equipment incorporated in the work shall be capable of withstanding shade temperatures of 45°C and if exposed to direct sunlight shall be capable of withstanding the additional heat gain up to 50°C , approx. 60% humidity and altitude up to 2300 m above sea level. All materials and equipment shall take into account the generally tropical conditions with occasional dust storms, intense rain storms.

- Markings:  Unless otherwise specified in the relevant standard, products are to have the following legible marks as appropriate, cast, stamped or indelibly painted:

-  Manufacturer’s name, initials and identification mark.

-  Class designation.

-  Date of manufacture.

-  Initials and number of relevant standards.

- Warranty: The supplier shall provide manufacturer’s warranty to the employer/UNOPs  that the Goods Supplied under the contract will comply strictly with the Contract and shall be first class in every case and shall be free from defects. The supplier further warrants to the Purchaser that all materials, equipment and supplies furnished by the supplier for the purpose of the goods will be new, merchantable of the most suitable grade, and fit for their intended purposes. This warranty shall remain valid for a one-year period starting of the date of the final acceptance delivery. After the final acceptance, any part of the equipment which fails or does not give satisfactory performance during this period of warranty, shall be replaced within three months from the date the Supplier has been notified to do so.All expenses involved in this connection shall be borne by the supplier who should take this into consideration when bidding.

- Technical Data/Brochures: bidders Must provide relevant technical data sheets and manufacturer catalogues  for all supplied items.

- Manufacturing and Country of origin Certificate:  All materials shall comply with specified International Standards and shall be supplied from reputable manufacturers.

- Manufacturing and test Certificates: The bidder shall submit a test certificate from the manufacturer certifying that all supplied items have been tested and that they have successfully passed the tests prescribed by the relative international standard specifications and test certificates for each item (according to serial number) shall be submitted for applicable items.

- Certification Standard: All materials supplied shall be the best of their respective kinds and in accordance with the current and relevant Standards for those particular classes of material where such standards are applicable and do not conflict with this specification.

- Transportation and Storage: Transport, handle and store all products and materials in accordance with the manufacturer’s recommendations and in a manner that prevents damage or deterioration or excessive distortion.

- The employer (UNOPS) shall have the right to reject any damaged or defective product material.

- Tests after Delivery: The Employer (UNOPS) has the right to take samples of the supplied materials, and the following tests (or any other required tests) shall be carried out in accordance with the relevant international standards or regulations by an approved laboratory at own bidder cost.

  - Material type and equipment performance

# Technical Specifications

This specification covers the design, material, construction features, manufacture, inspection, testing the performance of water Submersible deep borehole /well cables with all accessories.

- AC Drop Cables

| NO. | ITEM | SPECIFICATIONS |
| --- | --- | --- |
| 1. | Type | AC cables type H07RN-F or superior |
| 2. | Operating | suitable for drinking water |
| 3. | Size | As specified in BOQs |
| 4. | Insulation type | Double insulation |
| 5. | Heat resistant insulation | Heat resistant insulation with a thick flame retardant sheath |
| 6. | Nominal rated voltage (KV) | 450/750 - 0,6/1 |
| 7. | Conductor | tinned COPPER |
| 8. | Flexibility | CLASS 5 – acc. to IEC 60228 or equivalent |
| 9. | Insulation material | Ethylene Propylene Rubber (EPR) insulation and a Polychloroprene (PCP) outer sheath to BS 50363 or equivalant |

- SUBMERSIBLE Water level Sensor

| # | TECHNICAL ITEMS | SPECIFICATIONS |
| --- | --- | --- |
| 1 | Measuring range | 1m-500m |
| 2 | Shell protection | IP68 |
| 3 | Working temperature | -20~60℃ |
| 4 | Accuracy | 0.25%F.S |
| 5 | Material | SS 304 probe, rubber wire |

- PRESSURE SWITCHES

| # | TECHNICAL ITEMS | SPECIFICATIONS |
| --- | --- | --- |
| 1 | Used for | Water pumps |
| 2 | Setting range | 2 – 20 bar |
| 3 | Contact system | TPST and SPST |
| 4 | Electrical rating | 12 A, 400 V |
| 5 | Electrical connection | Screw terminals |
| 6 | Contact material | Silver |
| 7 | Differential | Adjustable |
| 8 | Degree of enclosure | IP43 or IP55 |
| 9 | Design | Box |

Delivery Requirements and Comparative Data Table:

| UNOPS Requirements |  | Is quotation compliant? Bidder to complete | Details Bidder to complete |
| --- | --- | --- | --- |
| Delivery time | The Bidder shall deliver the goods within 6 months after the Contract signature. | ☐ Yes ☐ No | Insert details |
| Delivery place and Incoterms rules | DAP as per Incoterms 2020 at Local water and sanitation corporations/Authority in Taiz City, Yemen. | ☐ Yes ☐ No | Insert details |
| UNOPS Right to vary requirements | At the time the Contract is awarded, UNOPS reserves the right to vary the quantity of the goods and associated services specified above, provided this does not exceed +/- [20%] , without any change in the unit prices or other terms and conditions of the RFQ. | ☐ Yes ☐ No | Insert details |