## BOQ-1&2
GLOBAL FUND ROUND 7
BILLS OF QUANTITIES FOR CONSTRUCTION OF TB LABORATORY IN UDICI
Item No. | Item Description | Unit | Quantity | Rate | Amount
| Rates shall be considered to be inclusive of all preliminary items; | Note
B | EXCAVATIONS AND EARTHWORKS
B.1 | Clearing and preparation of the site including cutting down and removal of top soil up to a depth of 150mm and disposed off as directed. | m2 | 102.96
B.2 | Excavation of trenches for wall foundations up to 1.2m deep in any material except rock requiring blasting and removal of surplus as directed. | m³ | 23.52
B.2a | Allow PC sum for relocating any service lines and maintain them in good working condition. | item | 1
B.2b | Ditto: Columns bases (9 No.) | m³ | 10.8
B.3 | Filling & Back filling
B.4 | Filling around strip foundations with selected excavated materials: ram and compact well | m³ | 12.544
B.5 | Filling under floors with 400mm thick gravel or other approved quality imported filling material, and 50mm thick sand blind. Spreading, watering and well ramming in layers. | m³ | 37.152
| Ditto- filling with 450mm thick selected excavated material well compacted | m³ | 240
B.6 | Anti - termite treatment to fillings and tops of foundations: as " Aldrex" or equal and approved insecticide treatment: applied in accordance with the manufacturer's printed instructions : include for 10 years warranty period. | m2 | 64.96
B
C | CONCRETE WORKS
In-situ Concrete
C.1 | Supplying and placing of Gr.20 concrete as specified to foundation strip footings | m3 | 3.624
C.1a | Ditto: 100mm thick ramps laid to fall. | m3 | 1
C.2a | Foundation pad Footings & stub columns. | m3 | 2.448
C.2b | Ditto: in ground beams size 200mm x 200mm | m3 | 1.568
C.2c | Ditto: to columns up to Tie beam | m3 | 1.26
C.2c | Ditto:For roof Tie beams | m3 | 1.96
C.2d | Ditto: 100mm thick floor beds. | m2 | 6.136
C.2e | Ditt: 75mm thick Conc.work tops | m2 | 6.3
C.2f | Ditto:75mm thick conc.to waiting area benches | m2 | 1.6425
Shuttering & Form Work
C.3a | Timber formwork to sides of Columns | m2 | 40.96
C.3b | Ditto:for sides of grade beams | m2 | 19.6
C.3c | Ditto: for roof tie beams | m2 | 19.6
C.3d | Ditto: for edges/soffits of floor beds,worktops | m2 | 10.0675
C.3e | Ditto: for sides & soffits of waiting area benches. | m2 | 2.3725
Mild Steel Reinforcement
C.5 | R8 bars mild steel reinforcement bars | Kg | 115.9022
C.6 | High Yield reinforcement bars (T8) at 150mm centres to conc.worktops,benches & waiting area cantilever | Kg | 47.229
C.7 | High Yield reinforcement bars (Y12) | Kg | 748.436
C.8 | Supplying & laying A BRC net for Ground floor slab: Include laps and Waste. | m2 | 64.96
C.9 | Lintel Size 200mm x 200mm in cross section: complete with 4 T12 bars and R8 bars at 300mm centres: include all required formwork. | m | 26.7
Splash Apron
In black cotton soils
C.11 | 75mm thick concrete (grade 20) 600x600mm slabs laid on 100mm sand blinding base well rammed and finished monolithically with 25mm thick cement and sand (1:3) screed trowelled smooth to gentle falls with joints pointed and including 150mm thick concrete block edge wall average 600mm deep rendered on and including 450mm x 150mm thick concrete grade 15 foundation and all necessary excavations and disposal of spoil and formwork to edge of apron. | m2 | 17.88
Masonry Work
Up to DPC level
D.1 | Solid concrete block walls in cement sand (1:5) mortar in Steps | Item | 1
D.2 | 200 mm Thick solid concrete block walls in cement sand (1:5) mortar in foundations | m2 | 70.56
Concrete block work
D.3 | 200mm thick walls in standard precast hollow cement blocks in 1:5 cement sand mortar for superstructure walls. | m2 | 93.7
D.4 | Ditto: 150mm Thick walls for work top & benches | m2 | 3.0075
D.5 | Supply and lay burnt clay, pompey grills to openings | m2 | 8
Masonry Work
THERMAL AND MOISTURE PROTECTION
Damp Proof Course
E.1 | Horizontal damp proof course: bituminous: laid horizontally on screeded 20 mm thick (1:3) screeded beds to receive block walls. | m2 | 4.22
Damp proof membrane
E.2 | Horizontal damp proof membrane :1000 gauge polythene membrane: laid on compacted fillings (measured separately) in ground floor beds. ( The rate shall include for laps & wastage). | m2 | 64.96
Thermal and Moisture Protection
F.1 | Roof truss RT1 spanning 5800mm wide, consisting of 2/50x50x4mm equal angle iron members welded to gusset plate with all necessary accessories. Rate shall include for painting as specified. | No | 4
F.2 | Roof truss RT2 spanning 4200mm wide, consisting of 2/50x50x4mm equal angle iron members welded to gusset plate with all necessary accessories. Rate shall include for painting as specified. | No | 2
F.7 | Rafters HR & VR, consisting of 50x50x4mm equal angle iron members welded to gusset plate all necessary accessories of fixing in place. Rate shall include for painting as specified. | m | 45
Purlins
F.8 | Supplying & fixing of Zed purlins, 75 x 50 x 2mm: welded to roof trusses ( measured separately)at 900mm centres: complete with all the required paint works and all necessary supports | m | 124
F.10 | Allow sum for any other item required for the construction and completion of the roof framework, which are not covered under the above items. | Item | 1
Structural Metal Works
Roof Covering
G.1 | Supplying & fixing of gauge 26 pre-painted Super VI profiled roofing sheets of approved colour: fixed with J-bolts to 75 x 50 x 2mm zed purlins ( measured separately) and rubber caping to tops of bolts | m² | 99.2
Ridges
G.2 | Supplying & fixing Gauge 26 pre-painted ridge cap; 650mm girth (average) in position complete with all necessary roofing screws or hooks as required. | m | 9.5
G.3 | Supplying & fixing Gauge 26 prepainted valleys; 650mm girth (average) in position complete with all necessary roofing screws or hooks as required. | m | 5
Valance / Barge Board
G.4 | 25x225mm high steel plate valance board / barge board fixed to edges of rafters including necessary fittings screws and nails etc. and painting | m | 38.8
G.5 | Supplying & fixing of PVC square eave gutters of cross section 200mm x 200mm or as specified, including all necessary accessories. | m | 38.8
G.6 | Supplying & fixing of 110 dia PVC rain water down pipes with metal straps to concrete block work at 1000mm centres vertically | m | 12
Roof Covering & Roof Plumbing
Doors
H.4 | Metal door set, type D1, of size 900x2500mm high overall including 400mm high 4mm steel louvre PV, comprising of 60x40x3mm RHS steel door frame fully welded and mitred at corners, 50x30x3mm RHS steel shutter frames: infilled with 1.5mm thick mild steel plate on two faces: include for all necessary door mortice locks, iron mongery, burglar proofing, final finish & fixing to concrete or blockwork as per drawings. | Nos. | 3
H.5 | Metal door set, type D2, of size 900x2500mm high overall including 400mm high 4mm steel louvre PV, comprising of 60x40x3mm RHS steel door frame fully welded and mitred at corners, 50x30x3mm RHS steel shutter frames: infilled with 1.5mm thick mild steel plate on two faces: include for all necessary door mortice locks, iron mongery, burglar proofing, final finish & fixing to concrete or blockwork as per drawings. | Nos. | 2
Windows
H.6 | Window, type W1, steel, size 1200x1500mm high overall including 400mm high steel louvre PV, Comprising of 60x40x4mm RHS frame fully welded and mitred at corners, Zed & Tee section side hung glass infilled window sashes, :include for all necessary fasteners,burglary proof and iron mongery, final finish, & fixing to concrete or blockwork as per drawings. | Nos. | 5
H.9 | Window, type W2, steel, size 600x1000mm high overall including 400mm high steel louvre PV, Comprising of 60x40x4mm RHS frame fully welded and mitred at corners, Zed & Tee section side hung glass infilled window sashes, :include for all necessary fasteners,burglary proof and iron mongery, final finish & fixing to concrete or blockwork as per drawings. | Nos. | 2
H | Doors & Windows
Wall Finishes
J.1 | 20mm thick cement & sand (1:5) render finished semi rough with wood float on external faces, on blockwalls or concrete surfaces | m² | 96.1
J.2 | 12mm thick cement lime sand (1:1:5) plaster finished smooth with lime putty or approved equivalent on internal faces, on blockwalls or concrete surfaces. | m² | 190.6
Floor finishes
J.3 | 40mm. thick cement and sand 1:3 screed finished rough with wooden float ready to receive floor tiles, cement grout & terrazzo (ms). | m² | 55.2
J.3a | Supply and fix non-slip ceramic floor tiles measuring 300x300mm on screed (ms) with approved adhesive, inclusive of 150mm high skirting. | m² | 64.56
J.3b | Ceramic wall tiles for toilets & work tops | m² | 30.36
J.3d | Coloured cement grouting to screeded floor (ms) finished smooth with steel floating | m² | 10.56
Plinth Plaster
J.4 | 20mm. thick cement and sand 1:3 plinth plaster finished with wooden float rough. | m² | 17.88
Ceiling Finishes
J.5 | Supply and fix gypsum plaster board or equally approved acoustic false ceiling panels on steel/aluminum branderings as per site engineers approval. | m² | 44.64
J.5.1 | Provide 150mm x 50mm timber joists and 75mm x 50mm timber brandering at a maximum spacing of 600mm x 600mm spacing and to it expanded metal lathe nailed ready to receive plaster | m² | 10.56
J.5.2 | 20mm. thick cement and sand 1:3 ceiling plaster finished smooth with lime floating. | m² | 10.56
Extra Over
| Supply and fixing of mahogany timber, MDF board or equally approved particle board cabinet shutters under worktops, including timber framing to engineers approval; include for all necessary iron mongery, final finish with clear varnish & fixing to concrete or blockwork as per drawings. | m | 10.5
J | Floor, Wall & Ceiling Finishes
Walls
K.1 | Prepare and apply one coat of primer and two coats of weather shield paint of approved colour and quality to external faces of walls | m² | 96.1
K.2 | Prepare and apply one coat of primer and two coats of vinly silk paint of approved colour and quality to internal faces of walls | m² | 190.6
K.3 | Ditto: Plinths | m² | 17.88
K | Painting
Cold Water Installation
Type 1000uPVC pipe with all necessary specials laid in water distribution system buried in brick walls / floor or clipped to any location where necessary.
L.1 | 20mm diameter. | m | 20
L.2 | 25mm diameter. | m | 30
L.3 | 32mm diameter. | m | 30
Taps and Valves
All taps and valves should be brass "Pegler" manufactured UK or approved equivalent, finish to be chrome plated or as per detail and as approved by the Engineer. Rate to include for joints to pipe work.
L.2 | 20mm diameter Bib Tap | Nos. | 1
L.3 | 20mm diameter Elbow knock taps | Nos. | 2
L.4 | 20mm diameter pillar Tap | Nos. | 1
L.5 | 25mm diameter angle valve. | Nos. | 2
L.6 | 20mm diameter isolation valve. | Nos. | 3
Waste and Sewage Disposal
Type 600 uPVC pipe with all necessary specials laid for internal and external waste and sewage Disposal system buried in brick walls / floor, clipped to any location or laid through ground soil where necessary.
L.6 | 50mm diameter. | m | 15
L.7 | 110mm diameter. | m | 30
L.8 | Fittings to 110 mm pipe work | Nos. | 6
L.9 | Supplying and fixing of uPVC trapped floor clean out including PVC grating. | Nos. | 4
Excavation for Pipes Works
L.10 | Excavation and back fill to pipe trench for normal pipe laying areas, depth not exceeding 1.0m deep as per detail drawing. (Rate shall include for screed concrete work) | m | 45
L.11 | Supplying & fixing of squatting pan with 'S' or 'P' trap outlet approved colour, complete with and fittings , drop pipe, flexible connections and necessary water connection etc. | Nos. | 2
L.11b | Supplying & fixing of Wash hand basins with 'S' or 'P' trap outlet approved colour, complete with and fittings , drop pipe, flexible connections and necessary water connection etc. | Nos. | 1
L.11c | Supplying & fixing of Dobby Sink size 550mm x 350mm with 'S' or 'P' trap outlet approved colour, complete with and fittings , drop pipe, flexible connections and necessary water connection etc. | Nos. | 1
Waste & Sewer Manholes, Septic tank & Soakage pit
L.14 | Gully trap 300 x300 complete with Gulley piece concrete surround and grating and 300 x 300 cast iron cover | No | 3
L.15 | 600 x 600mm Manhole 100mm deep(max) invert consisting of 150mm thick concrete block wall, benched and channeled in concrete Class "Q' and rendered and trowelled smooth in 20mm thick water proofed cement/sand screed including excavation and medium duty approved cast iron cover and frame | No | 4
L.16 | Vent Pipe of upvc 75mm dia x 3000mm, complte with mosquito gratings, fittings and connections. | No | 1
L.17 | Allow sum for connecting water to the main supply source. | item | 1
L.18 | Supply and install appropraite size PVC pipes and related accessories ( reducers, water valves, bends, unions etc) to connect the borehole with the water tank. It includes excavation, supply and placing sand benth the pipes, pipe supply & placing, backfilling with an optimum compaction. The gap in between the tank and the borehole would not be more than 45.0m. The rate shall also include supplying water from the water tanker into the existing toilet with two cells. | item | 1
L.19 | Provide, assemble and fix a steel water tower of height 3.85m, and other dimensions and details as shown on the plan for the same. It comprises excavation, reinforced concrete works, structural steels: 100*100*4mm SHS as main component, 50*50*3mm angle bars as ties and struts, 40*40*3mm SHS for the platform and rails, grade 4.6 18mm dia. bolts, 200*200*12mm base plates and 8mm thick gussets at joints of size as indicated on the drawing. Please refer the plan made for the tower and attached here with to compute each activities and materials required for the work. | item | 1
L.20 | Provide and fix a plastic water tank of standard quality with a capacity of 5,000liters. | pcs | 1
L.22 | Provide a well paved and standard water point having about four water taps within the premesis of the laboratory connected to the water tunker. | Ls | 1
L.23 | Testing & commissioning the entire installation | item | 1
Water Supply, Sewerage & Drainage Work (Plumbing)
Sub Distribution Board (SDB-1)
MCCB, MCB shall be manufactured by Merlin Gerin , F&G, Moler or equivalent & approved by the Engineer.
Supply and installation of switch gear cubicle made out of (2mm thickness) sheet steel enclosure (IP54) powder coated to the approval of the engineer.
Control panel for 100A, 3 Phase supply
01 Nos 40A , 2P RCCB
01 Nos 20A , 1P MCCB
02 Nos 6A , 1P MCCB
03 Nos 10 A , 2P MCB
01 Nos 30 A , 2P MCB
Set of Cu bus bars with neutral
Cu earth bar
Phase indicator lamps
| Wiring & other installation cost to include supply of a maximum of 30m 4 core 16mm2 diamter armoured underground electric cable connection to the nearest power supply | Nos. | 1
Final Circuit Wiring
Rates for final circuit wiring shall include all necessary switches, sockets, materials Cables, conduits, PVC sunk box, & junction boxes, draw wires, etc. and labour required to complete the electrical installation to good working order.
Light Point Wiring
| Wiring and installation (including supply of all materials) of the light points using approved type PVC insulated PVC sheathed 1 mm² copper cable and 2.5mm² Earth cable drawn through securely fixed concealed PVC conduit. (Switches shall be ABB / Clipsal / | Nos. | 9
13ASocket Outlet
M.3 | Supply & installation of 13A fused shuttered switched socket outlet to comply with relevant BS standard (Clipsal, Orange, Crabtree/ Tenby/ABB or equivalent). Wiring (including supply of earth wire & all other material required ) of above socket outlet | Nos. | 6
Fittings & Equipments
Light Fittings
M.4 | Supply and installation of Pendent lamp complete with 25 W CFL (Philips or equivalent) Lamp suitable for indoor use including all other necessary accessories like terminal block etc. (accessories - thorn / Philips or equivalent & fitting | Nos. | 3
M.5 | Supply and installation of Flourescent fitting complete with 25 W CFL (Philips or equivalent) Lamp suitable for indoor use including all other necessary accessories like terminal block etc. (accessories - thorn / Philips or equivalent & fitting | Nos. | 4
M.6 | Supply and installation of All-weather exterior light, 100 watt (Philips or equivalent) Lamp suitable for indoor use including all other necessary accessories like terminal block etc. (accessories - thorn / Philips or equivalent & fitting | Nos. | 2
Ceiling Fans
M.7 | Supply and installation of 56" sweep ceiling fan (Orient, KDK, Heavy Duty type, or as specified) complete with regulator, fan hook, extension rod & attachment - Guarantee cards should be provided from accredited agent before installation. | Nos. | 3
M.8 | Supply and installation of approved type Air condition system split level 12,000 BTU (LG or equivalent) complete with all necessary accessories to make it functional as approved by the engineer. | Nos.
Earthing Arrangement
M.9 | Supply and installation of approved type earthining system as approved by the engineer in order to keep the earth resistance below 10 ohms. The earth bar at the main distribution board should connect to the earth electrode with a 16mm2 PVC/CU cables | item | 1
| Supply and install a submersible solar water pump that can pump out water at least from 100m deep well, and pumps up the same into a water tank at a level 10.0m higher than the ground level where the pump is, and the discharge should not be less than 1,500.00 liters per hour ; Note that the pump shall be make GRUNDFOS SQF2.5-2 or SQF3A-10 or SQF5A-7(pupm selection shall depend on performance pump test results after well cleaning). | item | 1
M.10 | Allow the P.C Sum for the Supply & installation of Solar power system consisting of 12 No. 120W,12A Panels, 8No.200AH, 12V batteries;3KVA,24/48V inverters;60A,48V Charge Controller,20m,6mm single core cable, 6No. 4m long panel frames;16 No.35mm jumber c | item | 1
M.11 | Supply and install a solar power system that can run an submirsible pump up to its maximum output. The rate shall include provision and installation of supporting structures, fencing by chain link, if required, connecting with the pump and other related activities if any, that will make the pump function well. The solar panel support stand shall be angle bars 50*50*3mm coat finished , or aluminium. Foundation should be reinforced concrete. The design shall be presented to the engineer for approval prior to implementation. Note that the solar power does not need any backup. | item | 1
M.12 | Testing & commissioning the entire installation | item | 1
M | Electrical Installation
Shop Drawings & As Built Drawings
N.1 | Preparation of "Shop" drawings for the requirement of the construction | PS | 1
N.2 | Preparation of "As built" Drawings for the requirements of relevant authority or as directed by the Engineer. | PS | 2
N.3 | Allow provisional sum to cover possible additional costs due to any deviation from the tender issue drawings to construction issue drawings. | PS | 1
N | Provisional Sums
TOTAL

## Takeoff 1&2
Items | Item Description | Unit | No | Length | Width | Depth/Height | Preimeter | Area | Volume | Total | Remarks
A.1 | The contractor shall provide and maintain temporary sheds for the storage of materials, tools, and tackle and the use of all persons employed on the Site. Those used for the storage of cement and other perishable materials and the like are to be weatherproofed at all times | Item | 1 | [6 empty] | 1
A.2 | Provide, maintain and keep in a clean condition adequate temporary sanitary accommodation and facilities in accordance with local regulations for all persons employed on the Works. | Item | 1 | [6 empty] | 1
A.3 | Allow for supplying temporary electricity for the Works and facilities of the contractor including 'connection, distribution system for the work, internal arrangements and all payment to the authorities for connections. It is the responsibility of the Contractor to ensure steady and uninterrupted power supply to Works. The Contractor shall not be entitled to claim and the Employer shall not pay cost incurred by the Contractor for using electric power generators or for using other alternative power supply method in case there happened to be disruptions to normal power supply due to any reason. | Item | 1 | [6 empty] | 0
A.4 | Allow for provision of water for the works including drinking water, and paying all charges and other expenses in connection with the supply from water mains or any other alternative method of water supply, storage and distribution. It is the sole responsibility of the contractor to ensure steady, uninterrupted adequate supply of water required for main contract and nominated sub contract work. | Item | 1 | [6 empty] | 1
A.5 | Allow for providing and maintenance of name board and advertising board to the specifications and as directed by the Engineer. | Item | 1 | [6 empty] | 0
A.6 | Allow for mobilization i.e plant, machinery, other equipments including his work force etc to the site | Item | 1 | [6 empty] | 0
A.7 | Performance Guarantee | Item | 1 | [6 empty] | 0
A.8 | Contractor's All Risk Insurance(CAR)
| The All Risks insurance cover for the construction works, the construction plant, and for third party insurance. | Item | 1 | [6 empty] | 0
B | EXCAVATIONS AND EARTHWORKS
B.1 | Clearing and preparation of the site including cutting down and removal of top soil up to a depth of 150mm and disposed off as directed. | m² |  | 13.2 | 7.8 |  |  | 102.96 |  | 102.96
0
| Ditto but top soil at depth of 150mm | m2 | [7 empty] | 102.96
| Allow PC sum for relocating any service lines and maintance them in good condition. | item
B.2 | Excavation of trenches for wall strip foundations up to 1.2m deep in any material except rock requiring blasting and removal of surplus as directed. |  |  | 11.2 | 0.6 | 1 |  |  | 6.72 | 6.72
|  |  | 3 | 5.8 | 0.6 | 1 |  |  | 3.48 | 10.44
|  |  |  | 7 | 0.6 | 1 |  |  | 4.2 | 4.2
|  |  |  | 3.6 | 0.6 | 1 |  |  | 2.16 | 2.16
[10 empty] | 23.52 | strip excavation
B.2a | Ditto: Columns bases (9N0) | m³ | 9 | 1 | 1 | 1.2 |  |  | 1.2 | 10.8 | column exc.
Filling & Back filling
B.4 | Filling around strip foundations with selected excavated materials: ram and compact well | m³ |  |  | 0.4 | 0.8 | 39.2 |  | 12.544 | 12.544 | strip
| Ditto but fiiling around columns. | m³ | 9 | 2.2 | 0.4 | 1 |  |  | 0.88 | 7.92 | columns
B.5 | Filling under floors with 400mm thick gravel or other approved quality imported filling material, and 50mm thick sand blind. Spreading, watering and well ramming in layers. |  |  | 11.2 | 5.8 | 0.4 |  |  | 25.984 | 25.984
B.6 | Ditto- filling with 450mm thick selected excavated material well compacted |  |  | 11.2 | 5.8 | 0.45 |  |  | 29.232 | 29.232
B.6 | Anti - termite treatment to fillings and tops of foundations: as " Aldrex" or equal and approved insecticide treatment: applied in accordance with the manufacturer's printed instructions : include for 10 years warranty period. | m² | 1 | 11.2 | 5.8 |  |  | 64.96 |  | 64.96
0
C | CONCRETE WORKS
In Situ Concrete
C.1 | Supplying and placing of Gr.20 concrete as specified to foundation strip footings | m³ |  |  | 0.6 | 0.2 | 30.2 |  | 3.624 | 3.624
C.1a | Ditto: 100mm thick ramps laid to fall. | item
C.2a | Foundation pad Footings, Stub & verandah Columns | m³ | 9 | 1 | 1 | 0.05 |  |  | 0.45 | 4.05 | blinding
| Ditto: columns footings | m³ | 9 | 1 | 1 | 0.2 |  |  | 0.2 | 1.8
| Ditto: columns up to DPC Level | m³ | 9 | 0.2 | 0.2 | 1.8 |  |  | 0.072 | 0.648
2.448
C.2.b | Ditto: to columns up to Tie beam | m³ | 9 | 0.2 | 0.2 | 3.5 |  |  | 0.14 | 1.26
C.2b | Ditto: in ground beams size 200mm x 200mm | m³ |  |  | 0.2 | 0.2 | 39.2 |  | 1.568 | 1.568
C.2c | Ditto:For roof Tie beams | m³ |  |  | 0.2 | 0.25 | 39.2 |  | 1.96 | 1.96
C.2d | Ditto: 100mm thick floor beds. | m2 |  | 11.2 | 5.8 | 0.1 |  | 64.96 | 6.496 | 6.496
| Less | m³ | 9 | 0.2 | 0.2 |  |  | 0.04 |  | 0.36
[10 empty] | 6.136 | slab conc area
C.2e | Ditt: 75mm thick Conc.work tops | m2 |  | 10.5 | 0.6 |  | 10.5 | 6.3 |  | 6.3 | worktop
C.2f | Ditto:75mm thick conc.to waiting area benches | m2 |  | 3.65 | 0.45 |  |  | 1.6425 |  | 1.6425 | benches
Shuttering & Form Work
C.3a | Verandah Columns | m2 | 1 |  | 0.8 | 3.5 |  | 2.8 |  | 2.8
| Superstructure columns |  | 9 |  | 0.8 | 3.5 |  | 2.8 |  | 25.2
| Ditto: stiffener up to DPC Level | m2 | 9 |  | 0.8 | 1.8 |  | 1.44 |  | 12.96
40.96
C.3b | Ditto:for sides of grade beams | m2 | 2 |  |  | 0.25 | 39.2 | 19.6 |  | 19.6
C.3c | Ditto: for roof tie beams | m2 | 2 |  |  | 0.25 | 39.2 | 19.6 |  | 19.6
C.3d | Ditto: for edges/soffits of floor beds,worktops | m2
| Floor beds only | m2 | 1 |  |  | 0.1 | 29.8 | 2.98 |  | 2.98
| Worktops | m2 |  |  |  | 0.6 | 10.5 |  |  | 6.3 | soffits
[6 empty] | 0.075 | 10.5 |  |  | 0.7875 | edges
10.0675
C.3e | Ditto: for sides & soffits of waiting area benches. | m2 | 1 |  |  | 0.2 | 3.65 | 0.73 |  | 0.73 | edges
|  |  | 1 | 3.65 | 0.45 |  |  | 1.6425 |  | 1.6425 | soffits
2.3725
Steel Reinforcement
C.5 | R8 bars mild steel reinforcement bars
| Columns | Kg | 18 | 0.65 |  |  | 11.7 |  |  |  | columns below beam
|  |  | 26.5 | 0.65 |  |  | 17.225 |  |  |  | Columns above dpc level.
| Beams | Kg | 157.8 | 0.85 |  |  | 134.13
|  |  | 157.8 | 0.85 |  |  | 134.13 |  | `
297.185
[10 empty] | 115.9022 | total R8
C.6 | High Yield reinforcement bars (T8) at 150mm centres to conc.worktops,benches. | Kg | 4 | 3.65 |  |  | 14.6 |  |  | 14.6
|  |  | 25.3333 | 0.45 |  |  | 11.4 |  |  | 11.4
|  |  | 71 | 0.6 |  |  | 42.6 |  |  | 42.6
|  |  | 5 | 10.5 |  |  | 52.5 |  |  | 52.5 | worktops, benches
47.229
C.7 | High Yield reinforcement bars (Y12) | [5 empty] | 39.2
| Less |  | 9 | 0.2 |  |  | 1.8
37.4
| Foundation Strip footings | Kg | 4 |  |  |  | 37.4 |  |  | 132.8448 | Long bars
|  | Kg | 125.6667 |  |  |  | 0.5 |  |  | 55.796 | Crossing bars
188.6408
| Ditto: Columns | Kg | 9 | 14 |  |  | 126 |  |  |  | pads
|  | Kg | 36 | 1.8 |  |  | 64.8 |  |  |  | Columns high up to Dpc level.
[7 empty] | 190.8 |  |  | 169.4304
|  | Kg | 9 |  |  | 14 | 126 |  |  | 111.888 | Columns above dpc level.
| Beams | Kg | 4 |  |  |  | 39.2 |  |  | 139.2384 | grade beam
|  |  | 4 |  |  |  | 39.2 |  |  | 139.2384 | roof beam
278.4768
[10 empty] | 748.436 | total Y12
C.8 | Supplying & laying A BRC net for Ground floor slab: Include laps and Waste. | m2 | [5 empty] | 64.96 |  | 64.96
C.9 | Lintel Size 200mm x 200mm in cross section: complete with 4 T12 bars and R8 bars at 300mm centres: include all required formwork. | lm
|  |  | 2 | 0.6 |  |  | 1 |  |  | 2 | W2
|  |  | 7 | 1.2 |  |  | 1.6 |  |  | 11.2 | W1
|  |  | 5 | 0.9 |  |  | 1.3 |  |  | 6.5 | D1
|  |  | 1 | 2.6 |  |  | 3 |  |  | 3 | verandah
|  |  | 1 | 1.8 |  |  | 2.2 |  |  | 2.2 | POMPEY
|  |  | 1 | 1.4 |  |  | 1.8 |  |  | 1.8 | POMPEY
26.7
Splash Apron
In black cotton soils
C.11 | 75mm thick concrete (grade 20) 600x600mm slabs laid on 100mm sand blinding base well rammed and finished monolithically with 25mm thick cement and sand (1:3) screed trowelled smooth to gentle falls with joints pointed and including 150mm thick concrete block edge wall average 600mm deep rendered on and including 450mm x 150mm thick concrete grade 15 foundation and all necessary excavations and disposal of spoil and formwork to edge of apron. |  |  |  | 0.6 |  | 29.8 | 17.88 |  | 17.88
Masonry Work
Up to DPC level
D.1 | Solid concrete block walls in cement sand (1:5) mortar in Steps | item | 1 | [6 empty] | 1
D.2 | 200 mm Thick solid concrete block walls in cement sand (1:5) mortar in foundations | m2 |  |  |  | 1.8 | 39.2 | 70.56 |  | 70.56
Concrete block work
D.3 | 200mm thick walls in standard precast hollow cement blocks in 1:5 cement sand mortar for SUPERSTRUCTURE walls. | m2 | 3 | 5.8 |  | 3.25 | 17.4 | 56.55 |  | 56.55
|  |  | 1 | 11.2 |  | 3.25 | 11.2 | 36.4 |  | 36.4
|  |  | 1 | 3.6 |  | 3.25 | 3.6 | 11.7 |  | 11.7
|  |  | 1 | 2.2 |  | 3.25 | 2.2 | 7.15 |  | 7.15
|  |  | 1 | 6.6 |  | 3.25 | 6.6 | 21.45 |  | 21.45
[7 empty] | 41 |  |  | 133.25
| Less openings |  | 7 | 1.2 |  | 1.5 | 8.4 | 12.6 |  | 12.6 | W1
|  |  | 2 | 0.6 |  | 1 | 1.2 | 1.2 |  | 1.2 | W2
|  |  | 5 | 0.9 |  | 2.5 | 4.5 | 11.25 |  | 11.25 | D1
|  |  | 1 | 1.4 |  | 2.5 | 1.4 | 3.5 |  | 3.5 | pompey
|  |  | 1 | 1.8 |  | 2.5 | 1.8 | 4.5 |  | 4.5 | pompey
|  |  | 1 | 2.6 |  | 2.5 | 2.6 | 6.5 |  | 6.5 | VERANDAH
[7 empty] | 19.9 |  |  | 39.55
[10 empty] | 93.7 | Total wall area
D.4 | Ditto: 150mm Thick walls for work top & benches | m2 | 3 | 0.45 |  | 0.45 |  | 0.2025 |  | 0.6075 | benches
|  |  | 5 | 0.6 |  | 0.8 |  | 0.48 |  | 2.4 | worktops
3.0075
D.5 | Supply and lay pompey grills to openings | m2 | 0 | 1.4 |  | 2.5 |  | 3.5 |  | 3.5
|  |  |  | 1.8 |  | 2.5 |  | 4.5 |  | 4.5
8
E | THERMAL AND MOISTURE PROTECTION
Damp Proof Course
E.1 | Horizontal damp proof course: bituminous: laid horizontally on screeded 20 mm thick (1:3) screeded beds to receive block walls. | m2 |  | 21.1 |  | 0.2 |  | 4.22 |  | 4.22
Damp proof membrane
E.2 | Horizontal damp proof membrane :1000 gauge polythene membrane: laid on compacted fillings (measured separately) in ground floor beds. ( The rate shall include for laps & wastage). | m2 | [5 empty] | 64.96 |  | 64.96
F | STRUCTURAL METALWORKS
F.1 | Roof truss RT1 spanning 5800mm wide by 2000mm high, consisting of 2/50x50x4mm equal angle iron members welded to gusset plate. Rate shall include for painting as specified. |  | 4
F.2 | Roof truss RT2 spanning 4200mm wide, consisting of 2/50x50x4mm equal angle iron members welded to gusset plate with all necessary accessories. Rate shall include for painting as specified. |  | 2
F.7 | Rafters RR,HR & VR, consisting of 50x50x4mm equal angle iron members welded to gusset plate all necessary accessories of fixing in place. Rate shall include for painting as specified.
Purlins
F.8 | Supplying & fixing of Zed purlins, 75 x 50 x 2mm: welded to roof trusses ( measured separately)at 900mm centres: complete with all the required paint works and all necessary supports |  | 10 | 11.2 |  |  | 12.4 |  |  | 124
F.10 | Allow sum for any other item required for the construction and completion of the roof framework, which are not covered under the above items. | item
ROOF COVERINGS, CEILING AND PLUMBING
Roof Covering
G.1 | Supplying & fixing of gauge 26 pre-painted Super VI profiled roofing sheets of approved colour: fixed with J-bolts to 75 x 50 x 2mm zed purlins ( measured separately) and rubber caping to tops of bolts |  | 2 | 12.4 | 4 |  |  | 49.6 |  | 99.2
Ridges
G.2 | Supplying & fixing Gauge 26 pre-painted ridge cap; 650mm girth (average) in position complete with all necessary roofing screws or hooks as required. |  | 4 | 4 | [5 empty] | 4
|  |  |  | 5.5 | [5 empty] | 5.5
9.5
G.3 | Supplying & fixing Gauge 26 prepainted valleys; 650mm girth (average) in position complete with all necessary roofing screws or hooks as required. |  |  | 3.8 | [5 empty] | 3.8
Valance / Barge Board
G.4 | 25x225mm high timber valance board / barge board fixed to edges of rafters including necessary fittings screws and nails etc.: including wood preservative and painting |  |  | 12.4 | 7 |  | 38.8 |  |  | 38.8
G.5 | Supplying & fixing of PVC square eave gutters of cross section 200mm x 200mm or as specified, including all necessary accessories. |  |  | 38.8 | [5 empty] | 38.8
G.6 | Supplying & fixing of 110 dia PVC rain water down pipes with metal straps to concrete block work at 1000mm centres vertically |  | 3 | 4 |  |  | 12 |  |  | 12
H.3 | Door set, type D1, of size 900x2500mm high overall including 400mm high 4mm glass fanlight PV, comprising of 60x40x3mm RHS steel door frame fully welded and mitred at corners, Mahogany hardwood flush door shutters: include for all necessary door mortice locks, iron mongery, burglar proofing, final finish, & fixing to concrete or blockwork as per drawings. |  | 3 | [6 empty] | 3
H.5 | Metal door set, type D2, of size 800x2500mm high overall including 400mm high glass fanlight PV, comprising of 60x40x3mm RHS steel door frame fully welded and mitred at corners, Mahogany hardwood flush door shutters: include for all necessary door locks, iron mongery, final finish & fixing to concrete or blockwork as per drawings. |  | 2 | [6 empty] | 2
Windows
H.6 | Window, type W1, steel, size 1200x1500mm high overall including 400mm high steel louvre PV, Comprising of 60x40x4mm RHS frame fully welded and mitred at corners, Zed & Tee section side hung glass infilled window sashes, :include for all necessary fasteners,burglary proof and iron mongery, final finish, & fixing to concrete or blockwork as per drawings. |  | 5 | [6 empty] | 5
H.9 | Window, type W2, steel, size 600x1000mm high overall including 400mm high steel louvre PV, Comprising of 60x40x4mm RHS frame fully welded and mitred at corners, Zed & Tee section side hung glass infilled window sashes, :include for all necessary fasteners,burglary proof and iron mongery, final finish & fixing to concrete or blockwork as per drawings. |  | 2 | [6 empty] | 2
J.1 | 20mm thick cement & sand (1:5) render finished semi rough with wood float on external faces, on blockwalls or concrete surfaces |  | 1 | 11.2 | 5.8 | 3.5 | 34 | 119 |  | 119
| less openings |  | 4 | 1.2 |  | 1.5 |  | 1.8 |  | 7.2
|  |  | 2 | 0.6 |  | 1 |  | 0.6 |  | 1.2
|  |  | 1 | 1.8 |  | 2.5 |  | 4.5 |  | 4.5
|  |  | 1 | 2.6 |  | 2.5 |  | 6.5 |  | 6.5
|  |  | 1 | 1.4 |  | 2.5 |  | 3.5 |  | 3.5
22.9
[10 empty] | 96.1 | Total render
J.2 | 12mm thick cement lime sand (1:1:5) plaster finished smooth with lime putty or approved equivalent on internal faces, on blockwalls or concrete surfaces. |  | 4 | 5.4 |  | 3.5 |  | 18.9 |  | 75.6
|  |  | 2 | 3.6 |  | 3.5 |  | 12.6 |  | 25.2
|  |  | 2 | 2.2 |  | 3.5 |  | 7.7 |  | 15.4
|  |  | 2 | 11.2 |  | 3.5 |  | 39.2 |  | 78.4
|  |  | 2 | 6.8 |  | 3.5 |  | 23.8 |  | 47.6
242.2
| Less openings |  | 8 | 1.2 |  | 1.5 |  | 1.8 |  | 14.4
|  |  | 2 | 0.6 |  | 1 |  | 0.6 |  | 1.2
|  |  | 4 | 0.8 |  | 2.5 |  | 2 |  | 8
|  |  | 6 | 0.9 |  | 2.5 |  | 2.25 |  | 13.5
|  |  | 1 | 2.6 |  | 2.5 |  | 6.5 |  | 6.5
|  |  | 1 | 1.8 |  | 2.5 |  | 4.5 |  | 4.5
|  |  | 1 | 1.4 |  | 2.5 |  | 3.5 |  | 3.5
[10 empty] | 51.6 | Area openings
[10 empty] | 190.6 | Total plaster
Floor finishes
J.3 | 40mm. thick cement and sand 1:3 screed finished rough with wooden float ready to receive floor tiles, cement grout (ms). |  | 1 | 5.4 | 4 |  | 18.8 | 21.6 |  | 21.6
|  |  | 1 | 3.6 | 4 |  | 15.2 | 14.4 |  | 14.4
|  |  | 1 | 3.6 | 2.4 |  | 12 | 8.64 |  | 8.64
|  |  | 1 | 6.6 | 1.6 |  | 16.4 | 10.56 |  | 10.56
[7 empty] | 62.4 |  |  | 55.2
J.3a | Supply and fix non-slip ceramic floor tiles 300x300mm on screed (ms) with approved adhesive, inclusive of 150mm high skirting. | [6 empty] | 55.2 |  | 55.2
|  |  | 1 | 62.4 | 0.15 |  |  | 9.36 |  | 9.36 | Skirting
[10 empty] | 64.56 | Total floor tiles
J.3b | Ceramic wall tiles for toilets & work tops |  | 4 | 2 |  | 1.5 |  | 3 |  | 12
|  |  | 2 | 1.2 |  | 1.5 |  | 1.8 |  | 3.6
[10 empty] | 15.6 | toilets
|  |  | 2 | 12.3 |  | 0.6 |  | 7.38 |  | 14.76 | On and above worktops
[10 empty] | 30.36 | total wall tiles
J.3d | Coloured cement grouting to screeded floor (ms) finished smooth with steel floating |  |  | 6.6 | 1.6 |  |  | 10.56
[10 empty] | 10.56 | external passages
Plinth Plaster
J.4 | 20mm. thick cement and sand 1:3 plinth plaster finished smooth with coloured cement floating. |  | 1 | 29.8 |  | 0.6 |  | 17.88 |  | 17.88
[10 empty] | 17.88 | exposed plinth
Ceiling Finishes
J.5 | Supply and fix gypsum plaster board or equally approved acoustic false ceiling panels on steel/aluminum branderings as per site engineers approval. | [6 empty] | 55.2
[8 empty] | 10.56 |  | 44.64
J.5.1 | Provide 150mm x 50mm timber joists and 75mm x 50mm timber brandering at a maximum spacing of 600mm x 600mm spacing and to it expanded metal lathe nailed ready to receive plaster |  |  | 6.6 | 1.6 |  |  | 10.56 |  | 10.56
J.5.2 | 20mm. thick cement and sand 1:3 ceiling plaster finished smooth with lime floating. | [6 empty] | 10.56 |  | 10.56
Extra Over
J.6 | Supply and fixing of mahogany timber, MDF board or equally approved particle board cabinet shutters under worktops, including timber framing to engineers approval; include for all necessary iron mongery, final finish with clear varnish & fixing to concrete or blockwork as per drawings. | m |  | 10.5 | [5 empty] | 10.5
K.1 | Prepare and apply one coat of primer and two coats of weather shield paint of approved colour and quality to external faces of walls | [8 empty] | 96.1
K.2 | Prepare and apply one coat of primer and two coats of emulsion paint of approved colour and quality to internal faces of walls | [8 empty] | 190.6
Note on L9: Kenyi Koma: Not Providede.
Note on L12: Kenyi Koma: Only Simple hand tools used on the ground to produce work.
Note on L44: Kenyi Koma: Trapezium floor shape.