| Rehabilitation of Unified Water Plant in Rawah |  |  |  |
| --- | --- | --- | --- |
| Item # in BOQ | Item | Required Specifications | Submitted Specifications |
| C - Electrical works for project and service buildings |  |  |  |
| Item 31 | Distribution board | 1 main circuit breaker of three phase and 100 Amp capacity with bus bar of 100 Amp; 5 circuit breaker of 10 Amp capacity; 7 circuit breaker of 20 Amp capacity; 6 circuit breaker of 32 Amp capacity. Short circuit breaking capacity of circuit breakers shall not be less that 35 kA |  |
| F- water treatment unit |  |  |  |
| Item 28 & Item 73 | 2 Ton split unit | Type Wall Mounted Split Unit CHARACHTERISTICS Auxiliary supply voltage (V) 230 V/50HZ Tonnage Range (T) 2 Ton Compressor DC Inverter / T3 Refrigerant Gas R410A Cooling Capacity (BTUH) 24000 Filter Type Micro dust protection filter washable Running current (A) 14.8/15.4 Operation Range temperature © (17 -30) Remote Control Wireless /LCD type Noise Level (dB) 30 - 35 -40 Max ambient temp. T3 (52°C) Certification of origin Certification of origin Submit Manufacturer certification and test reports . Submit Detail drawing brochure catalogue. Submit Detail drawing brochure catalogue. |  |
| Item 74 | Water Boiler | Installation Vertical /Cylindrical Water Tank Coating Enameled Capacity Range 120 Liter Nominal power 3 KW / 220v-240v /50HZ Nominal pressure 0.8 Mpa In let & out let Decimeter ¾ “ Inch Electric heating type Immersion element Insulation Type Foam Protection Safety Valve ¾” Submit Manufacturer certification and test reports Submit Manufacturer certification and test reports |  |
| Item 80 | Split case pump of (480 m3/hr*50m) capacity | Pump Type: Horizontal Water Pump, Heavy duty application, soft backing, mechanical lubrication unit; Shaft: Stainless steel - GG25 (AISI420); Impeller: Bronze; Motor:IP55, Isolation class = f; Rated Voltage:380 – 400 V. Speed:1500 RPM; Main frequency:50hz; Enclosure class: IP 55 , Insulation class : F Max ambient temp : 60 C No of phase :3 Ph. / 50HZ Rated power : 250 Kw Certificate of origin and inspection documents are required. |  |
| Item 81 | Rotary Air Blower | Q= 750m3/hr. capacity, Head of pressure = 20 bar, 1500r/min, |  |
| Item 82 | Electrical crane of 5 Ton Capacity | Double girder (5Ton); 6 direction two speed for lower& Upper; the work includes supply festoon system (Cable, Channel, angle& trolley) of 60 m length, with overloads and slope sensors , as per specification following: 1-Hoisting capacity 5000Kg 2- Lifting Crane 9m3-Dynamic test load 5500kg at least 4-Static test load 5500kg at least 5-Lifting speed Creep 0.6m/min Fast 4m/min at least 6-Hoisting Break type Electromagnetic disk break. 7-Cross travel break type Electromagnetic.8-Control Type With pushbutton.9-Long Travel electrical component. Required brands are KM, GIS or ABM. |  |
| Item 86 | Gear box and electrical motor (which works to rotate muds sweeper around sedimentation basins) | 3 KW capacity, RPM 900 r/ min, three phases western origin |  |
| Item 87 | Electrical Motor ( which works on the movement and irritation of the muds in the small rotors existing in the sedimentation basins) | 10 KW capacity, RPM 900 r/ min, three phases with the shaft and its blades western origin |  |
| Item 88 | Distribution board | 2 Circuit breakers of 60 Amp. 10 contactors of 60 Amp; 1 amperage gage; 1 voltage meter; 1 HZ gage, 1 selector switch, 1 phase failure, 1 overload of 10 A capacity. Metal board of 70*35 cm required brands are ABB, Schneider, Hyundai and Siemens |  |
| Item89 | Chlorine device of 8 Kg.m/ hr. capacity | Injectors; Type : ( Alldoz ,OBL or equivalent ) . Copper pipes; Bronze valves, Network of PVC pipes; Western origin |  |
| Item 90 | chlorine Booster pumps | Brand : (Grundfos , wilo ,Lowara or equivalent ) Capacity :10 m3/h capacity Type : Vertical Multi stages H = 120 m |  |
| Item 93 | Electrical crane of 5 Ton Capacity | Single girder (5Ton); 2 direction two speed for lower& Upper; the work includes supply festoon system (Cable, Channel, angle& trolley), with overloads and slope sensors , as per specification following: 1-Hoisting capacity 5000Kg 2- Lifting Crane 9m 3-Dynamic test load 5500kg at least 4-Static test load 5500kg at least 5-Hoisting Break type Electromagnetic disk break. 6-Cross travel break type Electromagnetic. 7-Control type With pushbutton. 8-Long Travel electrical component. Required brands are KM, GIS or ABM. |  |
| Item 95 | Alum dossing pumps | capacity : 1200 L/h Pressure : 4 bar, Rated Power : 1.5 K.W Speed : 1500 rpm |  |
| Item 96 | Electrical motor for the alum mixer | shaft length of 1.5 m, 3 feathers stainless steel type, capacity of 2 kw, RPM 1500, |  |
| Item 101 | Submersible pump | 2 kW electrical motor capacity delivery hose is 2-inch diameter |  |
| G- Electrical Generators and transformer works: |  |  |  |
| Item 105, | Electrical Generator of 1250kVa Capacity - Silent Type | Prime Generator 1250 KVA,1MW , silent type1 - Original manufacturer (Local Assembled Not acceptable) Ambient temperature :Maximum:55/C Minimum:-10/C , Relative Humidity : around 60% at maximum temperature , Relative Humidity : around 60% at maximum, Altitude: 1000M above MSL . 2- System Voltage: 400V/ 3PH, 50 HZ , Guarantee: one year ,1000HR of operation , Generator output Range : 1500KVA prime , Exhaust and inlet/outlet air, stand by not less 1650 KVA, 400A 4pole and 8 hour operation base tank 3- No of cylinders : ,12 inline,1500 RPM, Electronic Governor, fuel system/storage Diesel tanks, Type of starting 24 DC Battery system, power factor between 0.8 and 1 . 4- Type of excitation: Brushless, self-regulation and self-exited, engine. cooling system: Topical radiator and engine driven cooling -fan, IP :not less than 23,Insulation type : class H, AVR type : digital ,transfer switch automatic(ATS) with option of manual operation and Earthing studs Brands :Cummins, Perkins and caterpillar or equivalent Manufacturer . ……………………………………………………………… Model No............................................................................... Country of Origin.................................................................. |  |
| Item 107 | changeover 1600 Amp. | 1600 Amp. capacity, metal board of 70*40*30cm size, bronze busbars, multi digit screen (V, A, Hz). brands are ABB, Schneider, Siemens or equivalent, |  |
| Item 110 | Distribution Transformer 11/0.416 kV 1000 KVA The following Technical data shall be furnished and filled by the bidders: |  |  |
|  | Description | UNDP required specifications | Offered specification |
| 1 | Make/Brand/Model: | To be Filled in |  |
| 2 | Name of manufacturer | To be filled in |  |
| 3 | Type: | Oil-immersed hermetically sealed - bolted type- three phase-outdoor |  |
| 4 | Country of origin | To be filled in |  |
| 5 | Reference standard | IEC 60076-1, 2,3,5,8, |  |
|  |  | IEC 60214, IEC 60137 |  |
| 6 | Ambient temperature: | Maximum:55/C |  |
|  |  | Minimum: -10/C |  |
| 7 | Air humidity: | 92% maximum |  |
| 8 | Altitude: | 1000M above MSL |  |
| 9 | Highest system voltage | 12 kV |  |
| 10 | Short circuit current on 11 kV side | 25 KA |  |
| 11 | 11 kV system earthing | To be Filled in |  |
| 12 | Low voltage side earthing | Neutral solidly earthed |  |
| 13 | Voltage Ratio | 11/0.416 KV |  |
| 14 | Type of cooling | ONAN |  |
| 15 | Rated Continuous Power | 1000 kVA |  |
| 16 | Rated Frequency | 50Hz |  |
| 17 | Impedance voltage at 75 deg at nominal tap | ≥ 5% |  |
| 18 | Nominal Voltage of winding |  |  |
|  | a) H.V. | 11 kV |  |
|  | b) L.V | 0.416 kV |  |
| 19 | Insulation level 11 kV |  |  |
|  | a) Lightning Impulse | 75 kV |  |
|  | b) AC power frequency | 28 kV |  |
| 20 | Insulation level LV -phases/neutral |  |  |
|  | AC power frequency | 3 kV |  |
| 21 | Winding temperature rise at rated power | 50 C |  |
| 22 | Top oil temperature rises at rated power | 45 C |  |
| 23 | No load loss in | KW |  |
| 24 | Load loss at full load at 75 deg temperature | KW |  |
| 25 | Efficiency | 98.90% |  |
| 26 | Regulation |  |  |
| 27 | Maximum flux density in iron at rated frequency and at rated voltage ratio at nominal voltage |  |  |
|  |  | ≤ 1.65 Tesla |  |
| 28 | Maximum current density in windings at |  |  |
|  | rated power |  |  |
|  | a) H.V. winding |  |  |
|  | b) L.V. winding |  |  |
| 29 | No load current at rated voltage | Amp |  |
| 30 | Material of windings | Copper |  |
| 31 | Type of insulation of | To be Filled in |  |
|  | a) Core assembly |  |  |
|  | b) Core laminations |  |  |
| 32 | Thickness of transformer |  |  |
|  | a) tank | Minimum 3 mm |  |
|  | b) sides | Minimum 3 mm |  |
|  | c) bottom | Minimum 3 mm |  |
| 33 | Thickness of radiator plates and for cooling tube | Minimum 1.5 mm |  |
| 34 | Winding connection |  |  |
|  | a) H.V. | Delta |  |
|  | b) L.V. | Star (Neutral brought out) |  |
| 35 | Vector group symbol | Dyn11 |  |
| 36 | Tap changer | Off-load tap changer with 5 positions in the HV winding giving ± 2 x 2.5 %. |  |
| 37 | 11 kV side terminal arrangement | Clamp type for terminating up to 150 mm2 copper conductor |  |
| 38 | Low voltage terminal arrangement | Suitable for terminating copper cables of cross section area 14×1×240 mm2 copper (not less than 3 holes per phase). |  |
| 39 | Low voltage terminal assignation | Neutral bushing should distinguished from phase bushing by longer distance of separation |  |
| 40 | Noise level at 0.3 m distance | ≤ 55 dB |  |
| 41 | Transformer oil |  |  |
|  | Type of oil | IEC60296 class 1 |  |
|  | Manufacturer | To be Filled in |  |
|  | Place of manufacture | To be Filled in |  |
|  | Manufacturer’s type designation | To be Filled in |  |
|  | Applied IEC standard | IEC 60296 |  |
|  | Kinematic viscosity mm2/s | To be Filled in |  |
|  | At 40 deg | ≤ 16.5 |  |
|  | At -15 deg | ≤ 800 |  |
|  | Flash point | ≥ 140 C |  |
|  | Pour point | ≤ - 30 C |  |
|  | Density at 20 deg C – kg/dm3 | ≤ 0.895 |  |
|  | Breakdown strength | kV |  |
| 41 | Dimensions of transformer | L 1700 ( mm) x W 1400.(mm) x H 1800.(mm) |  |
| 42 | Weight of transformer | kg |  |
| 43 | Type of corrosion protection on steel parts |  |  |
|  | a) Inside tank |  |  |
|  | b) Outside tank | Oil resistant paint |  |
| 44 | 11 kV bushings |  |  |
|  | Name of manufacturer |  |  |
|  | Make/Brand/Model: |  |  |
|  | Reference standard | IEC 60137 |  |
|  | Type of bushing |  |  |
|  | Rated current | Amp |  |
|  | Rated voltage | KV |  |
|  | Material | Porcelain |  |
|  | Color | Brown |  |
|  | Creepage distance | Minimum 300 mm |  |
| 45 | L V bushings |  |  |
|  | Name of manufacturer | To be Filled in |  |
|  | Make/Brand/Model: | To be Filled in |  |
|  | Reference standard | IEC 60137 |  |
|  | Type of bushing | To be Filled in |  |
|  | Rated current | Amp |  |
|  | Rated voltage | KV |  |
|  | Material | Porcelain |  |
|  | Color | Brown |  |
|  | Creepage distance | mm |  |
| 46 | Neutral bushing | Distinguished from phase bushing by longer distance of separation. |  |
| 47 | Warranty period | One year |  |
| 48 | Submit manufacturers certification | To be Submitted |  |
| 49 | Submit type test certificates or | To be Submitted |  |
|  | reports : |  |  |
| 50 | Submit Detail drawings, drawings of HV and LV bushings, details of accessories, brochures and catalogues: | To be Submitted |  |
| H- Withdrawals Section " Intake" |  |  |  |
| Item 111 | Horizontal pump of (500 m3/h *100-110m) capacity | Pump Type: Horizontal Water Pump (split case) ,Heavy duty application, soft backing, mechanical lubrication unit; Shaft: Stainless steel - GG25 (AISI420); Impeller: Bronze; Motor:IP55, Isolation class = f Rated power : 350 KW Voltage:380 – 400 V Rated Speed:1500 RPM; Main frequency:50hz; Enclosure class: IP 55 No of phase : 3 phase;. Certificate of origin and inspection documents are required. |  |
| Item 112 | Distribution Transformer 11/0.416 kV 1000 KVA The following Technical data shall be furnished and filled by the bidders: |  |  |
|  | Description | UNDP required specifications | Offered specification |
| 1 | Make/Brand/Model: | To be Filled in |  |
| 2 | Name of manufacturer | To be filled in |  |
| 3 | Type: | Oil-immersed hermetically sealed - bolted type- three phase-outdoor |  |
| 4 | Country of origin | To be filled in |  |
| 5 | Reference standard | IEC 60076-1, 2,3,5,8, |  |
|  |  | IEC 60214, IEC 60137 |  |
| 6 | Ambient temperature: | Maximum:55/C |  |
|  |  | Minimum: -10/C |  |
| 7 | Air humidity: | 92% maximum |  |
| 8 | Altitude: | 1000M above MSL |  |
| 9 | Highest system voltage | 12 kV |  |
| 10 | Short circuit current on 11 kV side | 25 KA |  |
| 11 | 11 kV system earthing | To be Filled in |  |
| 12 | Low voltage side earthing | Neutral solidly earthed |  |
| 13 | Voltage Ratio | 11/0.416 KV |  |
| 14 | Type of cooling | ONAN |  |
| 15 | Rated Continuous Power | 1000 kVA |  |
| 16 | Rated Frequency | 50Hz |  |
| 17 | Impedance voltage at 75 deg at nominal tap | ≥ 5% |  |
| 18 | Nominal Voltage of winding |  |  |
|  | a) H.V. | 11 kV |  |
|  | b) L.V | 0.416 kV |  |
| 19 | Insulation level 11 kV |  |  |
|  | a) Lightning Impulse | 75 kV |  |
|  | b) AC power frequency | 28 kV |  |
| 20 | Insulation level LV -phases/neutral |  |  |
|  | AC power frequency | 3 kV |  |
| 21 | Winding temperature rise at rated power | 50 C |  |
| 22 | Top oil temperature rise at rated power | 45 C |  |
| 23 | No load loss in | KW |  |
| 24 | Load loss at full load at 75 deg temperature | KW |  |
| 25 | Efficiency | 98.90% |  |
| 26 | Regulation |  |  |
| 27 | Maximum flux density in iron at rated frequency and at rated voltage ratio at nominal voltage |  |  |
|  |  | ≤ 1.65 Tesla |  |
| 28 | Maximum current density in windings at |  |  |
|  | rated power |  |  |
|  | a) H.V. winding |  |  |
|  | b) L.V. winding |  |  |
| 29 | No load current at rated voltage | Amp |  |
| 30 | Material of windings | Copper |  |
| 31 | Type of insulation of | To be Filled in |  |
|  | a) Core assembly |  |  |
|  | b) Core laminations |  |  |
| 32 | Thickness of transformer |  |  |
|  | a) tank | Minimum 3 mm |  |
|  | b) sides | Minimum 3 mm |  |
|  | c) bottom | Minimum 3 mm |  |
| 33 | Thickness of radiator plates and for cooling tube | Minimum 1.5 mm |  |
| 34 | Winding connection |  |  |
|  | a) H.V. | Delta |  |
|  | b) L.V. | Star (Neutral brought out) |  |
| 35 | Vector group symbol | Dyn11 |  |
| 36 | Tap changer | Off-load tap changer with 5 positions in the HV winding giving ± 2 x 2.5 %. |  |
| 37 | 11 kV side terminal arrangement | Clamp type for terminating up to 150 mm2 copper conductor |  |
| 38 | Low voltage terminal arrangement | Suitable for terminating copper cables of cross section area 14×1×240 mm2 copper (not less than 3 holes per phase). |  |
| 39 | Low voltage terminal assignation | Neutral bushing should distinguished from phase bushing by longer distance of separation |  |
| 40 | Noise level at 0.3 m distance | ≤ 55 dB |  |
| 41 | Transformer oil |  |  |
|  | Type of oil | IEC60296 class 1 |  |
|  | Manufacturer | To be Filled in |  |
|  | Place of manufacture | To be Filled in |  |
|  | Manufacturer’s type designation | To be Filled in |  |
|  | Applied IEC standard | IEC 60296 |  |
|  | Kinematic viscosity mm2/s | To be Filled in |  |
|  | At 40 deg | ≤ 16.5 |  |
|  | At -15 deg | ≤ 800 |  |
|  | Flash point | ≥ 140 C |  |
|  | Pour point | ≤ - 30 C |  |
|  | Density at 20 deg C – kg/dm3 | ≤ 0.895 |  |
|  | Breakdown strength | kV |  |
| 41 | Dimensions of transformer | L 1700 ( mm) x W 1400.(mm) x H 1800.(mm) |  |
| 42 | Weight of transformer | kg |  |
| 43 | Type of corrosion protection on steel parts |  |  |
|  | a) Inside tank |  |  |
|  | b) Outside tank | Oil resistant paint |  |
| 44 | 11 kV bushings |  |  |
|  | Name of manufacturer |  |  |
|  | Make/Brand/Model: |  |  |
|  | Reference standard | IEC 60137 |  |
|  | Type of bushing |  |  |
|  | Rated current | Amp |  |
|  | Rated voltage | KV |  |
|  | Material | Porcelain |  |
|  | Color | Brown |  |
|  | Creepage distance | Minimum 300 mm |  |
| 45 | L V bushings |  |  |
|  | Name of manufacturer | To be Filled in |  |
|  | Make/Brand/Model: | To be Filled in |  |
|  | Reference standard | IEC 60137 |  |
|  | Type of bushing | To be Filled in |  |
|  | Rated current | Amp |  |
|  | Rated voltage | KV |  |
|  | Material | Porcelain |  |
|  | Color | Brown |  |
|  | Creepage distance | mm |  |
| 46 | Neutral bushing | Distinguished from phase bushing by longer distance of separation. |  |
| 47 | Warranty period | One year |  |
| 48 | Submit manufacturers certification | To be Submitted |  |
| 49 | Submit type test certificates or | To be Submitted |  |
|  | reports : |  |  |
| 50 | Submit Detail drawings, drawings of HV and LV bushings, details of accessories, brochures and catalogues: | To be Submitted |  |
| Item 113 | changeover 1600 Amp. | 1600 Amp. capacity, metal board of 70*40*30cm size, bronze busbars, multi digit screen (V, A, Hz). brands are ABB, Schneider, Siemens or equivalent, |  |